## Schedule
rank | score | address | town | postcode | ba_name | firm_name | description | cls | hereditaments | area_m2 | area_sqft | unit | rv_total | primary | primary_match | km_to_primary | grid_site | gsp | zone | effective_headroom_mw | binding_tier | headroom_mw | rag_short | demand_firm_mw | demand_max_mw | limiting_factor | offers_accepted_mw | offers_made_mw | budget_est_mw | pipeline_pressure_mw | headroom_2030_mw | bsp_name | bsp_headroom_mw | bsp_constraint | bsp_offers_made_mw | gsp_headroom_mw | gsp_rag | gsp_queue_apps | gsp_queue_mva | gsp_queue_apps_since_2024 | firm_mva_winter | firm_mva_summer | season | unutilised_pct | headroom_polygon_mw | rag | edge_sqft_supportable_at_headroom | edge_share_of_building_pct | edge_fitout_whole_building_mva | indicative_existing_kva | other_candidates_on_primary | other_candidate_sqft_on_primary | lm_substation | lm_rating_kva | lm_headroom_kva | lm_band | lm_feeder | lm_distance_m | lm_hv_headroom_kva | lm_hv_distance_m | lm_source | tx_gsp_region | tx_tec_key | tx_tec_projects | tx_tec_pipeline_mw | tx_tec_storage_mw | tx_tec_demand_hybrid_mw | tx_tec_gate2_mw | tx_tec_connected_mw | tx_tec_next_date | epc_uprn | epc_property_type | epc_floor_area_m2 | epc_rating | epc_heating_fuel | epc_building_level | epc_aircon_kw | epc_environment | epc_lodged | epc_special_uses | epc_match_score | epc_is_data_centre | lat | lon | primary_floc | uarns | source
1 | 100 | LAKE VIEW HOUSE, RENNIE DRIVE | DARTFORD | DA1 5FU | Dartford |  | Warehouse And Premises | industrial | 1 | 11078.15 | 119244 | GIA | 1190000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.2 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 17.6 | 277 | 7 | 1043035 | [9 empty] | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10023441884 | B8 Storage or Distribution | 12344 | B | Natural Gas | 4 |  | Air Conditioning | 2021-03-31 |  | 1 | FALSE | 51.4609 | 0.23812 | SPN-S000000009377 | 9315027000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
2 | 100 | RESOURCES RECOVERY UNIT, RENNIE DRIVE | DARTFORD | DA1 5FD | Dartford |  | Warehouse And Premises | industrial | 1 | 9363.6 | 100789 | GIA | 1080000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.24 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 14.88 | 234 | 7 | 1061490 | SPN-S000000324286 | 1000 | 900 | 80-100% | LITTLEBROOK PARK 132/11KV | 396 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4604 | 0.23982 | SPN-S000000009377 | 9812792000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
3 | 100 | UNIT 14 (A), RENNIE DRIVE | DARTFORD | DA1 5FD | Dartford |  | Warehouse And Premises | industrial | 1 | 6765.92 | 72828 | GIA | 880000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.24 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 10.75 | 169 | 7 | 1089451 | SPN-S000000324286 | 1000 | 900 | 80-100% | LITTLEBROOK PARK 132/11KV | 396 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094157996 | B8 Storage or Distribution | 6595 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2021-09-17 |  | 1 | FALSE | 51.4604 | 0.23982 | SPN-S000000009377 | 14511233000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
4 | 95 | UNIT 1, RENNIE DRIVE | DARTFORD | DA1 5PR | Dartford |  | Car Showroom And Premises | bigbox | 1 | 5832.34 | 62779 | GIA | 1200000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.9 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 9.27 | 525 | 7 | 1099500 | SPN-S000000316824 | 1000 | 100 | 0-20% | CROSSWAYS | 346 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4552 | 0.24436 | SPN-S000000009377 | 12438960000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
5 | 90 | UNIT 11, RENNIE DRIVE | DARTFORD | DA1 5FD | Dartford |  | Warehouse And Premises | industrial | 3 | 16941.93 | 182361 | GIA | 2010000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.24 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 26.92 | 424 | 7 | 979918 | SPN-S000000324286 | 1000 | 900 | 80-100% | LITTLEBROOK PARK 132/11KV | 396 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094158000 | B8 Storage or Distribution | 2678 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2022-03-09 |  | 1 | FALSE | 51.4604 | 0.23982 | SPN-S000000009377 | 13591924000;14761260000;13184066000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
6 | 90 | UNIT 13 (C), RENNIE DRIVE | DARTFORD | DA1 5FD | Dartford |  | Warehouse And Premises | industrial | 1 | 1596 | 17179 | GIA | 202000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.24 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 2.54 | 40 | 7 | 1145100 | SPN-S000000324286 | 1000 | 900 | 80-100% | LITTLEBROOK PARK 132/11KV | 396 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094157998 | B8 Storage or Distribution | 1572 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2021-09-17 |  | 1 | FALSE | 51.4604 | 0.23982 | SPN-S000000009377 | 13993930000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
7 | 90 | UNIT 12 (B), RENNIE DRIVE | DARTFORD | DA1 5FD | Dartford |  | Warehouse And Premises | industrial | 1 | 1178.21 | 12682 | GIA | 147000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.24 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 100 | 1.87 | 29 | 7 | 1149597 | SPN-S000000324286 | 1000 | 900 | 80-100% | LITTLEBROOK PARK 132/11KV | 396 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094157997 | B8 Storage or Distribution | 1143 | A | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2021-09-17 |  | 1 | FALSE | 51.4604 | 0.23982 | SPN-S000000009377 | 13993906000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
8 | 86.4 | 19, LAKER ROAD, ROCHESTER AIRPORT INDUSTRIAL ESTATE | ROCHESTER | ME1 3QX | Tonbridge & Malling |  | Factory And Premises; Warehouse And Premises; Workshop And Premises | industrial | 3 | 12905.39 | 138912 | GIA | 968000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.82 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 20.51 | 774 | 29 | 1675196 | SPN-S000000313875 | 1000 | 700 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3539 | 0.4996 | SPN-S000000008508 | 6570127000;379746148;380347148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
9 | 86.4 | 1ST & 3RD FLRS & PT GND & 2ND FLRS, ANCHOR WHARF, BUILDING 3, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TE | Medway |  | Warehouse And Premises | industrial | 1 | 7651.52 | 82360 | GIA | 157000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 1.99 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 12.16 | 191 | 29 | 1731748 | SPN-S000000311758 | 500 | 250 | 40-60% | CHATHAM HILL 33/11KV | 205 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3934 | 0.52752 | SPN-S000000008508 | 5802013000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
10 | 86.4 | PT 1ST FLR, BUILDING 5, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TG | Medway |  | Workshop And Premises | industrial | 2 | 6485.84 | 69813 | GIA | 142000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.16 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 10.31 | 292 | 29 | 1744295 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3947 | 0.52876 | SPN-S000000008508 | 15019365000;15019367000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
11 | 86.4 | FORT BRIDGEWOOD, MAIDSTONE ROAD | ROCHESTER | ME1 3DT | Medway | ROYAL MAIL | Warehouse And Premises | industrial | 1 | 4667.4 | 50239 | GIA | 325000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.99 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 7.42 | 117 | 29 | 1763869 | SPN-S000000311586 | 500 | 250 | 40-60% | CHATHAM WEST 33/11KV (NEW) | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3771 | 0.50031 | SPN-S000000008508 | 385245147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
12 | 86.4 | CHDT NO 7 SLIP, MAIN GATE ROAD, BUILDING 46, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TZ | Medway |  | Store And Premises | industrial | 1 | 4386 | 47210 | GIA | 74500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.17 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 6.97 | 110 | 29 | 1766898 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3951 | 0.52806 | SPN-S000000008508 | 3702200000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
13 | 86.4 | COREFRESH, FORT BRIDGEWOOD, MAIDSTONE ROAD | ROCHESTER | ME1 3DQ | Medway |  | Warehouse And Premises | industrial | 1 | 3839.28 | 41326 | GIA | 285000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.42 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 6.1 | 96 | 29 | 1772782 | SPN-S000000311330 | 500 | 350 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44007103 | B2 to B7 General Industrial and Special Industrial Groups | 3312 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2018-12-15 |  | 0.75 | FALSE | 51.3597 | 0.49435 | SPN-S000000008508 | 13302137000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
14 | 86.4 | 21, LAKER ROAD | ROCHESTER | ME1 3QX | Medway |  | Factory And Premises | industrial | 1 | 3728.04 | 40128 | GIA | 265000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.82 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 5.92 | 224 | 29 | 1773980 | SPN-S000000313875 | 1000 | 700 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062374940 | B2 to B7 General Industrial and Special Industrial Groups | 3765 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-03-17 |  | 1 | FALSE | 51.3539 | 0.4996 | SPN-S000000008508 | 166248147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
15 | 86.4 | SUNLIGHT SERVICES, MAIDSTONE ROAD | CHATHAM | ME4 6DE | Medway |  | Workshop And Premises | industrial | 1 | 3549.94 | 38211 | GIA | 153000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.62 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 5.64 | 160 | 29 | 1775897 | SPN-S000000311715 | 500 | 50 | 0-20% | CHATHAM WEST 33/11KV (OLD) | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.376 | 0.52317 | SPN-S000000008508 | 5525382000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
16 | 86.4 | CHATHAM SORTING OFFICE, BEST STREET | CHATHAM | ME4 4AA | Medway |  | Sorting Office And Premises | industrial | 1 | 3211.13 | 34564 | GIA | 150000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.84 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 5.1 | 225 | 29 | 1779544 | SPN-S000000311735 | 500 | 50 | 0-20% | CHATHAM WEST 33/11KV (OLD) | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3806 | 0.52555 | SPN-S000000008508 | 27583147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
17 | 86.4 | TARRED YARN STORE, COTTAGE ROAD, BUILDING 7, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TG | Medway |  | Warehouse And Premises | industrial | 1 | 2002 | 21549 | GIA | 80500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.16 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 3.18 | 50 | 29 | 1792559 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3947 | 0.52876 | SPN-S000000008508 | 2977340000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
18 | 86 | UNIT 3, BELLINGHAM WAY, PANATTONI PARK | AYLESFORD | ME20 7WT | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 10367.38 | 111593 | GIA | 950000 | NEW HYTHE 33/11kV | inside-area | 0.31 | Burham Grid | Northfleet | Mid Kent Zone | 34.5 | primary | 34.5 | Green | 37.3 |  |  | 0 | 0 | 0 | 0 | 32 |  |  |  | 0 | 97 | GREEN | 13 | 552.7 | 3 | 37.3 | 29.4 | Winter | 92.4933 | 34.5 | Green (Over 5% headroom) | 245989 | 100 | 16.47 | 259 | 2 | 558450 | SPN-S000000392907 | 1000 | 900 | 80-100% | TOWNSEND HOOK 33/6.6KV | 266 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3034 | 0.45687 | SPN-S000000008682 | 14261835000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
19 | 82.5 | DISTRIBUTION CENTRE, RENNIE DRIVE | DARTFORD | DA1 5FD | Dartford | SAINSBURYS | Warehouse And Premises | industrial | 1 | 55223.17 | 594417 | GIA | 6640000 | LITTLEBROOK PARK 132/11KV | inside-area | 0.24 | Littlebrook Park 132/11 | Littlebrook | West Kent Zone | 47.8 | primary | 47.8 | Green | 60 | 12.2 | Thermal | 10 | 9.5 | 0 | 19.5 | 53 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | Green (Over 5% headroom) | 340820 | 57 | 87.75 | 1381 | 7 | 567862 | SPN-S000000324286 | 1000 | 900 | 80-100% | LITTLEBROOK PARK 132/11KV | 396 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4604 | 0.23982 | SPN-S000000009377 | 9812497000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
20 | 81.4 | NEW CUT | CHATHAM | ME4 6AA | Medway | WICKES BUILDING SUPPLIES | Retail Warehouse And Premises | bigbox | 2 | 5762.8 | 62030 | GIA | 760000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.64 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 9.16 | 519 | 29 | 1752078 | SPN-S000000311706 | 1000 | 500 | 40-60% | CHATHAM WEST 33/11KV (OLD) | 178 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44040709 | Retail/Financial and Professional Services | 2509 | B | Natural Gas | 3 | 3 | Heating and Natural Ventilation | 2023-08-07 |  | 1 | FALSE | 51.3817 | 0.52085 | SPN-S000000008508 | 391766147;391766147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
21 | 81.4 | 661-671, MAIDSTONE ROAD | ROCHESTER | ME1 3QJ | Medway |  | Sports Centre And Premises; Warehouse And Premises | bigbox | 2 | 3862.98 | 41581 | GIA | 264000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.52 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 6.14 | 309 | 29 | 1772527 | SPN-S000000324276 | 1000 | 700 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 140 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44009903 | General Assembly and Leisure, Night Clubs, and Theatres | 2127 | B | Natural Gas | 4 | 2 | Air Conditioning | 2023-09-26 |  | 1 | FALSE | 51.3574 | 0.49767 | SPN-S000000008508 | 363256000;394625147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
22 | 81.4 | W M MORRISONS, PRINCES AVENUE | CHATHAM | ME5 7PQ | Medway |  | Superstore And Premises | bigbox | 1 | 3634.63 | 39123 | GIA | 665000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 3.03 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 5.78 | 327 | 29 | 1774985 | SPN-S000000316802 | 1000 | 500 | 40-60% | CHATHAM WEST 33/11KV (OLD) | 104 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3534 | 0.53494 | SPN-S000000008508 | 14349654000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
23 | 81.4 | 68-72, THE PENTAGON | CHATHAM | ME4 4HP | Medway |  | Superstore And Premises | bigbox | 1 | 3175.5 | 34181 | GIA | 292500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 1.04 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 5.05 | 286 | 29 | 1779927 | SPN-S000000313709 | 1000 | 700 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 39 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3835 | 0.52587 | SPN-S000000008508 | 49129147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
24 | 80.3 | WAREHOUSE 16, KINGSMEAD | FOLKESTONE | CT19 5EU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 5087.98 | 54767 | GIA | 347500 | MOREHALL 132/11KV | inside-area | 1.41 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 8.09 | 127 | 34 | 1513971 | SPN-S000000362299 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50105154 | Storage or Distribution | 5091 | C | Natural Gas | 4 | 2 | Air Conditioning | 2023-06-08 |  | 1 | FALSE | 51.0934 | 1.1666 | SPN-S000000009320 | 8655524000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
25 | 80.3 | UNITS B/C/E/F/G/H, FIVE ACRE SITE, PARK FARM ROAD | FOLKESTONE | CT19 5DS | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 4454.34 | 47946 | GIA | 189000 | MOREHALL 132/11KV | inside-area | 1.81 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 7.08 | 111 | 34 | 1520792 | SPN-S000000362334 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50102908 | B8 Storage or Distribution | 834 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-10-23 |  | 1 | FALSE | 51.0951 | 1.1718 | SPN-S000000009320 | 13166315000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
26 | 80.3 | UNITS C14 AND C15, SHEARWAY BUSINESS PARK, PENT ROAD | FOLKESTONE | CT19 4RJ | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 4429.62 | 47680 | GIA | 225000 | MOREHALL 132/11KV | inside-area | 0.79 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 7.04 | 199 | 34 | 1521058 | SPN-S000000371398 | 500 | 350 | 60-80% | MOREHALL 132/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0928 | 1.1492 | SPN-S000000009320 | 15059271000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
27 | 80.3 | UNIT 7, BARNFIELD ROAD | FOLKESTONE | CT19 5EA | Folkestone & Hythe |  | Warehouse And Premises | industrial | 2 | 2955.1 | 31808 | GIA | 217000 | MOREHALL 132/11KV | inside-area | 1.65 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 4.7 | 74 | 34 | 1536930 | SPN-S000000361386 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0941 | 1.1701 | SPN-S000000009320 | 15050455000;15148819000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
28 | 80.3 | UNITS B-D, KINGSMEAD | FOLKESTONE | CT19 5EU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2383.13 | 25652 | GIA | 151000 | MOREHALL 132/11KV | inside-area | 1.41 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.79 | 60 | 34 | 1543086 | SPN-S000000362299 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0934 | 1.1666 | SPN-S000000009320 | 9050561000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
29 | 80.3 | ROSS DEPOT & 1ST FLR OFFICE, MILITARY ROAD | FOLKESTONE | CT20 3SP | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 2371.55 | 25527 | GIA | 159000 | MOREHALL 132/11KV | inside-area | 0.92 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.77 | 142 | 34 | 1543211 | SPN-S000000363630 | 315 | 94 | 20-40% | MOREHALL 132/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0802 | 1.1407 | SPN-S000000009320 | 10229303000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
30 | 80.3 | THE OLD BREWERY, PARK FARM CLOSE | FOLKESTONE | CT19 5DU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2227.5 | 23977 | GIA | 113000 | MOREHALL 132/11KV | inside-area | 1.74 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.54 | 56 | 34 | 1544761 | SPN-S000000362334 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 43 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0942 | 1.1716 | SPN-S000000009320 | 2313200000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
31 | 80.3 | CENTURY HOUSE, PARK FARM ROAD | FOLKESTONE | CT19 5DW | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 2224.15 | 23941 | GIA | 129000 | MOREHALL 132/11KV | inside-area | 1.7 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.53 | 100 | 34 | 1544797 | SPN-S000000362334 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50042157 | Offices and Workshop Businesses | 767 | C | Natural Gas | 4 |  | Heating and Natural Ventilation | 2023-08-14 |  | 1 | FALSE | 51.0939 | 1.1711 | SPN-S000000009320 | 10596450000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
32 | 80.3 | 331-333, CHERITON ROAD | FOLKESTONE | CT19 4BQ | Folkestone & Hythe |  | Store And Premises | industrial | 1 | 2005.74 | 21590 | GIA | 28250 | MOREHALL 132/11KV | inside-area | 0.19 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.19 | 50 | 34 | 1547148 | SPN-S000000361780 | 500 | 50 | 0-20% | MOREHALL 132/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0868 | 1.1484 | SPN-S000000009320 | 7943853000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
33 | 80.3 | WESTBOURNE CLEANING SUPPLY LTD, NORTH CLOSE | FOLKESTONE | CT20 3UH | Folkestone & Hythe | WESTBOURNE CLEANING SUPPLY LTD | Warehouse And Premises | industrial | 1 | 1925.39 | 20725 | GIA | 116000 | MOREHALL 132/11KV | inside-area | 1.05 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.06 | 48 | 34 | 1548013 | SPN-S000000363913 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | B8 Storage or Distribution | 704 | C | Grid Supplied Electricity | 3 |  | Heating and Mechanical Ventilation | 2019-12-18 |  | 0.5 | FALSE | 51.0802 | 1.1385 | SPN-S000000009320 | 131248145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
34 | 76.4 | 2ND - 11TH FLRS, MOUNTBATTEN HOUSE, MILITARY ROAD | CHATHAM | ME4 4JF | Medway |  | Offices And Premises | office | 1 | 7770.63 | 83642 | NIA | 322500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.99 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 12.35 | 544 | 29 | 1730466 | SPN-S000000313710 | 1000 | 700 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3838 | 0.52456 | SPN-S000000008508 | 7854134000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
35 | 76.4 | GND 1ST & 2ND FLRS, VICTORY HOUSE, MEETING HOUSE LANE | CHATHAM | ME4 4YU | Medway |  | Offices And Premises | office | 2 | 3253.76 | 35023 | NIA | 382000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.88 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 5.17 | 228 | 29 | 1779085 | SPN-S000000312188 | 750 | 375 | 40-60% | CHATHAM WEST 33/11KV (OLD) | 22 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44038762 | B1 Offices and Workshop businesses | 5803 | D | Natural Gas | 4 |  | Air Conditioning | 2014-07-11 |  | 1 | FALSE | 51.3817 | 0.52522 | SPN-S000000008508 | 4871044000;2154101000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
36 | 76.4 | MHS HOMES BROADSIDE, LEVIATHAN WAY, CHATHAM MARITIME | CHATHAM | ME4 4LL | Medway |  | Offices And Premises | office | 1 | 3014.11 | 32444 | NIA | 555000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.91 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 4.79 | 211 | 29 | 1781664 | SPN-S000000324260 | 1000 | 700 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | Offices and Workshop Businesses | 4157 | C | Natural Gas | 5 | 1 | Heating and Mechanical Ventilation | 2024-04-05 |  | 1 | FALSE | 51.4012 | 0.53222 | SPN-S000000008508 | 4759680000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
37 | 76.4 | CROWN HOUSE, THE BROOK | CHATHAM | ME4 4LB | Medway |  | Offices And Premises | office | 1 | 2829.78 | 30459 | NIA | 280000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 1.12 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 4.5 | 198 | 29 | 1783649 | SPN-S000000311760 | 500 | 250 | 40-60% | CHATHAM WEST 33/11KV (NEW) | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.381 | 0.52962 | SPN-S000000008508 | 888869000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
38 | 76.4 | 2, WALTER BURKE WAY, CHATHAM MARITIME | CHATHAM | ME4 4RN | Medway |  | Offices And Premises | office | 1 | 2426.43 | 26118 | NIA | 412500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.71 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 3.86 | 170 | 29 | 1787990 | SPN-S000000316944 | 315 | 158 | 40-60% | CHATHAM WEST 33/11KV (NEW) | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44113523 | Offices and Workshop Businesses | 3174 | A | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2024-04-16 |  | 0.8 | FALSE | 51.3986 | 0.53409 | SPN-S000000008508 | 14990498000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
39 | 76.4 | FIDENTIA HOUSE, WALTER BURKE WAY, CHATHAM MARITIME | CHATHAM | ME4 4RN | Medway |  | Offices And Premises | office | 1 | 2361.27 | 25416 | NIA | 407500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.71 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 3.75 | 165 | 29 | 1788692 | SPN-S000000316944 | 315 | 158 | 40-60% | CHATHAM WEST 33/11KV (NEW) | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44113523 | Offices and Workshop Businesses | 3174 | A | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2024-04-16 |  | 1 | FALSE | 51.3986 | 0.53409 | SPN-S000000008508 | 5173344000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
40 | 76.4 | 344, HIGH STREET | ROCHESTER | ME1 1BT | Medway |  | Workshop And Premises | industrial | 1 | 1613.29 | 17365 | GIA | 95000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.67 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 2.56 | 73 | 29 | 1796743 | SPN-S000000311666 | 500 | 350 | 60-80% | CHATHAM WEST 33/11KV (NEW) | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062374387 | A1/A2 Retail and Financial/Professional services | 690 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-10-21 |  | 0.5 | FALSE | 51.3834 | 0.51343 | SPN-S000000008508 | 394526147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
41 | 76.4 | CHDT PT THE LEAD & PAINT MILL, COTTAGE ROAD, BUILDING 9, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TZ | Medway |  | Workshop And Premises | industrial | 1 | 1411.41 | 15192 | GIA | 43000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.17 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 2.24 | 64 | 29 | 1798916 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | Storage or Distribution | 668 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-09-20 |  | 0.67 | FALSE | 51.3951 | 0.52806 | SPN-S000000008508 | 2937622000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
42 | 76.4 | SELECTRON HOUSE UNIT A, JENKINS DALE | CHATHAM | ME4 5RD | Medway |  | Warehouse And Premises | industrial | 1 | 1145.4 | 12329 | GIA | 78500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 0.89 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 1.82 | 29 | 29 | 1801779 | SPN-S000000311752 | 315 | 158 | 40-60% | CHATHAM WEST 33/11KV (OLD) | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3767 | 0.52731 | SPN-S000000008508 | 13339157000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
43 | 76.4 | CENTRE SECTION BRUNEL SAWMILL, BUILDING 38, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TL | Medway |  | Workshop And Premises | industrial | 1 | 1016.66 | 10943 | GIA | 53500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.34 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 1.62 | 46 | 29 | 1803165 | SPN-S000000314608 | 500 | 250 | 40-60% | CHATHAM WEST 33/11KV (OLD) | 83 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3957 | 0.53147 | SPN-S000000008508 | 2844744000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
44 | 76 | UNIT 2, GILL CLOSE, PANATTONI PARK | AYLESFORD | ME20 7XL | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 16735.02 | 180134 | GIA | 1620000 | NEW HYTHE 33/11kV | inside-area | 0.79 | Burham Grid | Northfleet | Mid Kent Zone | 34.5 | primary | 34.5 | Green | 37.3 |  |  | 0 | 0 | 0 | 0 | 32 |  |  |  | 0 | 97 | GREEN | 13 | 552.7 | 3 | 37.3 | 29.4 | Winter | 92.4933 | 34.5 | Green (Over 5% headroom) | 245989 | 100 | 26.59 | 418 | 2 | 489909 | SPN-S000000394880 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 315 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094698370 | B8 Storage or Distribution | 8100 | A | Grid Supplied Electricity | 5 |  | Air Conditioning | 2022-09-08 |  | 0.67 | FALSE | 51.3094 | 0.45421 | SPN-S000000008682 | 14073849000;14117109000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
45 | 75.3 | ASDA 19, BOUVERIE PLACE SHOPPING CENTRE, ALEXANDRA GARDENS | FOLKESTONE | CT20 1AU | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 9143.1 | 98415 | GIA | 995000 | MOREHALL 132/11KV | inside-area | 2.03 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 14.53 | 823 | 34 | 1470323 | SPN-S000000371345 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0798 | 1.1781 | SPN-S000000009320 | 9029994000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
46 | 75.3 | HOMEBASE (HHGL), PARK FARM ROAD | FOLKESTONE | CT19 5FJ | Folkestone & Hythe |  | Retail Warehouse And Premises | bigbox | 1 | 7100.96 | 76434 | GIA | 477500 | MOREHALL 132/11KV | inside-area | 1.76 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 11.28 | 639 | 34 | 1492304 | SPN-S000000363478 | 800 | 720 | 80-100% | MOREHALL 132/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0963 | 1.1694 | SPN-S000000009320 | 14333379000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
47 | 75.3 | TESCO STORES LTD, CHERITON HIGH STREET | FOLKESTONE | CT19 4QJ | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 5809.79 | 62536 | GIA | 1470000 | MOREHALL 132/11KV | inside-area | 1.55 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 9.23 | 523 | 34 | 1506202 | SPN-S000000363523 | 300 | 150 | 40-60% | MOREHALL 132/11KV | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50025281 | A1/A2 Retail and Financial/Professional services | 5556 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-03-29 |  | 1 | FALSE | 51.0904 | 1.1298 | SPN-S000000009320 | 14170537000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
48 | 75.3 | CANTERBURY ROAD | DOVER | CT15 7HX | Folkestone & Hythe | MACFARLANES NURSERIES | Garden Centre And Premises | bigbox | 1 | 4817.4 | 51854 | NIA | 52500 | MOREHALL 132/11KV | inside-area | 6.34 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 7.66 | 434 | 34 | 1516884 | SPN-R000000839119-000-181Z | 25 | 8 | 20-40% | DOVER 33/11KV | 337 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50036069 | Retail/Financial and Professional Services | 1076 | C | LPG | 3 |  | Heating and Natural Ventilation | 2024-02-12 |  | 1 | FALSE | 51.1422 | 1.1637 | SPN-S000000009320 | 73589145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
49 | 75.3 | MORRISONS, CHERITON ROAD | FOLKESTONE | CT19 5JU | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 4488.5 | 48314 | GIA | 950000 | MOREHALL 132/11KV | inside-area | 0.69 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 7.13 | 404 | 34 | 1520424 | SPN-S000000362220 | 300 | 210 | 60-80% | MOREHALL 132/11KV | 266 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0869 | 1.1604 | SPN-S000000009320 | 13841504000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
50 | 75.3 | SHORNCLIFFE MOTOR PARK, ROSS WAY | FOLKESTONE | CT20 3UJ | Folkestone & Hythe | KENT AUTO PANELS LTD | Car Showroom And Premises | bigbox | 1 | 4300.63 | 46292 | GIA | 535000 | MOREHALL 132/11KV | inside-area | 0.82 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 6.83 | 387 | 34 | 1522446 | SPN-S000000371608 | 500 | 450 | 80-100% | MOREHALL 132/11KV | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.081 | 1.1415 | SPN-S000000009320 | 538463145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
51 | 75.3 | SAINSBURYS 5, BOUVERIE ROAD WEST | FOLKESTONE | CT20 2RX | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 4189.12 | 45091 | GIA | 460000 | MOREHALL 132/11KV | inside-area | 1.91 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 6.66 | 377 | 34 | 1523647 | SPN-S000000364149 | 800 | 560 | 60-80% | MOREHALL 132/11KV | 96 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0788 | 1.1755 | SPN-S000000009320 | 9877311000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
52 | 75.3 | HOMEBASE LTD, PARK FARM ROAD | FOLKESTONE | CT19 5GA | Folkestone & Hythe |  | Retail Warehouse And Premises | bigbox | 1 | 3652.4 | 39314 | GIA | 397500 | MOREHALL 132/11KV | inside-area | 1.49 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 5.8 | 329 | 34 | 1529424 | SPN-S000000364294 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50034559 | A1/A2 Retail and Financial/Professional services | 3458 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-09-18 |  | 0.5 | FALSE | 51.0951 | 1.1658 | SPN-S000000009320 | 7205747000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
53 | 75.3 | WICKES, PARK FARM ROAD | FOLKESTONE | CT19 5UL | Folkestone & Hythe |  | Retail Warehouse And Premises | bigbox | 1 | 2229.21 | 23995 | GIA | 267500 | MOREHALL 132/11KV | inside-area | 1.34 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.54 | 201 | 34 | 1544743 | SPN-S000000364294 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 163 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0951 | 1.1627 | SPN-S000000009320 | 11005024000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
54 | 74.1 | 15, LEIGH ROAD | RAMSGATE | CT12 5EU | Thanet | AVIATION ENGINEERING | Factory And Premises; Warehouse And Premises; Warehouse, Office And Premises | industrial | 3 | 9864.83 | 106184 | GIA | 401750 | MANSTON 33/11KV | inside-area | 1.78 | Richborough Grid | Richborough | East Kent Zone | 25.6 | primary | 25.6 | Green | 38.1 | 2.4 | Thermal | 9 | 41 | 0 | 50 | 31.1 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.6 | 28.8 | Summer | 92.3611 | 26.6 | Green (Over 5% headroom) | 182531 | 100 | 15.68 | 592 | 4 | 265333 | SPN-S000000342203 | 500 | 250 | 40-60% | RAMSGATE 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3451 | 1.387 | SPN-S000000008616 | 454988145;536340145;531691145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
55 | 74.1 | UNIT 2 AT 24, LEIGH ROAD | RAMSGATE | CT12 5EU | Thanet |  | Warehouse And Premises | industrial | 3 | 5997.51 | 64557 | GIA | 414000 | MANSTON 33/11KV | inside-area | 1.78 | Richborough Grid | Richborough | East Kent Zone | 25.6 | primary | 25.6 | Green | 38.1 | 2.4 | Thermal | 9 | 41 | 0 | 50 | 31.1 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.6 | 28.8 | Summer | 92.3611 | 26.6 | Green (Over 5% headroom) | 182531 | 100 | 9.53 | 150 | 4 | 306960 | SPN-S000000342203 | 500 | 250 | 40-60% | RAMSGATE 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10097162832 | Storage or Distribution | 1350 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2024-09-23 |  | 1 | FALSE | 51.3451 | 1.387 | SPN-S000000008616 | 15148077000;15148076000;15148079000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
56 | 74.1 | 6-8, WILTON ROAD | RAMSGATE | CT12 5HE | Thanet |  | Factory And Premises | industrial | 1 | 2172.4 | 23383 | GIA | 68000 | MANSTON 33/11KV | inside-area | 1.72 | Richborough Grid | Richborough | East Kent Zone | 25.6 | primary | 25.6 | Green | 38.1 | 2.4 | Thermal | 9 | 41 | 0 | 50 | 31.1 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.6 | 28.8 | Summer | 92.3611 | 26.6 | Green (Over 5% headroom) | 182531 | 100 | 3.45 | 130 | 4 | 348134 | SPN-S000000342203 | 500 | 250 | 40-60% | RAMSGATE 33/11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062284097 | B8 Storage or Distribution | 429 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-04-30 |  | 1 | FALSE | 51.3461 | 1.3869 | SPN-S000000008616 | 454983145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
57 | 73.5 | BLOCK 8, VESTRY ROAD | SEVENOAKS | TN14 5EL | Sevenoaks |  | Warehouse And Premises | industrial | 4 | 7142.17 | 76878 | GIA | 720000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.47 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 11.35 | 179 | 19 | 766169 | SPN-S000000446574 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013775298 | Storage or Distribution | 1348 | B | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-12-07 |  | 1 | FALSE | 51.2988 | 0.19589 | SPN-S000000008447 | 1725870000;13693157000;5207369000;396137148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
58 | 73.5 | 6, CONNECTIONS BUSINESS PARK, VESTRY ROAD | SEVENOAKS | TN14 5DF | Sevenoaks |  | Warehouse And Premises; Workshop And Premises | industrial | 4 | 6820.27 | 73413 | GIA | 654000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.11 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 10.84 | 307 | 19 | 769634 | SPN-S000000446577 | 800 | 560 | 60-80% | NORTH SEVENOAKS 33/11KV | 205 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062548606 | General Industrial and Special Industrial Groups | 743 | A | Grid Supplied Electricity | 3 | 2 | Heating and Natural Ventilation | 2026-02-23 |  | 1 | FALSE | 51.2954 | 0.19515 | SPN-S000000008447 | 10917022000;10920795000;10917035000;10917026000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
59 | 73.5 | UNIT 8, NORTH DOWNS BUSINESS PARK, PILGRIMS WAY | SEVENOAKS | TN13 2TL | Sevenoaks |  | Warehouse And Premises | industrial | 5 | 6072.72 | 65366 | GIA | 687000 | NORTH SEVENOAKS 33/11KV | inside-area | 3.37 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 9.65 | 152 | 19 | 777681 | SPN-S000000446089 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3102 | 0.15514 | SPN-S000000008447 | 8174866000;409385148;409384148;14099138000;409389148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
60 | 73.5 | JARDOX, VESTRY ROAD | SEVENOAKS | TN14 5EL | Sevenoaks |  | Factory And Premises | industrial | 1 | 5391.52 | 58034 | GIA | 275000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.47 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 8.57 | 323 | 19 | 785013 | SPN-S000000446574 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062621733 | B1 Offices and Workshop businesses | 3023 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-02-12 |  | 0.5 | FALSE | 51.2988 | 0.19589 | SPN-S000000008447 | 8647506000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
61 | 73.5 | UNIT 8, GOYA BUSINESS PARK, THE MOOR ROAD | SEVENOAKS | TN14 5GY | Sevenoaks |  | Warehouse And Premises | industrial | 2 | 3764.26 | 40518 | GIA | 385000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.05 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 5.98 | 94 | 19 | 802529 | SPN-S000000451707 | 1000 | 900 | 80-100% | NORTH SEVENOAKS 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094318170 | B2 to B7 General Industrial and Special Industrial Groups | 1405 | A | Natural Gas | 5 | 2 | Air Conditioning | 2019-06-21 |  | 1 | FALSE | 51.2952 | 0.19394 | SPN-S000000008447 | 13184085000;14593558000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
62 | 73.5 | UNITS D1-D3, NORTH DOWNS BUSINESS PARK, PILGRIMS WAY | SEVENOAKS | TN13 2TL | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 3633.5 | 39111 | GIA | 377500 | NORTH SEVENOAKS 33/11KV | inside-area | 3.37 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 5.77 | 91 | 19 | 803936 | SPN-S000000446089 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3102 | 0.15514 | SPN-S000000008447 | 4591809000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
63 | 73.5 | UNIT 1, BAT AND BALL ENTERPRISE CENTRE, BAT AND BALL ROAD | SEVENOAKS | TN14 5LJ | Sevenoaks |  | Warehouse And Premises | industrial | 2 | 2871.11 | 30904 | GIA | 315000 | NORTH SEVENOAKS 33/11KV | inside-area | 0.76 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 4.56 | 72 | 19 | 812143 | SPN-S000000454017 | 800 | 560 | 60-80% | NORTH SEVENOAKS 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094319892 | B1 Offices and Workshop businesses | 1565 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-06-12 |  | 0.75 | FALSE | 51.2908 | 0.19555 | SPN-S000000008447 | 12079418000;12566310000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
64 | 73.5 | R/O DARENTH HOUSE 60, HIGH STREET | SEVENOAKS | TN14 5PH | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 2427.91 | 26134 | GIA | 96000 | NORTH SEVENOAKS 33/11KV | inside-area | 2.9 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 3.86 | 61 | 19 | 816913 | SPN-S000000446599 | 200 | 60 | 20-40% | NORTH SEVENOAKS 33/11KV | 243 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.313 | 0.18511 | SPN-S000000008447 | 3813434000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
65 | 70.4 | BST PT GND FLR 1ST-3RD FLRS MEDWAY COUNCIL HEADQUARTERS, DOCK ROAD | CHATHAM | ME4 4TR | Medway |  | Offices And Premises | office | 2 | 15718.01 | 169187 | NIA | 1187500 | CHATHAM WEST 33/11KV (NEW) | inside-area | 1.45 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 24.98 | 1100 | 29 | 1644921 | SPN-S000000314643 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 99 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000898373 | B1 Offices and Workshop businesses | 17961 | D | Natural Gas | 4 | 2 | Heating and Mechanical Ventilation | 2016-02-23 |  | 0.6 | FALSE | 51.3891 | 0.52402 | SPN-S000000008508 | 13887013000;13887022000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
66 | 70.4 | SAIL & COLOUR LOFT, CHURCH LANE, THE HISTORIC DOCKYARD | CHATHAM | ME4 4LF | Medway |  | Offices And Premises | office | 1 | 1835.23 | 19754 | GIA | 156000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.2 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 2.92 | 128 | 29 | 1794354 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3949 | 0.52957 | SPN-S000000008508 | 12533713000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
67 | 70.4 | 3RD & 4TH FLRS, MAIN GATE ROAD, FITTED RIGGING HOUSE NORTH, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TZ | Medway |  | Offices And Premises | office | 1 | 1597.12 | 17191 | NIA | 156000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.17 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 2.54 | 112 | 29 | 1796917 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44005591 | D1 Non-residential Institutions - Education | 902 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-04-27 |  | 0.67 | FALSE | 51.3951 | 0.52806 | SPN-S000000008508 | 14992941000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
68 | 70.4 | OSB HOUSE, QUAYSIDE, CHATHAM MARITIME | CHATHAM | ME4 4QZ | Medway |  | Offices And Premises | office | 1 | 1265.49 | 13622 | NIA | 204000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 3.11 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 2.01 | 89 | 29 | 1800486 | SPN-S000000316883 | 315 | 158 | 40-60% | CHATHAM WEST 33/11KV (OLD) | 35 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000899255 | B1 Offices and Workshop businesses | 1588 | C | Natural Gas | 3 |  | Air Conditioning | 2021-11-01 |  | 1 | FALSE | 51.4014 | 0.53778 | SPN-S000000008508 | 9897928000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
69 | 70.4 | 3RD AND 4TH FLRS NORTH, MAIN GATE ROAD, FITTED RIGGING HOUSE NORTH, THE HISTORIC DOCKYARD | CHATHAM | ME4 4TZ | Medway |  | Offices And Premises | office | 1 | 1160.02 | 12486 | NIA | 114000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.17 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 100 | 1.84 | 81 | 29 | 1801622 | SPN-S000000316982 | 315 | 220 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44005591 | D1 Non-residential Institutions - Education | 902 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-04-27 |  | 0.67 | FALSE | 51.3951 | 0.52806 | SPN-S000000008508 | 15135220000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
70 | 70.3 | WEST DESIGN PRODUCTS LTD WEST HOUSE, PENT ROAD, SHEARWAY BUSINESS PARK | FOLKESTONE | CT19 4RJ | Folkestone & Hythe |  | Warehouse And Premises | industrial | 3 | 19498.77 | 209883 | GIA | 1200000 | MOREHALL 132/11KV | inside-area | 0.79 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 30.99 | 487 | 34 | 1358855 | SPN-S000000371398 | 500 | 350 | 60-80% | MOREHALL 132/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50106788 | B1 Offices and Workshop businesses | 463 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2015-06-15 |  | 1 | FALSE | 51.0928 | 1.1492 | SPN-S000000009320 | 11314857000;11314857000;11314857000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
71 | 70.3 | ENBROOK PARK, SANDGATE HIGH STREET | FOLKESTONE | CT20 3SE | Folkestone & Hythe | SAGA GROUP LTD | Offices And Premises | office | 1 | 9259.7 | 99670 | NIA | 905000 | MOREHALL 132/11KV | inside-area | 1.12 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 14.71 | 648 | 34 | 1469068 | SPN-S000000361422 | 500 | 150 | 20-40% | MOREHALL 132/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Offices and Workshop Businesses | 1300 | B | Grid Supplied Electricity | 4 | 3 | Air Conditioning | 2023-06-07 |  | 1 | FALSE | 51.0757 | 1.1491 | SPN-S000000009320 | 968751000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
72 | 70.3 | PLOT A1, SHEARWAY BUSINESS PARK, SHEARWAY ROAD | FOLKESTONE | CT19 4RR | Folkestone & Hythe |  | Offices And Premises | office | 1 | 4758.73 | 51222 | NIA | 865000 | MOREHALL 132/11KV | inside-area | 1 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 7.56 | 333 | 34 | 1517516 | SPN-S000000371088 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0946 | 1.1522 | SPN-S000000009320 | 5562171000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
73 | 70.3 | FOLKESTONE & HYTHE DISTRICT COUNCIL CIVIC CENTRE, CASTLE HILL AVENUE | FOLKESTONE | CT20 2QY | Folkestone & Hythe |  | Offices And Premises | office | 1 | 3135.12 | 33746 | NIA | 226000 | MOREHALL 132/11KV | inside-area | 1.51 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 4.98 | 219 | 34 | 1534992 | SPN-S000000362043 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Offices and Workshop Businesses | 6150 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2022-07-27 |  | 1 | FALSE | 51.0795 | 1.1698 | SPN-S000000009320 | 12980406000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
74 | 70.3 | PALTING HOUSE, TRINITY ROAD | FOLKESTONE | CT20 2TP | Folkestone & Hythe |  | Offices And Premises | office | 1 | 2905.12 | 31270 | NIA | 200000 | MOREHALL 132/11KV | inside-area | 1.39 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 4.62 | 203 | 34 | 1537468 | SPN-S000000362042 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0791 | 1.1675 | SPN-S000000009320 | 8816003000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
75 | 70.3 | 2ND 3RD & 4TH FLRS, CASTLE HOUSE, CASTLE HILL AVENUE | FOLKESTONE | CT20 2FT | Folkestone & Hythe |  | Offices And Premises | office | 1 | 2664.2 | 28677 | NIA | 204000 | MOREHALL 132/11KV | inside-area | 1.41 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 4.23 | 186 | 34 | 1540061 | SPN-S000000362042 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 62 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0781 | 1.1667 | SPN-S000000009320 | 12170710000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
76 | 70.3 | U DRIVE RENTAL, SHORNCLIFFE ROAD | FOLKESTONE | CT20 3PA | Folkestone & Hythe |  | Offices And Premises | office | 1 | 1966.5 | 21167 | OTH | 37750 | MOREHALL 132/11KV | inside-area | 0.27 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 3.12 | 138 | 34 | 1547571 | SPN-S000000363624 | 500 | 150 | 20-40% | MOREHALL 132/11KV | 200 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0846 | 1.154 | SPN-S000000009320 | 2629545000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
77 | 70.3 | J H YOUNG LTD, CAESARS WAY | FOLKESTONE | CT19 4AL | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1702.2 | 18322 | GIA | 132000 | MOREHALL 132/11KV | inside-area | 0.93 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 2.7 | 43 | 34 | 1550416 | SPN-S000000371137 | 500 | 450 | 80-100% | MOREHALL 132/11KV | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0938 | 1.1469 | SPN-S000000009320 | 14845332000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
78 | 70.3 | 1ST FLR 14, SANDGATE ROAD | FOLKESTONE | CT20 1DP | Folkestone & Hythe |  | Store And Premises | industrial | 1 | 1700.8 | 18307 | GIA | 22500 | MOREHALL 132/11KV | inside-area | 2.15 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 2.7 | 43 | 34 | 1550431 | SPN-S000000361989 | 500 | 350 | 60-80% | MOREHALL 132/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | B1 Offices and Workshop businesses | 1413 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-05-29 |  | 0.67 | FALSE | 51.0796 | 1.1798 | SPN-S000000009320 | 7931196000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
79 | 70.3 | ACTION CARPETS LTD, PARK FARM ROAD | FOLKESTONE | CT19 5DU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1623.5 | 17475 | GIA | 104000 | MOREHALL 132/11KV | inside-area | 1.74 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 2.58 | 41 | 34 | 1551263 | SPN-S000000362334 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 43 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50103252 | A1/A2 Retail and Financial/Professional services | 1640 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-03-27 |  | 1 | FALSE | 51.0942 | 1.1716 | SPN-S000000009320 | 7223798000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
80 | 70.3 | UNITS G & H, KINGSMEAD | FOLKESTONE | CT19 5EU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1225 | 13186 | GIA | 73500 | MOREHALL 132/11KV | inside-area | 1.41 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 1.95 | 31 | 34 | 1555552 | SPN-S000000362299 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50103926 | Storage or Distribution | 787 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-03-28 |  | 0.67 | FALSE | 51.0934 | 1.1666 | SPN-S000000009320 | 5502611000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
81 | 70.3 | SELF STORAGE AT ROSS ENTERPRISE CENTRE, ROSS WAY | FOLKESTONE | CT20 3UJ | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1215.7 | 13086 | GIA | 72500 | MOREHALL 132/11KV | inside-area | 0.82 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 1.93 | 30 | 34 | 1555652 | SPN-S000000371608 | 500 | 450 | 80-100% | MOREHALL 132/11KV | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50026106 | B1 Offices and Workshop businesses | 1218 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-03-03 |  | 0.5 | FALSE | 51.081 | 1.1415 | SPN-S000000009320 | 15020658000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
82 | 70.3 | UNIT 5, THREE ACRE SITE, PARK FARM ROAD | FOLKESTONE | CT19 5FG | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1184.14 | 12746 | GIA | 100000 | MOREHALL 132/11KV | inside-area | 1.72 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 1.88 | 30 | 34 | 1555992 | SPN-S000000363478 | 800 | 720 | 80-100% | MOREHALL 132/11KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50033759 | A1/A2 Retail and Financial/Professional services | 524 | D | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2017-05-03 |  | 0.6 | FALSE | 51.0966 | 1.1682 | SPN-S000000009320 | 13183791000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
83 | 69.3 | UNIT 4A, LONDON MEDWAY COMMERCIAL PARK, JAMES SWALLOW WAY | ROCHESTER | ME3 9GX | Medway |  | Warehouse And Premises | industrial | 1 | 5988.87 | 64464 | GIA | 620000 | KINGSNORTH GRID 11KV | inside-area | 1.55 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 9.52 | 150 | 12 | 1269204 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4335 | 0.60735 | SPN-S000000009525 | 11707491000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
84 | 69.3 | KINGSNORTH | ROCHESTER | ME3 9LY | Medway | B P INTERNATIONAL LTD | Store And Premises | industrial | 1 | 4881.4 | 52543 | GIA | 211000 | KINGSNORTH GRID 11KV | inside-area | 0.98 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 7.76 | 122 | 12 | 1281125 | SPN-R000000952509-000-006Z | 100 | 10 | 0-20% | SHARNAL STREET 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4304 | 0.5986 | SPN-S000000009525 | 167400147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
85 | 69.3 | TANKERWASTE (KENT) LTD, KINGSNORTH INDUSTRIAL ESTATE | ROCHESTER | ME3 9ND | Medway | TANKERWASTE (KENT) LTD | Storage Depot And Premises | industrial | 1 | 3500 | 37674 | OTH | 71000 | KINGSNORTH GRID 11KV | inside-area | 0.84 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 5.56 | 88 | 12 | 1295994 | SPN-R000000952509-000-006Z | 100 | 10 | 0-20% | SHARNAL STREET 33/11KV | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4291 | 0.59841 | SPN-S000000009525 | 399343147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
86 | 69.3 | BUILDINGS 212 & 213, KINGSNORTH INDUSTRIAL ESTATE | ROCHESTER | ME3 9ND | Medway | IKO PLC | Warehouses And Premises | industrial | 1 | 3255.07 | 35037 | GIA | 185000 | KINGSNORTH GRID 11KV | inside-area | 0.84 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 5.17 | 81 | 12 | 1298631 | SPN-R000000952509-000-006Z | 100 | 10 | 0-20% | SHARNAL STREET 33/11KV | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4291 | 0.59841 | SPN-S000000009525 | 5359709000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
87 | 69.3 | UNIT 7A, LONDON MEDWAY COMMERCIAL PARK, JAMES SWALLOW WAY | ROCHESTER | ME3 9GX | Medway |  | Warehouse And Premises | industrial | 1 | 3199.92 | 34444 | GIA | 57000 | KINGSNORTH GRID 11KV | inside-area | 1.55 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 5.09 | 80 | 12 | 1299224 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4335 | 0.60735 | SPN-S000000009525 | 13002238000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
88 | 69.3 | UNIT 6, KINGSNORTH INDUSTRIAL ESTATE | ROCHESTER | ME3 9ND | Medway |  | Warehouse And Premises | industrial | 1 | 2342.93 | 25219 | GIA | 173000 | KINGSNORTH GRID 11KV | inside-area | 0.84 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 3.72 | 59 | 12 | 1308449 | SPN-R000000952509-000-006Z | 100 | 10 | 0-20% | SHARNAL STREET 33/11KV | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44041196 | General Industrial and Special Industrial Groups | 515 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-03-27 |  | 1 | FALSE | 51.4291 | 0.59841 | SPN-S000000009525 | 10797286000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
89 | 69.1 | SAINSBURYS SUPERMARKET (WESTWOOD CROSS THANET), DADSON WAY | RAMSGATE | CT12 5FJ | Thanet |  | Superstore And Premises | bigbox | 1 | 11438.99 | 123128 | GIA | 1780000 | MANSTON 33/11KV | inside-area | 2.03 | Richborough Grid | Richborough | East Kent Zone | 25.6 | primary | 25.6 | Green | 38.1 | 2.4 | Thermal | 9 | 41 | 0 | 50 | 31.1 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.6 | 28.8 | Summer | 92.3611 | 26.6 | Green (Over 5% headroom) | 182531 | 100 | 18.18 | 1030 | 4 | 248389 | SPN-S000000342019 | 800 | 560 | 60-80% | THANET 33/11KV | 331 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013308364 | Retail/Financial and Professional Services | 13012 | B | Grid Supplied Electricity | 4 |  | Heating and Mechanical Ventilation | 2025-04-25 |  | 0.67 | FALSE | 51.3563 | 1.3936 | SPN-S000000008616 | 15075299000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
90 | 68.9 | AIRPORT WORKS, MAIDSTONE ROAD | ROCHESTER | ME1 2XX | Medway | BAE SYSTEM AVIONICS LTD | Factory And Premises | industrial | 1 | 51255.55 | 551710 | GIA | 1030000 | CHATHAM WEST 33/11KV (NEW) | inside-area | 2.39 | Medway Grid | Kingsnorth | Mid Kent Zone | 34.8 | bsp | 41.7 | Green | 72 | 20 | Thermal | 0 | 0 | 2 | 0 | 47.9 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | Green (Over 5% headroom) | 248128 | 45 | 81.45 | 3075 | 29 | 1262398 | SPN-S000000324254 | 800 | 560 | 60-80% | MEDWAY 33/11KV | 159 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3572 | 0.5031 | SPN-S000000008508 | 2849213000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
91 | 68.5 | GEBERIT TERRAIN LTD, NEW HYTHE BUSINESS PARK, COLLEGE ROAD, BELLINGHAM WAY | AYLESFORD | ME20 7PJ | Tonbridge & Malling |  | Factory And Premises | industrial | 2 | 35146.72 | 378316 | GIA | 1550000 | NEW HYTHE 33/11kV | inside-area | 0.79 | Burham Grid | Northfleet | Mid Kent Zone | 34.5 | primary | 34.5 | Green | 37.3 |  |  | 0 | 0 | 0 | 0 | 32 |  |  |  | 0 | 97 | GREEN | 13 | 552.7 | 3 | 37.3 | 29.4 | Winter | 92.4933 | 34.5 | Green (Over 5% headroom) | 245989 | 65 | 55.85 | 2109 | 2 | 291727 | SPN-S000000394880 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 287 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.308 | 0.45214 | SPN-S000000008682 | 4362271000;4362271000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
92 | 68.5 | J SAINSBURY PLC, OTFORD ROAD | SEVENOAKS | TN14 5EG | Sevenoaks |  | Superstore And Premises | bigbox | 1 | 10120.86 | 108940 | GIA | 2080000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.04 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 16.08 | 911 | 19 | 734107 | SPN-S000000446571 | 300 | 90 | 20-40% | NORTH SEVENOAKS 33/11KV | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2957 | 0.19206 | SPN-S000000008447 | 14849528000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
93 | 68.5 | UNIT A, RIVERSIDE RETAIL PARK, OLD OTFORD ROAD | SEVENOAKS | TN14 5DE | Sevenoaks |  | Retail Warehouse And Premises | bigbox | 1 | 3907.72 | 42062 | GIA | 467500 | NORTH SEVENOAKS 33/11KV | inside-area | 0.68 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 6.21 | 352 | 19 | 800985 | SPN-S000000446564 | 500 | 250 | 40-60% | NORTH SEVENOAKS 33/11KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035184078 | Retail/Financial and Professional Services | 2383 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-07-11 |  | 0.5 | FALSE | 51.2926 | 0.1907 | SPN-S000000008447 | 407124148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
94 | 68.5 | UNIT 1, OTFORD ROAD | SEVENOAKS | TN14 5EG | Sevenoaks |  | Retail Warehouse And Premises | bigbox | 1 | 2397.45 | 25806 | GIA | 407500 | NORTH SEVENOAKS 33/11KV | inside-area | 1.04 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 3.81 | 216 | 19 | 817241 | SPN-S000000446571 | 300 | 90 | 20-40% | NORTH SEVENOAKS 33/11KV | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062621953 | A1/A2 Retail and Financial/Professional services | 1655 | A | Grid Supplied Electricity | 5 | 1 | Heating and Mechanical Ventilation | 2019-02-15 |  | 0.5 | FALSE | 51.2957 | 0.19206 | SPN-S000000008447 | 3462747000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
95 | 68.5 | WOLFE GARAGE, SEVENOAKS ROAD | SEVENOAKS | TN14 5PA | Sevenoaks |  | Car Showroom And Premises | bigbox | 1 | 2268.78 | 24421 | GIA | 312500 | NORTH SEVENOAKS 33/11KV | inside-area | 2.48 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 3.61 | 204 | 19 | 818626 | SPN-S000000446582 | 500 | 350 | 60-80% | NORTH SEVENOAKS 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002016682 | A1/A2 Retail and Financial/Professional services | 2225 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-06-12 |  | 0.5 | FALSE | 51.3092 | 0.19052 | SPN-S000000008447 | 199729148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
96 | 67.7 | LOWFIELD DISTRIBUTION, SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HB | Gravesham | BLOCK K | Cold Store Warehouses & Premises | industrial | 1 | 12922.6 | 139098 | GIA | 1030000 | EBBSFLEET 33/11KV | inside-area | 1.71 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 20.54 | 1551 | 7 | 323302 | SPN-S000000314021 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 112 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4343 | 0.33226 | SPN-S000000008627 | 389339147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
97 | 67.7 | SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HN | Gravesham | HT WEBB & CO LTD | Warehouses Chill Stores & Premises | industrial | 2 | 12187.63 | 131186 | GIA | 1100000 | EBBSFLEET 33/11KV | inside-area | 1.54 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 19.37 | 305 | 7 | 331214 | SPN-S000000314022 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012025487 | B2 to B7 General Industrial and Special Industrial Groups | 342 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-04-11 |  | 1 | FALSE | 51.4365 | 0.33309 | SPN-S000000008627 | 744965000;744965000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
98 | 67.7 | UNITS W & X, SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HB | Gravesham |  | Warehouse And Premises | industrial | 1 | 4644.71 | 49995 | GIA | 397500 | EBBSFLEET 33/11KV | inside-area | 1.71 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 7.38 | 116 | 7 | 412405 | SPN-S000000314021 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 112 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4343 | 0.33226 | SPN-S000000008627 | 10452060000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
99 | 67.7 | GRAVESHAM BOROUGH COUNCIL DEPOT, SPRINGHEAD ROAD | GRAVESEND | DA11 8HW | Gravesham |  | Storage Depot And Premises | industrial | 1 | 4393.96 | 47296 | GIA | 184000 | EBBSFLEET 33/11KV | inside-area | 1.77 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 6.98 | 110 | 7 | 415104 | SPN-S000000314361 | 315 | 158 | 40-60% | EBBSFLEET 33/11KV | 272 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4352 | 0.33568 | SPN-S000000008627 | 13700147000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
100 | 67.7 | UNIT U, SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HJ | Gravesham |  | Warehouse Offices And Premises | industrial | 1 | 2749 | 29590 | GIA | 255000 | EBBSFLEET 33/11KV | inside-area | 1.66 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 4.37 | 192 | 7 | 432810 | SPN-S000000314022 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062310904 | B1 Offices and Workshop businesses | 2715 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-06-23 |  | 1 | FALSE | 51.435 | 0.33279 | SPN-S000000008627 | 167536147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
101 | 67.7 | UNIT S, SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HJ | Gravesham |  | Factory And Premises | industrial | 1 | 2008.33 | 21617 | GIA | 202000 | EBBSFLEET 33/11KV | inside-area | 1.66 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 3.19 | 120 | 7 | 440783 | SPN-S000000314022 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062310903 | B1 Offices and Workshop businesses | 1993 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2012-04-20 |  | 1 | FALSE | 51.435 | 0.33279 | SPN-S000000008627 | 167534147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
102 | 67.3 | SAINSBURYS, PARK FARM ROAD | FOLKESTONE | CT19 5GA | Folkestone & Hythe |  | Superstore And Premises | bigbox | 2 | 14493.96 | 156012 | GIA | 3260000 | MOREHALL 132/11KV | inside-area | 1.49 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 23.03 | 1304 | 34 | 1412726 | SPN-S000000364294 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50116835 | Retail/Financial and Professional Services | 103 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2026-04-27 |  | 1 | FALSE | 51.0951 | 1.1658 | SPN-S000000009320 | 14849226000;14849226000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
103 | 65.7 | FUJI SEAL EUROPE LTD, SCIMITAR CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0RJ | Medway |  | Warehouse And Premises | industrial | 1 | 9527.35 | 102551 | GIA | 575000 | RAINHAM MARK 33/11KV | inside-area | 0.49 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 15.14 | 238 | 37 | 2285694 | SPN-S000000316902 | 315 | 158 | 40-60% | RAINHAM MARK 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3653 | 0.57245 | SPN-S000000008525 | 10004425000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
104 | 65.7 | FREIGHT SERVICES FACILITY EAST, LOWER ROAD WEST, EASTERN DOCKS | DOVER | CT16 1JA | Dover |  | Warehouse And Premises | industrial | 1 | 8934.11 | 96166 | GIA | 565000 | DOVER 33/11KV | inside-area | 1.66 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 14.2 | 223 | 39 | 1288255 | SPN-R000000839108-000-189Z | 100 | 70 | 60-80% | DOVER 33/11KV | 353 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1292 | 1.3349 | SPN-S000000008391 | 11909890000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
105 | 65.7 | BATLEYS CASH & CARRY, COURTENEY ROAD | GILLINGHAM | ME8 0RT | Medway |  | Warehouse And Premises | industrial | 1 | 8272.79 | 89047 | GIA | 715000 | RAINHAM MARK 33/11KV | inside-area | 0.15 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 13.15 | 207 | 37 | 2299198 | SPN-S000000311994 | 750 | 675 | 80-100% | RAINHAM MARK 33/11KV | 200 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000901222 | A1/A2 Retail and Financial/Professional services | 10922 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-05-13 |  | 1 | FALSE | 51.3633 | 0.58046 | SPN-S000000008525 | 7013098000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
106 | 65.7 | WOZAIR LTD, GROSVENOR ROAD, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0SA | Medway |  | Factory And Premises | industrial | 1 | 7922 | 85272 | GIA | 550000 | RAINHAM MARK 33/11KV | inside-area | 0.84 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 12.59 | 475 | 37 | 2302973 | SPN-S000000316804 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.367 | 0.56829 | SPN-S000000008525 | 10058861000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
107 | 65.7 | PUSTERLA WAREHOUSE, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 2 | 7825.56 | 84234 | GIA | 434500 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 12.44 | 196 | 39 | 1300187 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1313 | 1.2799 | SPN-S000000008391 | 15158855000;11247945000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
108 | 65.7 | MEDCARE HOUSE, CENTURION CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0SB | Medway |  | Factory And Premises | industrial | 1 | 7441.74 | 80102 | GIA | 550000 | RAINHAM MARK 33/11KV | inside-area | 0.73 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 11.83 | 447 | 37 | 2308143 | SPN-S000000312286 | 500 | 350 | 60-80% | RAINHAM MARK 33/11KV | 314 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000900112 | B8 Storage or Distribution | 13661 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-15 |  | 1 | FALSE | 51.3659 | 0.5691 | SPN-S000000008525 | 402561147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
109 | 65.7 | UNITS 2-5, CHIEFTAIN CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PP | Medway | ROYAL MAIL PARCELFORCE | Warehouse And Premises | industrial | 2 | 6677.05 | 71871 | GIA | 515000 | RAINHAM MARK 33/11KV | inside-area | 0.27 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 10.61 | 167 | 37 | 2316374 | SPN-S000000313856 | 1000 | 700 | 60-80% | RAINHAM MARK 33/11KV | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200003621242 | Storage or Distribution | 508 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-02-17 |  | 1 | FALSE | 51.3653 | 0.57798 | SPN-S000000008525 | 8308201000;398823147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
110 | 65.7 | WAREHOUSE & OFFICES OFF, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Warehouse And Premises | industrial | 1 | 6503 | 69998 | GIA | 735000 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 10.33 | 163 | 37 | 2318247 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | B8 Storage or Distribution | 3839 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-09-18 |  | 0.67 | FALSE | 51.3645 | 0.57398 | SPN-S000000008525 | 9217536000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
111 | 65.7 | DERFSHAW LTD, BREDGAR ROAD | GILLINGHAM | ME8 6PL | Medway |  | Factory And Premises | industrial | 1 | 5504 | 59245 | GIA | 250000 | RAINHAM MARK 33/11KV | inside-area | 2 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 8.75 | 330 | 37 | 2329000 | SPN-S000000311984 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3808 | 0.57991 | SPN-S000000008525 | 1380305000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
112 | 65.7 | EASTCOURT WORKS, BEECHINGS WAY | GILLINGHAM | ME8 6XS | Medway |  | Workshop And Premises | industrial | 1 | 5474.68 | 58929 | GIA | 460000 | RAINHAM MARK 33/11KV | inside-area | 1.68 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 8.7 | 246 | 37 | 2329316 | SPN-S000000312038 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3744 | 0.59422 | SPN-S000000008525 | 15030887000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
113 | 65.7 | LINEAGE, VALENTINE CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0QR | Medway |  | Cold Stores And Premises | industrial | 1 | 5367.06 | 57770 | GIA | 357500 | RAINHAM MARK 33/11KV | inside-area | 0.49 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 8.53 | 644 | 37 | 2330475 | SPN-S000000314028 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 106 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000901277 | Storage or Distribution | 2416 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-03-28 |  | 0.67 | FALSE | 51.3666 | 0.5747 | SPN-S000000008525 | 14801735000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
114 | 65.7 | LOK N STORE, COURTENEY ROAD | GILLINGHAM | ME8 0RT | Medway |  | Warehouse And Premises | industrial | 1 | 4950.43 | 53286 | GIA | 243000 | RAINHAM MARK 33/11KV | inside-area | 0.15 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 7.87 | 124 | 37 | 2334959 | SPN-S000000311994 | 750 | 675 | 80-100% | RAINHAM MARK 33/11KV | 200 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3633 | 0.58046 | SPN-S000000008525 | 11257631000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
115 | 65.7 | UNIT 1, DUBRIS CLOSE, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 3FJ | Dover |  | Warehouse And Premises | industrial | 1 | 4908.24 | 52832 | GIA | 187000 | DOVER 33/11KV | inside-area | 2.65 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 7.8 | 123 | 39 | 1331589 | SPN-S000000371388 | 315 | 158 | 40-60% | DOVER 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034891786 | A1/A2 Retail and Financial/Professional services | 5041 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2018-08-08 |  | 0.67 | FALSE | 51.1526 | 1.3043 | SPN-S000000008391 | 11841672000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
116 | 65.7 | 1, PORT ZONE, PALMERSTON ROAD, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 3NF | Dover |  | Cold Store And Premises | industrial | 1 | 4343.54 | 46753 | GIA | 470000 | DOVER 33/11KV | inside-area | 2.68 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 6.9 | 521 | 39 | 1337668 | SPN-S000000371107 | 1000 | 700 | 60-80% | DOVER 33/11KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034880247 | Storage or Distribution | 4441 | B | Natural Gas | 3 |  | Air Conditioning | 2025-07-23 |  | 1 | FALSE | 51.1481 | 1.2875 | SPN-S000000008391 | 1744407000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
117 | 65.7 | ASTRA PARK, COURTENEY ROAD | GILLINGHAM | ME8 0EZ | Medway |  | Warehouse And Premises | industrial | 2 | 4222.14 | 45447 | GIA | 403000 | RAINHAM MARK 33/11KV | inside-area | 0.25 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 6.71 | 106 | 37 | 2342798 | SPN-S000000311994 | 750 | 675 | 80-100% | RAINHAM MARK 33/11KV | 38 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44013191 | B1 Offices and Workshop businesses | 204 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-11-10 |  | 1 | FALSE | 51.3648 | 0.58016 | SPN-S000000008525 | 7388367000;7388367000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
118 | 65.7 | THERMOSTATIC UNIT 6, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Cold Store And Premises | industrial | 1 | 4062.3 | 43726 | GIA | 285000 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 6.46 | 487 | 37 | 2344519 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | B8 Storage or Distribution | 3839 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-09-18 |  | 0.67 | FALSE | 51.3645 | 0.57398 | SPN-S000000008525 | 14801732000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
119 | 65.7 | JAMES WELLESLEY LTD, MOTNEY HILL ROAD | GILLINGHAM | ME8 7TZ | Medway |  | Factory And Premises | industrial | 1 | 3544.35 | 38151 | GIA | 122000 | RAINHAM MARK 33/11KV | inside-area | 2.95 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 5.63 | 213 | 37 | 2350094 | SPN-S000000312089 | 300 | 90 | 20-40% | RAINHAM MARK 33/11KV | 118 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062396436 | B2 to B7 General Industrial and Special Industrial Groups | 2842 | E | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2018-02-19 |  | 0.5 | FALSE | 51.3762 | 0.61518 | SPN-S000000008525 | 14156079000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
120 | 65.7 | UNITS 1-3, BEECHINGS WAY INDUSTRIAL ESTATE, INVICTA BUSINESS CENTRE, BEECHINGS WAY | GILLINGHAM | ME8 6PG | Medway |  | Warehouse And Premises | industrial | 1 | 3491.8 | 37585 | GIA | 188000 | RAINHAM MARK 33/11KV | inside-area | 1.98 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 5.55 | 87 | 37 | 2350660 | SPN-S000000311984 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44005374 | Storage or Distribution | 3915 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-03-12 |  | 0.75 | FALSE | 51.3807 | 0.57902 | SPN-S000000008525 | 5682613000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
121 | 65.7 | A & S SELF STORAGE UNIT 4, OLD PARK | DOVER | CT16 2HQ | Dover |  | Store And Premises | industrial | 1 | 3449.61 | 37131 | GIA | 153000 | DOVER 33/11KV | inside-area | 2.79 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 5.48 | 86 | 39 | 1347290 | SPN-S000000371561 | 500 | 350 | 60-80% | DOVER 33/11KV | 225 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.15 | 1.2889 | SPN-S000000008391 | 525417145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
122 | 65.7 | 21A, BAILEY COURT, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Factory And Premises | industrial | 1 | 3380.74 | 36390 | GIA | 312500 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 5.37 | 203 | 37 | 2351855 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000901172 | B2 to B7 General Industrial and Special Industrial Groups | 3458 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-10-23 |  | 1 | FALSE | 51.3645 | 0.57398 | SPN-S000000008525 | 389347147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
123 | 65.7 | WAREHOUSE A WAREHOUSE B AND OFFICE C BIG OFFICES WHITECLIFF HOUSE, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 1 | 3247.5 | 34956 | GIA | 199000 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 5.16 | 81 | 39 | 1349465 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Storage or Distribution | 861 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-03-21 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 15096938000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
124 | 65.7 | 15, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PU | Medway |  | Warehouse And Premises | industrial | 1 | 3213.12 | 34586 | GIA | 337500 | RAINHAM MARK 33/11KV | inside-area | 0.52 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 5.11 | 80 | 37 | 2353659 | SPN-S000000314028 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3674 | 0.57637 | SPN-S000000008525 | 7229788000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
125 | 65.7 | UNIT 4, MEDWAY DISTRIBUTION CENTRE, COURTENEY ROAD | GILLINGHAM | ME8 0RR | Medway |  | Builders Merchants And Premises; Warehouse And Premises | industrial | 2 | 3192.82 | 34367 | GIA | 322000 | RAINHAM MARK 33/11KV | inside-area | 0.28 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 5.07 | 287 | 37 | 2353878 | SPN-S000000311101 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3624 | 0.57448 | SPN-S000000008525 | 2476549000;256880000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
126 | 65.7 | 18-20, POULTON CLOSE | DOVER | CT17 0HL | Dover | APOLLO MOTOR COMPANY | Vehicle Repair Workshop And Premises; Warehouse And Premises | industrial | 2 | 2908.66 | 31309 | GIA | 181500 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 4.62 | 131 | 39 | 1353112 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062290064 | General Industrial and Special Industrial Groups | 683 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-12-23 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 13091355000;12674584000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
127 | 65.7 | UNITS 1-4 BOWEN HOUSE INDUSTRIAL ESTATE, BREDGAR ROAD | GILLINGHAM | ME8 6PG | Medway |  | Workshop And Premises | industrial | 1 | 2484.67 | 26745 | GIA | 99500 | RAINHAM MARK 33/11KV | inside-area | 1.98 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.95 | 112 | 37 | 2361500 | SPN-S000000311984 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3807 | 0.57902 | SPN-S000000008525 | 12657862000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
128 | 65.7 | PHASE 24, GROSVENOR ROAD, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0SA | Medway |  | Factory And Premises | industrial | 1 | 2470.04 | 26587 | GIA | 233000 | RAINHAM MARK 33/11KV | inside-area | 0.84 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.93 | 148 | 37 | 2361658 | SPN-S000000316804 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000900375 | General Industrial and Special Industrial Groups | 4368 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-03-28 |  | 0.67 | FALSE | 51.367 | 0.56829 | SPN-S000000008525 | 8288165000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
129 | 65.7 | 19, VALENTINE CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PU | Medway |  | Warehouse And Premises | industrial | 1 | 2409 | 25930 | GIA | 223000 | RAINHAM MARK 33/11KV | inside-area | 0.52 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.83 | 60 | 37 | 2362315 | SPN-S000000314028 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3674 | 0.57637 | SPN-S000000008525 | 389688147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
130 | 65.7 | R T QUAIFE ENGINEERING LTD, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Factory And Premises | industrial | 1 | 2366.83 | 25476 | GIA | 215000 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.76 | 142 | 37 | 2362769 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062395976 | General Industrial and Special Industrial Groups | 2583 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-06-13 |  | 1 | FALSE | 51.3645 | 0.57398 | SPN-S000000008525 | 6792543000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
131 | 65.7 | VBH HOUSE, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0WG | Medway |  | Warehouse And Premises | industrial | 1 | 2317.2 | 24942 | GIA | 216000 | RAINHAM MARK 33/11KV | inside-area | 0.64 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.68 | 58 | 37 | 2363303 | SPN-S000000316954 | 500 | 350 | 60-80% | RAINHAM MARK 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062395921 | B8 Storage or Distribution | 1172 | C | Natural Gas | 5 | 1 | Heating and Natural Ventilation | 2022-03-04 |  | 1 | FALSE | 51.3679 | 0.57399 | SPN-S000000008525 | 404152147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
132 | 65.7 | MIKE BEER TRANSPORT LTD, PORT ZONE, MENZIES ROAD, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 2HQ | Dover |  | Vehicle Repair Workshop, Office And Premises | industrial | 1 | 2302.56 | 24785 | GIA | 149000 | DOVER 33/11KV | inside-area | 2.79 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 3.66 | 104 | 39 | 1359636 | SPN-S000000371561 | 500 | 350 | 60-80% | DOVER 33/11KV | 225 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034877407 | B2 to B7 General Industrial and Special Industrial Groups | 3643 | C | Natural Gas | 3 | 1 | Air Conditioning | 2020-10-05 |  | 1 | FALSE | 51.15 | 1.2889 | SPN-S000000008391 | 2869414000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
133 | 65.7 | UNIT 1, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Factory And Premises | industrial | 1 | 2253.7 | 24259 | GIA | 210000 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.58 | 135 | 37 | 2363986 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | B8 Storage or Distribution | 3839 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-09-18 |  | 0.67 | FALSE | 51.3645 | 0.57398 | SPN-S000000008525 | 9771707000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
134 | 65.7 | PENTLAND HOUSE, SARACEN CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PU | Medway |  | Warehouse And Premises | industrial | 1 | 2183.6 | 23504 | GIA | 209000 | RAINHAM MARK 33/11KV | inside-area | 0.52 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 3.47 | 55 | 37 | 2364741 | SPN-S000000314028 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3674 | 0.57637 | SPN-S000000008525 | 408460147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
135 | 65.7 | EUROMOTIVE PART WAREHOUSE, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 1 | 2154.59 | 23192 | GIA | 132000 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 3.42 | 54 | 39 | 1361229 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1313 | 1.2799 | SPN-S000000008391 | 11247949000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
136 | 65.7 | WAREHOUSE B BIG OFFICES WHITECLIFF HOUSE, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 1 | 1965 | 21151 | GIA | 127000 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 3.12 | 49 | 39 | 1363270 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Storage or Distribution | 2122 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-03-21 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 15096923000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
137 | 65.7 | CHARLTON BODIES LTD, PORT ZONE, MENZIES ROAD, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 2HQ | Dover |  | Factory And Premises | industrial | 1 | 1866.57 | 20092 | GIA | 155000 | DOVER 33/11KV | inside-area | 2.79 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.97 | 112 | 39 | 1364329 | SPN-S000000371561 | 500 | 350 | 60-80% | DOVER 33/11KV | 225 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.15 | 1.2889 | SPN-S000000008391 | 2856770000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
138 | 65.7 | HAMMOND HOUSE & UNIT 12, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Factory And Premises | industrial | 1 | 1861.26 | 20034 | GIA | 117000 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.96 | 112 | 39 | 1364387 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062290100 | Offices and Workshop Businesses | 126 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-01-23 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 12523826000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
139 | 64.3 | KENT REPORTING CENTRE 7, SHORNCLIFFE ROAD | FOLKESTONE | CT20 2SH | Folkestone & Hythe |  | Offices And Premises | office | 1 | 1448.15 | 15588 | NIA | 80000 | MOREHALL 132/11KV | inside-area | 1.54 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 2.3 | 101 | 34 | 1553150 | SPN-S000000361382 | 750 | 375 | 40-60% | MOREHALL 132/11KV | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.081 | 1.1713 | SPN-S000000009320 | 3778650000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
140 | 64.3 | BOUVERIE PLACE | FOLKESTONE | CT20 1AU | Folkestone & Hythe | POST OFFICE | Post Office And Premises | office | 1 | 1163.4 | 12523 | NIA | 72000 | MOREHALL 132/11KV | inside-area | 2.03 | Folkestone Total | Sellindge | East Kent Zone | 30.2 | bsp | 40.7 | Green | 76.2 | 22 | Thermal | 0 | 1.6 | 0 | 1.6 | 50 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | Green (Over 5% headroom) | 215330 | 100 | 1.85 | 81 | 34 | 1556215 | SPN-S000000371345 | 1000 | 700 | 60-80% | MOREHALL 132/11KV | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50107234 | A1/A2 Retail and Financial/Professional services | 1792 | B | Grid Supplied Electricity | 4 | 3 | Air Conditioning | 2018-04-21 |  | 1 | FALSE | 51.0798 | 1.1781 | SPN-S000000009320 | 77754145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
141 | 64.3 | HOMELEIGH, RATCLIFFE HIGHWAY | ROCHESTER | ME3 8QD | Medway |  | Garden Centre Nursery And Premises | bigbox | 1 | 2743.12 | 29527 | NIA | 34250 | KINGSNORTH GRID 11KV | inside-area | 2.75 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 4.36 | 247 | 12 | 1304141 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4329 | 0.55994 | SPN-S000000009525 | 157885147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
142 | 64.1 | SAGA CALL CENTRE, EUROKENT BUSINESS PARK, HOLMES WAY | RAMSGATE | CT12 5AE | Thanet |  | Offices And Premises | office | 1 | 5041.35 | 54265 | NIA | 535000 | MANSTON 33/11KV | inside-area | 1.61 | Richborough Grid | Richborough | East Kent Zone | 25.6 | primary | 25.6 | Green | 38.1 | 2.4 | Thermal | 9 | 41 | 0 | 50 | 31.1 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.6 | 28.8 | Summer | 92.3611 | 26.6 | Green (Over 5% headroom) | 182531 | 100 | 8.01 | 353 | 4 | 317252 | SPN-S000000343480 | 1000 | 500 | 40-60% | THANET 33/11KV | 152 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100061137212 | Storage or Distribution | 5082 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-07-26 |  | 0.67 | FALSE | 51.3554 | 1.3877 | SPN-S000000008616 | 2931602000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
143 | 63.5 | GND FLR AT 160, LONDON ROAD | SEVENOAKS | TN13 1BT | Sevenoaks |  | Offices And Premises | office | 2 | 9353.82 | 100684 | NIA | 1495000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.04 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 14.86 | 655 | 19 | 742363 | SPN-S000000446939 | 500 | -50 | -20-0% |  | 219 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013772079 | B1 Offices and Workshop businesses | 4299 | E | Natural Gas | 3 |  | Air Conditioning | 2019-05-14 |  | 1 | FALSE | 51.2781 | 0.18169 | SPN-S000000008447 | 12161520000;12161522000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
144 | 63.5 | CONWAY HOUSE, VESTRY ROAD | SEVENOAKS | TN14 5EL | Sevenoaks |  | Offices And Premises | office | 1 | 3589.77 | 38640 | NIA | 550000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.47 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 5.7 | 251 | 19 | 804407 | SPN-S000000446574 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000848577 | Offices and Workshop Businesses | 3740 | C | Natural Gas | 4 | 3 | Air Conditioning | 2024-05-13 |  | 1 | FALSE | 51.2988 | 0.19589 | SPN-S000000008447 | 10780103000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
145 | 63.5 | QUAIFE ENGINEERING, VESTRY ROAD | SEVENOAKS | TN14 5EL | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1713.7 | 18446 | GIA | 181000 | NORTH SEVENOAKS 33/11KV | inside-area | 1.47 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 2.72 | 77 | 19 | 824601 | SPN-S000000446574 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062548340 | Storage or Distribution | 534 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-11-18 |  | 0.5 | FALSE | 51.2988 | 0.19589 | SPN-S000000008447 | 2361393000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
146 | 63.5 | STATION WORKS, RYE LANE | SEVENOAKS | TN14 5HD | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1660.36 | 17872 | GIA | 85500 | NORTH SEVENOAKS 33/11KV | inside-area | 1.14 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 2.64 | 42 | 19 | 825175 | SPN-S000000451661 | 500 | 350 | 60-80% | NORTH SEVENOAKS 33/11KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062621464 | General Industrial and Special Industrial Groups | 2351 | C | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2024-07-02 |  | 1 | FALSE | 51.2939 | 0.17432 | SPN-S000000008447 | 15104386000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
147 | 63.5 | UNIT 2-3A, MOREWOOD CLOSE | SEVENOAKS | TN13 2HU | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1248.37 | 13437 | GIA | 106000 | NORTH SEVENOAKS 33/11KV | inside-area | 1 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 1.98 | 31 | 19 | 829610 | SPN-S000000451218 | 500 | 350 | 60-80% | NORTH SEVENOAKS 33/11KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013770378 | B1 Offices and Workshop businesses | 1114 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-09-22 |  | 1 | FALSE | 51.2801 | 0.1773 | SPN-S000000008447 | 7679558000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
148 | 63.5 | CHANNEL COMMERCIALS, PILGRIMS WAY | SEVENOAKS | TN13 2TL | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1062.47 | 11436 | GIA | 116000 | NORTH SEVENOAKS 33/11KV | inside-area | 3.37 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 1.69 | 48 | 19 | 831611 | SPN-S000000446089 | 1000 | 700 | 60-80% | NORTH SEVENOAKS 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3102 | 0.15514 | SPN-S000000008447 | 6054976000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
149 | 63.5 | THE TEA SHED AT CONEY SHAW FARM, KEMSING ROAD | SEVENOAKS | TN15 6NN | Tonbridge & Malling |  | Factory And Premises | industrial | 1 | 1017.62 | 10954 | GIA | 91000 | NORTH SEVENOAKS 33/11KV | inside-area | 6.29 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 1.62 | 61 | 19 | 832093 | SPN-S000000447518 | 500 | 450 | 80-100% | NORTH SEVENOAKS 33/11KV | 151 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10092972567 | B2 to B7 General Industrial and Special Industrial Groups | 1087 | A | Biomass | 4 |  | Heating and Natural Ventilation | 2019-07-04 |  | 0.83 | FALSE | 51.3067 | 0.27125 | SPN-S000000008447 | 10719350000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
150 | 61.3 | H E SERVICES, WHITEWALL ROAD | ROCHESTER | ME2 4DZ | Medway |  | Factory And Premises | industrial | 1 | 11775.44 | 126750 | GIA | 495000 | STROOD 132/11KV | inside-area | 0.82 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 90 | 18.71 | 707 | 62 | 3214708 | SPN-S000000316841 | 1000 | 700 | 60-80% | STROOD 132/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3987 | 0.51136 | SPN-S000000009948 | 7782634000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
151 | 61.3 | MEDWAY 1, ANTHONYS WAY, MEDWAY CITY ESTATE | ROCHESTER | ME2 4DN | Medway |  | Warehouse And Premises | industrial | 1 | 10986.05 | 118253 | GIA | 1030000 | STROOD 132/11KV | inside-area | 1.22 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 96 | 17.46 | 275 | 62 | 3223205 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3979 | 0.51697 | SPN-S000000009948 | 3629153000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
152 | 61.3 | EUROPA AND JENNER HOUSE, TRIDENT CLOSE | ROCHESTER | ME2 4ER | Medway | MIQ LOGISTICS | Warehouse And Premises | industrial | 1 | 10480.25 | 112808 | GIA | 555000 | STROOD 132/11KV | inside-area | 1.16 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 16.65 | 262 | 62 | 3228650 | SPN-S000000316763 | 1000 | 300 | 20-40% | STROOD 132/11KV | 179 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44027755 | B2 to B7 General Industrial and Special Industrial Groups | 5502 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-09-29 |  | 0.67 | FALSE | 51.3952 | 0.51453 | SPN-S000000009948 | 8419883000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
153 | 61.3 | MORGAN & CO (STROOD) LTD, TEMPLE MARSH ESTATE, KNIGHT ROAD | ROCHESTER | ME2 2BA | Medway |  | Factory And Premises | industrial | 1 | 10143.1 | 109179 | GIA | 302500 | STROOD 132/11KV | inside-area | 1.46 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 16.12 | 609 | 62 | 3232279 | SPN-S000000311110 | 500 | 150 | 20-40% | STROOD 132/11KV | 180 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3885 | 0.48973 | SPN-S000000009948 | 5697360000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
154 | 61.3 | PELICAN HOUSE, CLIPPER CLOSE | ROCHESTER | ME2 4QP | Medway | VIRIDOR WASTE MEDWAY LTD | Warehouse And Premises; Warehouse And Premises Part Undergoing Works | industrial | 2 | 9617.4 | 103521 | GIA | 777500 | STROOD 132/11KV | inside-area | 1.48 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 15.28 | 240 | 62 | 3237937 | SPN-S000000316834 | 800 | 400 | 40-60% | STROOD 132/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200003623190 | B2 to B7 General Industrial and Special Industrial Groups | 480 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-04-10 |  | 1 | FALSE | 51.3939 | 0.51873 | SPN-S000000009948 | 11411104000;11411104000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
155 | 61.3 | UNIT 2A & 2B, M2 CITY LINK, ANTHONYS WAY | ROCHESTER | ME2 4NW | Medway |  | Warehouse And Premises | industrial | 1 | 8992.6 | 96795 | GIA | 640000 | STROOD 132/11KV | inside-area | 1.08 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 14.29 | 225 | 62 | 3244663 | SPN-S000000324641 | 800 | 560 | 60-80% | STROOD 132/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3986 | 0.51511 | SPN-S000000009948 | 13684880000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
156 | 61.3 | 21, NEPTUNE CLOSE | ROCHESTER | ME2 4LT | Medway | VEETEE RICE CO LTD | Factory And Premises | industrial | 1 | 8908.73 | 95893 | GIA | 690000 | STROOD 132/11KV | inside-area | 1.43 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 14.16 | 535 | 62 | 3245565 | SPN-S000000316834 | 800 | 400 | 40-60% | STROOD 132/11KV | 27 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3938 | 0.51769 | SPN-S000000009948 | 389834000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
157 | 61.3 | COMMISSIONERS ROAD | ROCHESTER | ME2 4EF | Medway | BUILDINGS 1 & 2 BSK; CASTACRETE LTD | Factory And Premises | industrial | 2 | 8244.89 | 88747 | GIA | 482000 | STROOD 132/11KV | inside-area | 0.7 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 13.1 | 495 | 62 | 3252711 | SPN-S000000311625 | 800 | 400 | 40-60% | STROOD 132/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388812 | General Industrial and Special Industrial Groups | 3342 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-02-11 |  | 1 | FALSE | 51.3971 | 0.50866 | SPN-S000000009948 | 133156147;12612492000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
158 | 61.3 | KNIGHT ROAD | ROCHESTER | ME2 2BP | Medway | NESTLEDOWN (HS) LTD | Factory And Premises | industrial | 1 | 7936.99 | 85433 | GIA | 397500 | STROOD 132/11KV | inside-area | 1.6 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 12.61 | 476 | 62 | 3256025 | SPN-S000000311110 | 500 | 150 | 20-40% | STROOD 132/11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388283 | Offices and Workshop Businesses | 230 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-01-10 |  | 1 | FALSE | 51.3886 | 0.48598 | SPN-S000000009948 | 139571147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
159 | 61.3 | 1, ROYAL EAGLE CLOSE | ROCHESTER | ME2 4NF | Medway |  | Workshop And Premises | industrial | 2 | 7809.29 | 84058 | GEA | 92250 | STROOD 132/11KV | inside-area | 1.42 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 12.41 | 351 | 62 | 3257400 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 232 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44027821 | Offices and Workshop Businesses | 12552 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2026-07-18 |  | 0.67 | FALSE | 51.3971 | 0.51966 | SPN-S000000009948 | 15078132000;15078132000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
160 | 61.3 | W E HASELDEN & SON LTD, WHITEWALL ROAD | ROCHESTER | ME2 4DZ | Medway |  | Warehouse And Premises | industrial | 1 | 7799.51 | 83953 | GIA | 500000 | STROOD 132/11KV | inside-area | 0.82 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 12.39 | 195 | 62 | 3257505 | SPN-S000000316841 | 1000 | 700 | 60-80% | STROOD 132/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3987 | 0.51136 | SPN-S000000009948 | 7277380000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
161 | 61.3 | GROUND FLOOR, VEETEE HOUSE, SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4DP | Medway |  | Warehouse And Premises | industrial | 1 | 7675.99 | 82624 | GIA | 525000 | STROOD 132/11KV | inside-area | 1.77 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 12.2 | 192 | 62 | 3258834 | SPN-S000000312295 | 1000 | 500 | 40-60% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.39 | 0.51954 | SPN-S000000009948 | 9313699000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
162 | 61.3 | BUILDINGS 4 5 6 AND 9 BSK, COMMISSIONERS ROAD | ROCHESTER | ME2 4EF | Medway |  | Warehouse And Premises | industrial | 1 | 7281 | 78372 | GIA | 467500 | STROOD 132/11KV | inside-area | 0.7 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 11.57 | 182 | 62 | 3263086 | SPN-S000000311625 | 800 | 400 | 40-60% | STROOD 132/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388812 | General Industrial and Special Industrial Groups | 3342 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-02-11 |  | 0.67 | FALSE | 51.3971 | 0.50866 | SPN-S000000009948 | 11726235000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
163 | 61.3 | ENTERPRISE CLOSE | ROCHESTER | ME2 4LY | Medway | I C M LTD; PARKERDELL REFINING LTD; WILLIAM T EDEN | Factory And Premises; Warehouse And Premises | industrial | 3 | 6643.72 | 71512 | GIA | 561500 | STROOD 132/11KV | inside-area | 1.01 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 10.56 | 399 | 62 | 3269946 | SPN-S000000314025 | 500 | 250 | 40-60% | STROOD 132/11KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062389231 | B2 to B7 General Industrial and Special Industrial Groups | 163 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2016-05-24 |  | 1 | FALSE | 51.3981 | 0.51392 | SPN-S000000009948 | 166139147;135190147;390311147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
164 | 61.3 | SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4DP | Medway | CHRISTIAN SALVESEN | Warehouse And Premises | industrial | 1 | 6527.05 | 70257 | GIA | 545000 | STROOD 132/11KV | inside-area | 1.77 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 10.37 | 163 | 62 | 3271201 | SPN-S000000312295 | 1000 | 500 | 40-60% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062389031 | B2 to B7 General Industrial and Special Industrial Groups | 356 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-09-24 |  | 1 | FALSE | 51.39 | 0.51954 | SPN-S000000009948 | 1611680000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
165 | 61.3 | WAREHOUSE 1, WHITEWALL ROAD | ROCHESTER | ME2 4EW | Medway |  | Warehouse And Premises | industrial | 2 | 6474.04 | 69686 | GIA | 484000 | STROOD 132/11KV | inside-area | 0.9 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 10.29 | 162 | 62 | 3271772 | SPN-S000000311654 | 300 | 90 | 20-40% | STROOD 132/11KV | 104 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3976 | 0.51211 | SPN-S000000009948 | 10570649000;3295337000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
166 | 61.3 | MCD HOUSE, VIKING CLOSE | ROCHESTER | ME2 2ND | Medway |  | Warehouse And Premises | industrial | 1 | 5363.5 | 57732 | GIA | 365000 | STROOD 132/11KV | inside-area | 2.77 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 8.52 | 134 | 62 | 3283726 | SPN-S000000311432 | 500 | 150 | 20-40% | STROOD 132/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3942 | 0.46091 | SPN-S000000009948 | 390004147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
167 | 61.3 | INNOVATION HOUSE, NORMAN CLOSE | ROCHESTER | ME2 2NF | Medway |  | Warehouse And Premises | industrial | 1 | 5214 | 56123 | GIA | 322500 | STROOD 132/11KV | inside-area | 2.18 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 8.29 | 130 | 62 | 3285335 | SPN-S000000316782 | 800 | 560 | 60-80% | STROOD 132/11KV | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.384 | 0.48177 | SPN-S000000009948 | 15095555000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
168 | 61.3 | ASHWORTH FRASERHOME COUNTIES LTD, NEPTUNE CLOSE | ROCHESTER | ME2 4NA | Medway |  | Workshop And Premises | industrial | 1 | 4488.1 | 48309 | GIA | 307500 | STROOD 132/11KV | inside-area | 1.62 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 7.13 | 202 | 62 | 3293149 | SPN-S000000313897 | 1000 | 500 | 40-60% | STROOD 132/11KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44013187 | General Industrial and Special Industrial Groups | 2978 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-04-04 |  | 0.5 | FALSE | 51.3931 | 0.52018 | SPN-S000000009948 | 5165559000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
169 | 61.3 | SEAPLANE HOUSE, SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4DP | Medway |  | Factory And Premises | industrial | 1 | 4049.78 | 43591 | GIA | 315000 | STROOD 132/11KV | inside-area | 1.77 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 6.44 | 243 | 62 | 3297867 | SPN-S000000312295 | 1000 | 500 | 40-60% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.39 | 0.51954 | SPN-S000000009948 | 390436147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
170 | 61.3 | VAILLANT HOUSE, TRIDENT CLOSE | ROCHESTER | ME2 4ER | Medway | KEY PROMOTIONS UK LTD | Warehouse And Premises | industrial | 1 | 3696.54 | 39789 | GIA | 260000 | STROOD 132/11KV | inside-area | 1.16 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 5.87 | 92 | 62 | 3301669 | SPN-S000000316763 | 1000 | 300 | 20-40% | STROOD 132/11KV | 179 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3952 | 0.51453 | SPN-S000000009948 | 3889056000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
171 | 61.3 | COMMUNICATION H, KNIGHT ROAD | ROCHESTER | ME2 2AH | Medway |  | Factory And Premises | industrial | 1 | 3340.29 | 35955 | GIA | 260000 | STROOD 132/11KV | inside-area | 1.5 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 5.31 | 200 | 62 | 3305503 | SPN-S000000311110 | 500 | 150 | 20-40% | STROOD 132/11KV | 157 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3883 | 0.48934 | SPN-S000000009948 | 390006147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
172 | 61.3 | GPS MARINE HOUSE, ORDNANCE YARD, UPNOR ROAD | ROCHESTER | ME2 4UY | Medway |  | Warehouse And Premises | industrial | 1 | 3110.3 | 33479 | GIA | 173000 | STROOD 132/11KV | inside-area | 2.25 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.94 | 78 | 62 | 3307979 | SPN-S000000324519 | 315 | 220 | 60-80% | STROOD 132/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4094 | 0.52844 | SPN-S000000009948 | 10583514000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
173 | 61.3 | UNITS 1-7, COMMUNICATIONS PARK, KNIGHT ROAD | ROCHESTER | ME2 2AX | Medway |  | Store And Premises | industrial | 1 | 3050.7 | 32837 | GIA | 142000 | STROOD 132/11KV | inside-area | 1.51 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.85 | 76 | 62 | 3308621 | SPN-S000000311110 | 500 | 150 | 20-40% | STROOD 132/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000896337 | B2 to B7 General Industrial and Special Industrial Groups | 5375 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-11-06 |  | 1 | FALSE | 51.3887 | 0.488 | SPN-S000000009948 | 3985379000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
174 | 61.3 | MASTACAB, GEORGE SUMMERS CLOSE | ROCHESTER | ME2 4NQ | Medway |  | Road Haulage Depot And Premises | industrial | 1 | 2990 | 32184 | OTH | 52000 | STROOD 132/11KV | inside-area | 1.31 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.75 | 75 | 62 | 3309274 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 167 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3989 | 0.51846 | SPN-S000000009948 | 11537707000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
175 | 61.3 | A1 - A4, KNIGHTS PARK, KNIGHT ROAD | ROCHESTER | ME2 2LS | Medway |  | Warehouse And Premises | industrial | 1 | 2809.18 | 30238 | GIA | 237000 | STROOD 132/11KV | inside-area | 1.36 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.46 | 70 | 62 | 3311220 | SPN-S000000316869 | 1000 | 700 | 60-80% | STROOD 132/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000896409 | Offices and Workshop Businesses | 902 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2022-10-28 |  | 1 | FALSE | 51.3904 | 0.48765 | SPN-S000000009948 | 10187499000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
176 | 61.3 | UNIT D, NORMAN CLOSE | ROCHESTER | ME2 2NU | Medway |  | Factory And Premises | industrial | 1 | 2737 | 29461 | GIA | 228000 | STROOD 132/11KV | inside-area | 2.29 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.35 | 164 | 62 | 3311997 | SPN-S000000316778 | 500 | 250 | 40-60% | STROOD 132/11KV | 197 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3835 | 0.48022 | SPN-S000000009948 | 1848940000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
177 | 61.3 | 1-6, CONQUEST ESTATE, KNIGHT ROAD | ROCHESTER | ME2 2AL | Medway |  | Warehouse And Premises | industrial | 1 | 2727.29 | 29356 | GIA | 202000 | STROOD 132/11KV | inside-area | 1.54 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.33 | 68 | 62 | 3312102 | SPN-S000000324359 | 315 | 94 | 20-40% | STROOD 132/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44055985 | B2 to B7 General Industrial and Special Industrial Groups | 2708 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2018-03-23 |  | 1 | FALSE | 51.3891 | 0.4863 | SPN-S000000009948 | 11209238000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
178 | 61.3 | PRIORY ROAD | ROCHESTER | ME2 2EG | Medway | QUARTIC ENGINEERING LTD | Factory And Premises; Warehouse And Premises | industrial | 2 | 2438.59 | 26249 | GIA | 154500 | STROOD 132/11KV | inside-area | 1.13 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 3.88 | 146 | 62 | 3315209 | SPN-S000000314354 | 315 | 158 | 40-60% | STROOD 132/11KV | 157 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062631595 | B1 Offices and Workshop businesses | 490 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-01-26 |  | 1 | FALSE | 51.392 | 0.48991 | SPN-S000000009948 | 143260147;13544334000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
179 | 61.3 | ARKEMA, WHITEWALL ROAD | ROCHESTER | ME2 4DZ | Medway |  | Factory And Premises | industrial | 1 | 1934.71 | 20825 | GIA | 144000 | STROOD 132/11KV | inside-area | 0.82 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 3.07 | 116 | 62 | 3320633 | SPN-S000000316841 | 1000 | 700 | 60-80% | STROOD 132/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3987 | 0.51136 | SPN-S000000009948 | 5313728000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
180 | 60.7 | J SAINSBURY'S 14, HEMPSTEAD SHOPPING CENTRE | GILLINGHAM | ME7 3PB | Medway |  | Superstore And Premises | bigbox | 1 | 11910.22 | 128200 | GIA | 1450000 | RAINHAM MARK 33/11KV | inside-area | 2.39 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 18.93 | 1072 | 37 | 2260045 | SPN-S000000313816 | 1000 | 500 | 40-60% | RAINHAM MARK 33/11KV | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3416 | 0.57307 | SPN-S000000008525 | 15046003000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
181 | 60.7 | DOBBIES GARDEN CENTRE, COURTENEY ROAD | GILLINGHAM | ME8 0SB | Medway |  | Garden Centre And Premises | bigbox | 1 | 10639.67 | 114524 | NIA | 407500 | RAINHAM MARK 33/11KV | inside-area | 0.73 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 16.91 | 958 | 37 | 2273721 | SPN-S000000312286 | 500 | 350 | 60-80% | RAINHAM MARK 33/11KV | 314 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000900112 | B8 Storage or Distribution | 13661 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-15 |  | 0.5 | FALSE | 51.3659 | 0.5691 | SPN-S000000008525 | 8060603000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
182 | 60.7 | TESCO LTD, COURTENEY ROAD | GILLINGHAM | ME8 0GX | Medway |  | Superstore And Premises | bigbox | 1 | 9414.02 | 101332 | GIA | 2150000 | RAINHAM MARK 33/11KV | inside-area | 0.62 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 14.96 | 847 | 37 | 2286913 | SPN-S000000311997 | 500 | 350 | 60-80% | RAINHAM MARK 33/11KV | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062395920 | A1/A2 Retail and Financial/Professional services | 5346 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-03-29 |  | 1 | FALSE | 51.3676 | 0.58335 | SPN-S000000008525 | 10724823000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
183 | 60.7 | TESCO SUPERSTORE, HONEYWOOD ROAD | DOVER | CT16 3EH | Dover |  | Superstore And Premises | bigbox | 1 | 9336.41 | 100496 | GIA | 1980000 | DOVER 33/11KV | inside-area | 3.08 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 14.84 | 840 | 39 | 1283925 | SPN-S000000363044 | 500 | 250 | 40-60% | DOVER 33/11KV | 11 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.154 | 1.2916 | SPN-S000000008391 | 13268405000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
184 | 60.7 | B& Q WAREHOUSE, HONEYWOOD PARKWAY, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 3GN | Dover |  | Retail Warehouse And Premises | bigbox | 1 | 7846.9 | 84463 | GIA | 555000 | DOVER 33/11KV | inside-area | 2.5 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 12.47 | 706 | 39 | 1299958 | SPN-S000000371385 | 800 | 560 | 60-80% | DOVER 33/11KV | 195 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1516 | 1.3084 | SPN-S000000008391 | 6626492000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
185 | 60.7 | UNIT 22, GROSVENOR ROAD, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0SA | Medway | HOCHIKI EUROPE (UK) LTD | Car Showroom And Premises; Factory And Premises | bigbox | 2 | 5716.4 | 61531 | GIA | 902000 | RAINHAM MARK 33/11KV | inside-area | 0.84 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 9.08 | 343 | 37 | 2326714 | SPN-S000000316804 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062395982 | General Industrial and Special Industrial Groups | 1941 | C | Natural Gas | 4 |  | Air Conditioning | 2022-09-02 |  | 0.67 | FALSE | 51.367 | 0.56829 | SPN-S000000008525 | 6823376000;387104147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
186 | 60.7 | HOME BARGAINS, HONEYWOOD PARKWAY | DOVER | CT16 3PT | Dover |  | Retail Warehouse And Premises | bigbox | 1 | 4875.03 | 52474 | GIA | 490000 | DOVER 33/11KV | inside-area | 2.76 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 7.75 | 439 | 39 | 1331947 | SPN-S000000371388 | 315 | 158 | 40-60% | DOVER 33/11KV | 97 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034877293 | A1/A2 Retail and Financial/Professional services | 3763 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2020-07-07 |  | 1 | FALSE | 51.1535 | 1.3035 | SPN-S000000008391 | 13019316000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
187 | 60.7 | MORRISONS, BRIDGE STREET | DOVER | CT16 2LB | Dover |  | Superstore And Premises | bigbox | 1 | 4731.26 | 50927 | GIA | 1060000 | DOVER 33/11KV | inside-area | 0.47 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 7.52 | 426 | 39 | 1333494 | SPN-S000000364442 | 800 | 560 | 60-80% | DOVER 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1316 | 1.3055 | SPN-S000000008391 | 9601022000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
188 | 60.7 | ROKO HEALTH CLUB, WILL ADAMS WAY | GILLINGHAM | ME8 6ED | Medway |  | Leisure Centre And Premises | bigbox | 1 | 2930.58 | 31544 | GIA | 285000 | RAINHAM MARK 33/11KV | inside-area | 0.84 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 4.66 | 234 | 37 | 2356701 | SPN-S000000316954 | 500 | 350 | 60-80% | RAINHAM MARK 33/11KV | 159 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3698 | 0.5733 | SPN-S000000008525 | 6379561000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
189 | 60.7 | LIDL, HONEYWOOD PARKWAY, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 3PT | Dover |  | Superstore And Premises | bigbox | 1 | 2559.06 | 27545 | GIA | 540000 | DOVER 33/11KV | inside-area | 2.76 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 4.07 | 230 | 39 | 1356876 | SPN-S000000371388 | 315 | 158 | 40-60% | DOVER 33/11KV | 97 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034883431 | B8 Storage or Distribution | 7944 | D | Natural Gas | 4 |  | Heating and Natural Ventilation | 2013-10-11 |  | 0.8 | FALSE | 51.1535 | 1.3035 | SPN-S000000008391 | 11349120000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
190 | 60.7 | B & M HOME STORE UNIT C TO F, HONEYWOOD RETAIL PARK, HONEYWOOD PARKWAY | DOVER | CT16 3FF | Dover |  | Retail Warehouse And Premises | bigbox | 1 | 2469.14 | 26578 | GIA | 367500 | DOVER 33/11KV | inside-area | 2.72 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 3.92 | 222 | 39 | 1357843 | SPN-S000000364395 | 500 | 250 | 40-60% | DOVER 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1524 | 1.2992 | SPN-S000000008391 | 10132198000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
191 | 60.7 | UNITS 1 & 2 TRANSPORT DEPOT, HONEYWOOD PARKWAY, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 3EH | Dover | TRAVIS PERKINS | Builders Merchants And Premises | bigbox | 1 | 2015.52 | 21695 | GIA | 207000 | DOVER 33/11KV | inside-area | 3.08 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 3.2 | 181 | 39 | 1362726 | SPN-S000000363044 | 500 | 250 | 40-60% | DOVER 33/11KV | 11 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.154 | 1.2916 | SPN-S000000008391 | 8077136000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
192 | 59.7 | UNIT K, CHANNEL ROAD, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JR | Thanet |  | Factory And Premises | industrial | 1 | 4826.91 | 51956 | GIA | 277500 | MARGATE 33/11KV | inside-area | 1.77 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 7.67 | 290 | 24 | 512655 | SPN-S000000342996 | 315 | 94 | 20-40% | THANET 33/11KV | 176 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3665 | 1.3906 | SPN-S000000008655 | 1987862000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
193 | 59.7 | UNIT B, ENTERPRISE ROAD, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JA | Thanet |  | Factory And Premises | industrial | 1 | 3469.5 | 37345 | GIA | 165000 | MARGATE 33/11KV | inside-area | 1.68 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 5.51 | 208 | 24 | 527266 | SPN-S000000343250 | 500 | 350 | 60-80% | THANET 33/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 |  | B2 to B7 General Industrial and Special Industrial Groups | 2999 | B | Biomass | 3 | 2 | Heating and Natural Ventilation | 2021-05-24 |  | 0.67 | FALSE | 51.367 | 1.3891 | SPN-S000000008655 | 1283001000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
194 | 59.7 | UNITS W1 W2 & W3 CONTINENTAL APPROACH, CONTINENTAL APPROACH, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JG | Thanet |  | Workshop And Premises | industrial | 1 | 3432.51 | 36947 | GIA | 176000 | MARGATE 33/11KV | inside-area | 1.53 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 5.45 | 154 | 24 | 527664 | SPN-R000000834910-000-001Z | 200 | 140 | 60-80% | MARGATE 33/11KV | 118 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.368 | 1.3877 | SPN-S000000008655 | 12202831000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
195 | 59.7 | UNIT 1, TIVOLI BROOKS | MARGATE | CT9 5TB | Thanet |  | Warehouse And Premises | industrial | 1 | 3137.3 | 33770 | GIA | 181000 | MARGATE 33/11KV | inside-area | 0.24 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 4.99 | 78 | 24 | 530841 | SPN-S000000343679 | 1000 | 700 | 60-80% | MARGATE 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013310198 | B8 Storage or Distribution | 1866 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-09-17 |  | 0.67 | FALSE | 51.383 | 1.3792 | SPN-S000000008655 | 3383073000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
196 | 59.7 | UNITS 1-2, OCIVAN WAY | MARGATE | CT9 4NN | Thanet |  | Factory And Premises; Warehouse And Premises | industrial | 2 | 2902.4 | 31241 | GIA | 210000 | MARGATE 33/11KV | inside-area | 1.99 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 4.61 | 174 | 24 | 533370 | SPN-S000000343595 | 315 | 220 | 60-80% | THANET 33/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10012960010 | B8 Storage or Distribution | 599 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-04-18 |  | 1 | FALSE | 51.3643 | 1.3903 | SPN-S000000008655 | 6214995000;5102757000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
197 | 59.7 | UNITS N1-N4, ENTERPRISE ROAD, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JA | Thanet |  | Factory And Premises | industrial | 1 | 2639.47 | 28411 | GIA | 151000 | MARGATE 33/11KV | inside-area | 1.68 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 4.19 | 158 | 24 | 536200 | SPN-S000000343250 | 500 | 350 | 60-80% | THANET 33/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013310889 | Storage or Distribution | 759 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-12-13 |  | 1 | FALSE | 51.367 | 1.3891 | SPN-S000000008655 | 10615333000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
198 | 59.3 | UNIT 5, LONDON MEDWAY COMMERICAL PARK | ROCHESTER | ME3 9BJ | Medway |  | Warehouse And Premises | industrial | 1 | 24764.98 | 266568 | GIA | 2290000 | KINGSNORTH GRID 11KV | inside-area | 1.57 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 59 | 39.35 | 619 | 12 | 1067100 | SPN-R000000952505-000-025Z | 200 | 180 | 80-100% | KINGSNORTH GRID 11KV | 199 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4257 | 0.57354 | SPN-S000000009525 | 11385376000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
199 | 59.3 | BUTTERCROCK WHARF, VICARAGE LANE | ROCHESTER | ME3 9LQ | Medway |  | Workshop And Premises | industrial | 1 | 1394.79 | 15013 | GIA | 129000 | KINGSNORTH GRID 11KV | inside-area | 2.01 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 2.22 | 63 | 12 | 1318655 | SPN-S000000311945 | 800 | 560 | 60-80% | KINGSNORTH GRID 11KV | 169 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4137 | 0.56931 | SPN-S000000009525 | 9061684000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
200 | 59.3 | FOOD MACHINERY & EQUIPMENT GROUP LTD, FENN CORNER | ROCHESTER | ME3 8RF | Medway |  | Workshop And Premises | industrial | 1 | 1286.89 | 13852 | GIA | 83500 | KINGSNORTH GRID 11KV | inside-area | 3.31 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 2.04 | 58 | 12 | 1319816 | SPN-R000000952509-000-107Z | 100 | 50 | 40-60% | SHARNAL STREET 33/11KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44027379 | B1 Offices and Workshop businesses | 381 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2015-05-14 |  | 0.8 | FALSE | 51.4513 | 0.58863 | SPN-S000000009525 | 14262100000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
201 | 59.3 | UNITS A B & C2, VICARAGE LANE | ROCHESTER | ME3 9LW | Medway |  | Warehouse And Premises | industrial | 1 | 1183 | 12734 | GIA | 53000 | KINGSNORTH GRID 11KV | inside-area | 2.17 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 100 | 1.88 | 30 | 12 | 1320934 | SPN-S000000311926 | 800 | 400 | 40-60% | KINGSNORTH GRID 11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4189 | 0.56434 | SPN-S000000009525 | 7855794000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
202 | 59.3 | 5, BUTTERLY AVENUE, QUESTOR | DARTFORD | DA1 1JG | Dartford |  | Warehouse And Premises | industrial | 7 | 11139.34 | 119903 | GIA | 1289000 | DARTFORD GRID B 11KV | inside-area | 2.1 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 86 | 17.7 | 278 | 54 | 2652846 | SPN-S000000316389 | 1000 | 500 | 40-60% | DARTFORD 132/11KV | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4323 | 0.22378 | LPN-S000000000716 | 3316148000;3316157000;12522859000;3316153000;6354168000;3316150000;3316154000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
203 | 59.3 | 11, APPLEGARTH DRIVE, QUESTOR | DARTFORD | DA1 1JD | Dartford |  | Factory And Premises; Warehouse And Premises | industrial | 3 | 11003.1 | 118436 | GIA | 1159500 | DARTFORD GRID B 11KV | inside-area | 1.94 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 87 | 17.48 | 660 | 54 | 2654313 | SPN-S000000314400 | 500 | 250 | 40-60% | DARTFORD 132/11KV | 16 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094155075 | B8 Storage or Distribution | 1693 | A | Natural Gas | 5 |  | Air Conditioning | 2019-06-14 |  | 1 | FALSE | 51.4332 | 0.22102 | LPN-S000000000716 | 12269510000;11886820000;11057895000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
204 | 59.3 | UNIT 2 MAXMOR HOUSE, SANDPIT ROAD | DARTFORD | DA1 5BU | Dartford |  | Warehouse And Premises | industrial | 2 | 10763.67 | 115859 | GIA | 945000 | DARTFORD GRID B 11KV | inside-area | 0.84 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 89 | 17.1 | 269 | 54 | 2656890 | LPN-S000000073854 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4565 | 0.20713 | LPN-S000000000716 | 13295965000;13420119000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
205 | 59.3 | ONE HUNDRED HOUSE, BRUNEL WAY | DARTFORD | DA1 5TH | Dartford |  | Warehouse, Office And Premises | industrial | 1 | 10635.7 | 114482 | GIA | 1220000 | DARTFORD GRID B 11KV | inside-area | 1.61 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 90 | 16.9 | 744 | 54 | 2658267 | LPN-S000000073904 | 500 | 350 | 60-80% | DARTFORD GRID B 11KV | 210 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4601 | 0.22879 | LPN-S000000000716 | 9252933000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
206 | 59.3 | DIASORIN, CENTRAL ROAD | DARTFORD | DA1 5LR | Dartford |  | Factory And Premises | industrial | 1 | 10012.8 | 107777 | GIA | 715000 | DARTFORD GRID B 11KV | inside-area | 0.6 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 96 | 15.91 | 601 | 54 | 2664972 | LPN-S000000072016 | 500 | 450 | 80-100% | DARTFORD GRID B 11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000530746 | General Industrial and Special Industrial Groups | 8212 | C | Natural Gas | 4 |  | Heating and Natural Ventilation | 2024-09-11 |  | 0.5 | FALSE | 51.4495 | 0.22119 | LPN-S000000000716 | 10340700000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
207 | 59.3 | 599-613, PRINCES ROAD | DARTFORD | DA2 6HH | Dartford |  | Car Showroom And Premises; Warehouse And Premises | industrial | 2 | 9313.73 | 100252 | GIA | 604000 | DARTFORD GRID B 11KV | inside-area | 2.63 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 14.8 | 838 | 54 | 2672497 | LPN-S000000072099 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 38 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000542820 | B1 Offices and Workshop businesses | 396 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-05-03 |  | 1 | FALSE | 51.4384 | 0.24578 | LPN-S000000000716 | 2834820000;7023504000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
208 | 59.3 | 50, WEST HILL | DARTFORD | DA1 2EU | Dartford |  | Sorting Office And Premises | industrial | 1 | 7663.12 | 82485 | GIA | 287500 | DARTFORD GRID B 11KV | inside-area | 0.52 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 12.18 | 536 | 54 | 2690264 | LPN-S000000074194 | 800 | 720 | 80-100% | DARTFORD GRID B 11KV | 58 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4456 | 0.20922 | LPN-S000000000716 | 168317147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
209 | 59.3 | UNIT 3, DARTFORD TRADING ESTATE, VICTORIA ROAD | DARTFORD | DA1 5XS | Dartford |  | Warehouse And Premises | industrial | 5 | 7530.08 | 81053 | GIA | 1006000 | DARTFORD GRID B 11KV | inside-area | 0.22 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 11.97 | 188 | 54 | 2691696 | LPN-S000000073830 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094157370 | B1 Offices and Workshop businesses | 1329 | A | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2020-12-10 |  | 1 | FALSE | 51.451 | 0.21516 | LPN-S000000000716 | 14241543000;13691296000;14335866000;14241563000;13691295000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
210 | 59.3 | UNIT 21, FAWKES AVENUE, QUESTOR | DARTFORD | DA1 1JQ | Dartford |  | Factory And Premises; Warehouse And Premises | industrial | 4 | 7305.08 | 78631 | GIA | 917000 | DARTFORD GRID B 11KV | inside-area | 2 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 11.61 | 438 | 54 | 2694118 | SPN-S000000314400 | 500 | 250 | 40-60% | DARTFORD 132/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10023442171 | Storage or Distribution | 3356 | D | Natural Gas | 3 | 3 | Heating and Natural Ventilation | 2022-10-12 |  | 1 | FALSE | 51.4328 | 0.22185 | LPN-S000000000716 | 9058942000;12940577000;1309597000;13771561000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
211 | 59.3 | 11-12, ORBITAL ONE TRADING ESTATE, GREEN STREET GREEN ROAD | DARTFORD | DA1 1QG | Dartford |  | Factory And Premises; Warehouse And Premises | industrial | 5 | 5720.42 | 61574 | GIA | 750000 | DARTFORD GRID B 11KV | inside-area | 2.44 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 9.09 | 343 | 54 | 2711175 | LPN-S000000072077 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000534002 | Storage or Distribution | 584 | D | Natural Gas | 5 | 1 | Air Conditioning | 2025-04-02 |  | 1 | FALSE | 51.4339 | 0.2369 | LPN-S000000000716 | 11010097000;4147004000;12095814000;12097089000;12097057000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
212 | 59.3 | E, RIVERSIDE INDUSTRIAL ESTATE | DARTFORD | DA1 5BS | Dartford |  | Storage Depot And Premises | industrial | 1 | 4947.8 | 53258 | GIA | 442500 | DARTFORD GRID B 11KV | inside-area | 0.53 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 7.86 | 124 | 54 | 2719491 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4517 | 0.21963 | LPN-S000000000716 | 168137147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
213 | 59.3 | 23A, FAWKES AVENUE, QUESTOR | DARTFORD | DA1 1JQ | Dartford |  | Warehouse And Premises | industrial | 1 | 4451.61 | 47917 | GIA | 720000 | DARTFORD GRID B 11KV | inside-area | 2 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 7.07 | 111 | 54 | 2724832 | SPN-S000000314400 | 500 | 250 | 40-60% | DARTFORD 132/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094155486 | B2 to B7 General Industrial and Special Industrial Groups | 4483 | A | Natural Gas | 5 |  | Air Conditioning | 2019-06-14 |  | 1 | FALSE | 51.4328 | 0.22185 | LPN-S000000000716 | 12269514000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
214 | 59.3 | UCC COFFEE, RIVERSIDE INDUSTRIAL ESTATE | DARTFORD | DA1 5BS | Dartford |  | Factory And Premises | industrial | 1 | 4331.31 | 46622 | GIA | 437500 | DARTFORD GRID B 11KV | inside-area | 0.53 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 6.88 | 260 | 54 | 2726127 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4517 | 0.21963 | LPN-S000000000716 | 13992024000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
215 | 59.3 | 625-649, PRINCES ROAD | DARTFORD | DA2 6EF | Dartford |  | Factory And Premises; Warehouse And Premises | industrial | 3 | 4134.92 | 44508 | GIA | 318000 | DARTFORD GRID B 11KV | inside-area | 2.92 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 6.57 | 248 | 54 | 2728241 | LPN-S000000072127 | 500 | 350 | 60-80% | DARTFORD GRID B 11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 100062313929 | Storage or Distribution | 1437 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2024-07-04 |  | 1 | FALSE | 51.4385 | 0.25062 | LPN-S000000000716 | 396496147;2315112000;14722147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
216 | 59.3 | UNIT 1 & 2 162-172, BURNHAM ROAD | DARTFORD | DA1 5BL | Dartford |  | Warehouse And Premises | industrial | 1 | 4065.66 | 43762 | GIA | 535000 | DARTFORD GRID B 11KV | inside-area | 0.7 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 6.46 | 102 | 54 | 2728987 | LPN-S000000073854 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094158983 | Storage or Distribution | 2360 | A+ | Grid Supplied Electricity | 4 | 2 | Heating and Natural Ventilation | 2022-11-04 |  | 0.5 | FALSE | 51.4553 | 0.20767 | LPN-S000000000716 | 14317034000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
217 | 59.3 | UNIT 4, SWAN BUSINESS PARK, SANDPIT ROAD | DARTFORD | DA1 5ED | Dartford |  | Warehouse And Premises | industrial | 3 | 3348.3 | 36041 | GIA | 389000 | DARTFORD GRID B 11KV | inside-area | 0.73 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 5.32 | 84 | 54 | 2736708 | LPN-S000000073854 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000530364 | B1 Offices and Workshop businesses | 1089 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-06-14 |  | 1 | FALSE | 51.4559 | 0.20861 | LPN-S000000000716 | 13916738000;13916738000;336375147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
218 | 59.3 | UNITS K1-K9, RIVERSIDE INDUSTRIAL ESTATE | DARTFORD | DA1 5BS | Dartford |  | Workshop And Premises | industrial | 1 | 2978.25 | 32058 | GIA | 282500 | DARTFORD GRID B 11KV | inside-area | 0.53 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 4.73 | 134 | 54 | 2740691 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000531858 | Non-residential Institutions: Education | 453 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-02-02 |  | 1 | FALSE | 51.4517 | 0.21963 | LPN-S000000000716 | 14482166000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
219 | 59.3 | UNIT AA, FAWKES AVENUE, QUESTOR | DARTFORD | DA1 1JQ | Dartford |  | Warehouse And Premises | industrial | 2 | 2854.68 | 30727 | GIA | 331000 | DARTFORD GRID B 11KV | inside-area | 2 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 4.54 | 71 | 54 | 2742022 | SPN-S000000314400 | 500 | 250 | 40-60% | DARTFORD 132/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094155486 | B2 to B7 General Industrial and Special Industrial Groups | 4483 | A | Natural Gas | 5 |  | Air Conditioning | 2019-06-14 |  | 0.67 | FALSE | 51.4328 | 0.22185 | LPN-S000000000716 | 4262613000;4262613000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
220 | 59.3 | GREEN STREET GREEN ROAD | DARTFORD | DA1 1QE | Dartford | CURTIS HOLT LTD | Warehouse And Premises | industrial | 1 | 2602.94 | 28018 | GIA | 265000 | DARTFORD GRID B 11KV | inside-area | 2.2 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 4.14 | 65 | 54 | 2744731 | LPN-S000000073881 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 134 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000541852 | General Industrial and Special Industrial Groups | 2571 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-12-11 |  | 1 | FALSE | 51.4362 | 0.23563 | LPN-S000000000716 | 6544147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
221 | 59.3 | MUREX BIOTECH, CENTRAL ROAD | DARTFORD | DA1 5LR | Dartford |  | Factory And Premises | industrial | 1 | 2534.83 | 27285 | GIA | 198000 | DARTFORD GRID B 11KV | inside-area | 0.6 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 4.03 | 152 | 54 | 2745464 | LPN-S000000072016 | 500 | 450 | 80-100% | DARTFORD GRID B 11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4495 | 0.22119 | LPN-S000000000716 | 10759247000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
222 | 59.3 | ST VINCENTS ROAD | DARTFORD | DA1 1UU | Dartford | A PILE & SON | Workshop And Premises | industrial | 2 | 2477.2 | 26664 | GIA | 224500 | DARTFORD GRID B 11KV | inside-area | 1.29 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.94 | 111 | 54 | 2746085 | LPN-S000000072121 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000531461 | Offices and Workshop Businesses | 1321 | E | Natural Gas | 3 | 3 | Heating and Mechanical Ventilation | 2023-08-06 |  | 1 | FALSE | 51.447 | 0.23067 | LPN-S000000000716 | 17233147;17233147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
223 | 59.3 | WATTS FARMS LTD, SANDPIT ROAD | DARTFORD | DA1 5BU | Dartford |  | Warehouse And Premises | industrial | 1 | 2370.74 | 25518 | GIA | 242000 | DARTFORD GRID B 11KV | inside-area | 0.84 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.77 | 59 | 54 | 2747231 | LPN-S000000073854 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4565 | 0.20713 | LPN-S000000000716 | 11171110000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
224 | 59.3 | 1A, CENTRAL ROAD | DARTFORD | DA1 5BG | Dartford |  | Warehouse And Premises | industrial | 1 | 2338.3 | 25169 | GIA | 129000 | DARTFORD GRID B 11KV | inside-area | 0.57 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.72 | 58 | 54 | 2747580 | LPN-S000000072016 | 500 | 450 | 80-100% | DARTFORD GRID B 11KV | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000545012 | B2 to B7 General Industrial and Special Industrial Groups | 2361 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-11-28 |  | 1 | FALSE | 51.4502 | 0.22078 | LPN-S000000000716 | 170049147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
225 | 59.3 | UNITS 1-3 SAUNDERS WAY, QUESTOR | DARTFORD | DA1 1JS | Dartford |  | Warehouse And Premises | industrial | 1 | 1944.55 | 20931 | GIA | 227000 | DARTFORD GRID B 11KV | inside-area | 2.02 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.09 | 49 | 54 | 2751818 | SPN-S000000316389 | 1000 | 500 | 40-60% | DARTFORD 132/11KV | 99 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4334 | 0.22478 | LPN-S000000000716 | 13218304000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
226 | 58.8 | UNITS 1-4, LORDSWOOD INDUSTRIAL ESTATE, REVENGE ROAD | CHATHAM | ME5 8UD | Maidstone |  | Warehouse And Premises; Workshop And Premises | industrial | 3 | 5535.34 | 59582 | GIA | 523000 | LORDSWOOD 33/11KV | inside-area | 2.14 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 100 | 8.8 | 249 | 6 | 398104 | SPN-S000000313791 | 1000 | 500 | 40-60% | LORDSWOOD 33/11KV | 34 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10022896993 | Storage or Distribution | 796 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2025-01-23 |  | 1 | FALSE | 51.3286 | 0.54515 | SPN-S000000008646 | 8660665000;1554559000;14648746000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
227 | 58.8 | 6 - 8, REVENGE ROAD | CHATHAM | ME5 8UD | Medway |  | Factory And Premises; Workshop And Premises | industrial | 2 | 4773.7 | 51384 | GIA | 324500 | LORDSWOOD 33/11KV | inside-area | 2.14 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 100 | 7.59 | 286 | 6 | 406302 | SPN-S000000313791 | 1000 | 500 | 40-60% | LORDSWOOD 33/11KV | 34 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44012915 | B1 Offices and Workshop businesses | 4994 | C | Grid Supplied Electricity | 4 |  | Air Conditioning | 2018-03-27 |  | 1 | FALSE | 51.3286 | 0.54515 | SPN-S000000008646 | 11819805000;45278147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
228 | 58.8 | APEX HOUSE 96, HOPEWELL DRIVE | CHATHAM | ME5 7NL | Medway |  | Warehouse And Premises | industrial | 1 | 3268.93 | 35186 | GIA | 200000 | LORDSWOOD 33/11KV | inside-area | 1.9 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 100 | 5.19 | 82 | 6 | 422500 | SPN-S000000311841 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3649 | 0.54544 | SPN-S000000008646 | 8428545000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
229 | 58.8 | WESTFIELD SOLE ROAD | MAIDSTONE | ME14 3EH | Maidstone | WESTSOLE FENCING | Store And Premises | industrial | 1 | 3196.6 | 34408 | OTH | 45250 | LORDSWOOD 33/11KV | inside-area | 2.41 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 100 | 5.08 | 80 | 6 | 423278 | SPN-S000000311908 | 500 | 250 | 40-60% | LORDSWOOD 33/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10014312822 | Offices and Workshop Businesses | 115 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-04-15 |  | 1 | FALSE | 51.327 | 0.55401 | SPN-S000000008646 | 400536148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
230 | 58.8 | UNIT 37-38, LORDSWOOD INDUSTRIAL ESTATE, GLEAMING WOOD DRIVE | CHATHAM | ME5 8RZ | Maidstone |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 2049.39 | 22059 | GIA | 258000 | LORDSWOOD 33/11KV | inside-area | 2.33 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 100 | 3.26 | 92 | 6 | 435627 | SPN-S000000316880 | 500 | 250 | 40-60% | MEDWAY 33/11KV | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3269 | 0.54607 | SPN-S000000008646 | 1710927000;15116965000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
231 | 57.7 | FLEET HOUSE, SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HJ | Gravesham |  | Offices And Premises | office | 1 | 2601.49 | 28002 | GIA | 235000 | EBBSFLEET 33/11KV | inside-area | 1.66 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 4.13 | 182 | 7 | 434398 | SPN-S000000314022 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062310761 | B1 Offices and Workshop businesses | 4568 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2021-06-03 |  | 1 | FALSE | 51.435 | 0.33279 | SPN-S000000008627 | 13037670000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
232 | 57.7 | UNIT R, SPRINGHEAD ENTERPRISE PARK, SPRINGHEAD ROAD | GRAVESEND | DA11 8HJ | Gravesham |  | Warehouse And Premises | industrial | 1 | 1450.8 | 15616 | GIA | 141000 | EBBSFLEET 33/11KV | inside-area | 1.66 | Northfleet East | Northfleet | West Kent Zone | 20.8 | primary | 20.8 | Green | 34 | 11.7 | Thermal | 0 | 16.1 | 0 | 16.1 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | Green (Over 5% headroom) | 148307 | 100 | 2.31 | 36 | 7 | 446784 | SPN-S000000314022 | 800 | 400 | 40-60% | EBBSFLEET 33/11KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062310902 | Offices and Workshop Businesses | 232 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-08-14 |  | 1 | FALSE | 51.435 | 0.33279 | SPN-S000000008627 | 167533147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
233 | 57.7 | NOTCUTTS GARDEN CENTRE, TONBRIDGE ROAD | TUNBRIDGE WELLS | TN2 4QN | Tunbridge Wells |  | Garden Centre And Premises | bigbox | 1 | 6111.5 | 65784 | NIA | 170000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 2.79 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 9.71 | 550 | 13 | 348272 | SPN-S000000443193 | 800 | 560 | 60-80% | TUNBRIDGE WELLS TOWN 132/6.6kV | 337 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024137750 | A1/A2 Retail and Financial/Professional services | 2352 | A | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2014-04-30 |  | 1 | FALSE | 51.1453 | 0.3085 | SPN-S000000009251 | 176988148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
234 | 57.7 | 3, MOUNT EPHRAIM | TUNBRIDGE WELLS | TN4 8AE | Tunbridge Wells |  | Car Showroom And Premises | bigbox | 1 | 5066.43 | 54535 | GIA | 442500 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.7 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 8.05 | 456 | 13 | 359521 | SPN-S000000451632 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS TOWN 11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.136 | 0.26113 | SPN-S000000009251 | 395054148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
235 | 57.7 | 29, GROSVENOR ROAD | TUNBRIDGE WELLS | TN1 2AH | Tunbridge Wells | TESCO | Supermarket & Premises | bigbox | 1 | 2300 | 24757 | GIA | 241000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.67 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 3.65 | 207 | 13 | 389299 | SPN-S000000442129 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS TOWN 132/6.6kV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062543053 | A1/A2 Retail and Financial/Professional services | 2417 | C | Grid Supplied Electricity | 4 |  | Air Conditioning | 2021-11-05 |  | 1 | FALSE | 51.1349 | 0.26309 | SPN-S000000009251 | 9419675000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
236 | 57.5 | AREA 3, FORT HALSTEAD, STAR HILL ROAD | SEVENOAKS | TN14 7BP | Sevenoaks |  | Offices And Premises | office | 1 | 1857.25 | 19991 | NIA | 147000 | NORTH SEVENOAKS 33/11KV | inside-area | 3.93 | Chelsfield Grid | Northfleet | West Kent Zone | 25.1 | primary | 25.1 | Green | 45.8 | 20.4 | Thermal | 0 | 9.2 | 1.5 | 9.2 | 21.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | Green (Over 5% headroom) | 178966 | 100 | 2.95 | 130 | 19 | 823056 | SPN-S000000446606 | 500 | 350 | 60-80% | NORTH SEVENOAKS 33/11KV | 163 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035183452 | Offices and Workshop Businesses | 1501 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-06-01 |  | 0.67 | FALSE | 51.315 | 0.15185 | SPN-S000000008447 | 14991355000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
237 | 57.5 | UNIT 10, GALLEON BOULEVARD, NEWTONS COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QL | Dartford |  | Warehouse And Premises | industrial | 5 | 13439.87 | 144665 | GIA | 1719500 | CROSSWAYS | inside-area | 0.52 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 65 | 21.36 | 336 | 35 | 5774636 | SPN-S000000311176 | 1000 | 500 | 40-60% | CROSSWAYS | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000545735 | A1/A2 Retail and Financial/Professional services | 6336 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2022-02-17 |  | 0.83 | FALSE | 51.4535 | 0.25646 | SPN-S000000008626 | 827977000;341541147;397685147;341526147;14876783000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
238 | 57.5 | UNIT 60, EDISON PARK, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QN | Dartford |  | Warehouse And Premises | industrial | 3 | 12328.22 | 132700 | GIA | 1487500 | CROSSWAYS | inside-area | 0.74 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 70 | 19.59 | 308 | 35 | 5786601 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.457 | 0.25538 | SPN-S000000008626 | 688412000;688402000;688407000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
239 | 57.5 | UNIT 4, ALBION ROAD | DARTFORD | DA1 5PZ | Dartford |  | Warehouse And Premises | industrial | 3 | 11134.25 | 119848 | GIA | 1282500 | CROSSWAYS | inside-area | 1.12 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 78 | 17.69 | 278 | 35 | 5799453 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4612 | 0.24719 | SPN-S000000008626 | 9811511000;12103528000;9811478000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
240 | 57.5 | LONG REACH, GALLEON BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QE | Dartford | CURTIS HOLT LTD | Warehouse And Premises | industrial | 1 | 10393.26 | 111872 | GIA | 895000 | CROSSWAYS | inside-area | 0.32 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 83 | 16.52 | 260 | 35 | 5807429 | SPN-S000000324354 | 1000 | 700 | 60-80% | CROSSWAYS | 216 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4529 | 0.25374 | SPN-S000000008626 | 2150638000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
241 | 57.5 | FURLONG CARPETS LTD, EDISON PARK, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QN | Dartford |  | Warehouse And Premises | industrial | 1 | 9688.7 | 104288 | GIA | 890000 | CROSSWAYS | inside-area | 0.74 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 90 | 15.4 | 242 | 35 | 5815013 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.457 | 0.25538 | SPN-S000000008626 | 1072639000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
242 | 57.5 | FLAGSHIP HOUSE, VICTORY WAY, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QD | Dartford |  | Warehouse And Premises | industrial | 1 | 7804.72 | 84009 | GIA | 900000 | CROSSWAYS | inside-area | 0.49 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 12.4 | 195 | 35 | 5835292 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 186 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000543552 | Offices and Workshop Businesses | 2905 | C | Natural Gas | 3 | 2 | Air Conditioning | 2023-09-13 |  | 1 | FALSE | 51.4557 | 0.24881 | SPN-S000000008626 | 2579797000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
243 | 57.5 | GND FLR 16 NEWTONS COURT GALLEON BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QL | Dartford |  | Warehouse And Premises | industrial | 1 | 6656.79 | 71653 | GIA | 570000 | CROSSWAYS | inside-area | 0.52 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 10.58 | 166 | 35 | 5847648 | SPN-S000000311176 | 1000 | 500 | 40-60% | CROSSWAYS | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000545735 | A1/A2 Retail and Financial/Professional services | 6336 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2022-02-17 |  | 0.83 | FALSE | 51.4535 | 0.25646 | SPN-S000000008626 | 12957042000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
244 | 57.5 | 2-3 ANCHOR BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QH | Dartford |  | Vehicle Repair Workshop And Premises | industrial | 1 | 6258.29 | 67364 | GIA | 515000 | CROSSWAYS | inside-area | 0.37 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 9.95 | 282 | 35 | 5851937 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 124 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000544252 | B1 Offices and Workshop businesses | 5490 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2021-11-12 |  | 0.75 | FALSE | 51.4541 | 0.25254 | SPN-S000000008626 | 13935454000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
245 | 57.5 | REMEL HOUSE, CLIPPER BOULEVARD WEST, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6PT | Dartford |  | Business Unit And Premises | industrial | 1 | 6128.85 | 65970 | GIA | 735000 | CROSSWAYS | inside-area | 0.69 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 9.74 | 153 | 35 | 5853331 | SPN-S000000316825 | 315 | 158 | 40-60% | STONE MARSHES 33/11KV | 127 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4573 | 0.25227 | SPN-S000000008626 | 3097870000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
246 | 57.5 | 32-33, CLIPPER BOULEVARD EAST, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QB | Dartford |  | Factory And Premises | industrial | 1 | 4402.08 | 47384 | GIA | 635000 | CROSSWAYS | inside-area | 1.18 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 7 | 264 | 35 | 5871917 | SPN-S000000314562 | 500 | 350 | 60-80% | CROSSWAYS | 375 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537922 | B8 Storage or Distribution | 4935 | A | Natural Gas | 4 | 2 | Air Conditioning | 2020-10-21 |  | 1 | FALSE | 51.4551 | 0.2658 | SPN-S000000008626 | 13202419000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
247 | 57.5 | 35, CLIPPER BOULEVARD WEST, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6PT | Dartford |  | Warehouse And Premises | industrial | 1 | 3614.1 | 38902 | GIA | 462500 | CROSSWAYS | inside-area | 0.69 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 5.74 | 90 | 35 | 5880399 | SPN-S000000316825 | 315 | 158 | 40-60% | STONE MARSHES 33/11KV | 127 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4573 | 0.25227 | SPN-S000000008626 | 4653241000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
248 | 57.5 | 55A, BRIDGE CLOSE, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Warehouse And Premises | industrial | 1 | 3400.28 | 36600 | GIA | 412500 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 5.4 | 85 | 35 | 5882701 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002024632 | Offices and Workshop Businesses | 3248 | B | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2025-09-22 |  | 0.67 | FALSE | 51.4606 | 0.25638 | SPN-S000000008626 | 12539199000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
249 | 57.5 | CLIPPER BOULEVARD WEST, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QS | Dartford | GEFCO UK LTD | Warehouse And Premises | industrial | 1 | 3315.4 | 35687 | GIA | 362500 | CROSSWAYS | inside-area | 0.74 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 5.27 | 83 | 35 | 5883614 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.457 | 0.2554 | SPN-S000000008626 | 406582147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
250 | 57.5 | 10, CAPSTAN COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QG | Dartford |  | Warehouse And Premises | industrial | 1 | 3249.59 | 34978 | GIA | 445000 | CROSSWAYS | inside-area | 0.26 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 5.16 | 81 | 35 | 5884323 | SPN-S000000316824 | 1000 | 100 | 0-20% | CROSSWAYS | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000542331 | Storage or Distribution | 2856 | B | Natural Gas | 3 | 2 | Air Conditioning | 2024-07-25 |  | 0.67 | FALSE | 51.453 | 0.2473 | SPN-S000000008626 | 2326180000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
251 | 57.5 | 55B, BRIDGE CLOSE, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Warehouse And Premises | industrial | 1 | 2561.58 | 27573 | GIA | 332500 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 4.07 | 64 | 35 | 5891728 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10009429013 | B8 Storage or Distribution | 2569 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-11-02 |  | 0.67 | FALSE | 51.4606 | 0.25638 | SPN-S000000008626 | 12539200000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
252 | 57.5 | UNIT 25, EDISON PARK, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Factory And Premises | industrial | 1 | 2310.06 | 24865 | GIA | 340000 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 3.67 | 139 | 35 | 5894436 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4606 | 0.25638 | SPN-S000000008626 | 3427349000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
253 | 57.5 | MILLMOLL HOUSE UNIT 1, GALLEON BOULEVARD, NEWTONS COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QL | Dartford |  | Warehouse And Premises | industrial | 1 | 2279 | 24531 | GIA | 342500 | CROSSWAYS | inside-area | 0.52 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 3.62 | 57 | 35 | 5894770 | SPN-S000000311176 | 1000 | 500 | 40-60% | CROSSWAYS | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000543094 | B1 Offices and Workshop businesses | 2484 | C | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2019-07-11 |  | 1 | FALSE | 51.4535 | 0.25646 | SPN-S000000008626 | 11855492000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
254 | 57.5 | UNIT G PANORAMA, BRIDGE CLOSE, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Warehouse And Premises | industrial | 1 | 2214.97 | 23842 | GIA | 315000 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 3.52 | 55 | 35 | 5895459 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4606 | 0.25638 | SPN-S000000008626 | 13286882000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
255 | 57.5 | UNIT A, BRIDGE CLOSE, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Warehouse And Premises | industrial | 1 | 1957.65 | 21072 | GIA | 267500 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 3.11 | 49 | 35 | 5898229 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094156147 | B8 Storage or Distribution | 1934 | A | Natural Gas | 4 |  | Heating and Natural Ventilation | 2020-09-14 |  | 1 | FALSE | 51.4606 | 0.25638 | SPN-S000000008626 | 13016959000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
256 | 57.3 | PARK CENTRAL, CULLET DRIVE | QUEENBOROUGH | ME11 5JS | Swale |  | Workshop And Premises | industrial | 1 | 5773.86 | 62149 | GIA | 800000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.77 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 9.18 | 260 | 15 | 1077903 | SPN-S000000393826 | 500 | 250 | 40-60% | QUEENBOROUGH 33/6.6KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023196469 | Offices and Workshop Businesses | 5802 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-09-30 |  | 1 | FALSE | 51.4071 | 0.75041 | SPN-S000000008368 | 9257198000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
257 | 57.3 | AL-LE LOGISTICS, RUSHENDEN ROAD | QUEENBOROUGH | ME11 5HB | Swale |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 5336.68 | 57443 | GIA | 194000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.2 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 8.48 | 240 | 15 | 1082609 | SPN-S000000391561 | 300 | 90 | 20-40% | QUEENBOROUGH 33/6.6KV | 62 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4155 | 0.74772 | SPN-S000000008368 | 9176604000;15142284000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
258 | 57.3 | DWL HOME IMPROVEMENTS LTD, MAIN ROAD | QUEENBOROUGH | ME11 5BB | Swale |  | Factory And Premises | industrial | 1 | 4774.79 | 51395 | GIA | 157000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.12 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 7.59 | 286 | 15 | 1088657 | SPN-S000000391561 | 300 | 90 | 20-40% | QUEENBOROUGH 33/6.6KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4148 | 0.74821 | SPN-S000000008368 | 7565955000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
259 | 57.3 | 2-5, STALHAM BUSINESS CENTRE, RUSHENDEN ROAD | QUEENBOROUGH | ME11 5HE | Swale |  | Factory And Premises; Workshop And Premises | industrial | 2 | 4039.6 | 43482 | GIA | 171000 | QUEENBOROUGH 33/6.6KV | inside-area | 1.02 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 6.42 | 242 | 15 | 1096570 | SPN-S000000393967 | 500 | 350 | 60-80% | QUEENBOROUGH 33/6.6KV | 103 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 |  | B2 to B7 General Industrial and Special Industrial Groups | 3205 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-04-04 |  | 0.75 | FALSE | 51.4046 | 0.74801 | SPN-S000000008368 | 7160750000;394023147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
260 | 57.3 | UNITS 6-10, CULLET DRIVE | QUEENBOROUGH | ME11 5JS | Swale |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 4026.04 | 43336 | GIA | 284000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.77 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 6.4 | 181 | 15 | 1096716 | SPN-S000000393826 | 500 | 250 | 40-60% | QUEENBOROUGH 33/6.6KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002529330 | B1 Offices and Workshop businesses | 2861 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2017-10-29 |  | 1 | FALSE | 51.4071 | 0.75041 | SPN-S000000008368 | 14504169000;9328946000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
261 | 57.3 | OLYMPIC GLASS, MAIN ROAD | QUEENBOROUGH | ME11 5BB | Swale |  | Factory And Premises | industrial | 1 | 2660.5 | 28637 | GIA | 118000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.12 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 4.23 | 160 | 15 | 1111415 | SPN-S000000391561 | 300 | 90 | 20-40% | QUEENBOROUGH 33/6.6KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4148 | 0.74821 | SPN-S000000008368 | 7565953000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
262 | 57.3 | UNITS 6B 7 8 9 10A 11 12 40 & 41, QUEENBOROUGH SHIPYARD, SOUTH STREET | QUEENBOROUGH | ME11 5AF | Swale |  | Factory, Office And Premises | industrial | 1 | 2290.34 | 24653 | GIA | 98000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.48 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 3.64 | 137 | 15 | 1115399 | SPN-S000000391531 | 300 | 150 | 40-60% | QUEENBOROUGH 33/6.6KV | 41 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4166 | 0.74219 | SPN-S000000008368 | 8943405000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
263 | 57.1 | GOPAK LTD WAREHOUSE ONE, RANGE ROAD INDUSTRIAL ESTATE, RANGE ROAD | HYTHE | CT21 6HG | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 2848.76 | 30664 | GIA | 130000 | HYTHE MAIN 33/11KV | inside-area | 1.4 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 4.53 | 171 | 7 | 176691 | SPN-S000000361378 | 800 | 400 | 40-60% | HYTHE MAIN 33/11KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50116127 | B1 Offices and Workshop businesses | 901 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-07-26 |  | 0.67 | FALSE | 51.066 | 1.0761 | SPN-S000000008421 | 9589778000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
264 | 57.1 | H V WOODING LTD STORE A, RANGE ROAD INDUSTRIAL ESTATE, RANGE ROAD | HYTHE | CT21 6HG | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 2465.76 | 26541 | GIA | 111000 | HYTHE MAIN 33/11KV | inside-area | 1.4 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 3.92 | 148 | 7 | 180814 | SPN-S000000361378 | 800 | 400 | 40-60% | HYTHE MAIN 33/11KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50116127 | B1 Offices and Workshop businesses | 901 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-07-26 |  | 0.67 | FALSE | 51.066 | 1.0761 | SPN-S000000008421 | 9044775000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
265 | 57.1 | H V WOODING MAIN SITE, RANGE ROAD INDUSTRIAL ESTATE, RANGE ROAD | HYTHE | CT21 6HG | Folkestone & Hythe |  | Workshop, Storage And Premises | industrial | 1 | 2183.8 | 23506 | GIA | 106000 | HYTHE MAIN 33/11KV | inside-area | 1.4 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 3.47 | 98 | 7 | 183849 | SPN-S000000361378 | 800 | 400 | 40-60% | HYTHE MAIN 33/11KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50104236 | B1 Offices and Workshop businesses | 2338 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2015-06-25 |  | 1 | FALSE | 51.066 | 1.0761 | SPN-S000000008421 | 9047385000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
266 | 56.3 | MORRISONS SUPERMARKET, KNIGHT ROAD | ROCHESTER | ME2 2AH | Medway |  | Superstore And Premises | bigbox | 1 | 7215.26 | 77664 | GIA | 1670000 | STROOD 132/11KV | inside-area | 1.5 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 11.47 | 649 | 62 | 3263794 | SPN-S000000311110 | 500 | 150 | 20-40% | STROOD 132/11KV | 157 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3883 | 0.48934 | SPN-S000000009948 | 14822676000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
267 | 56.3 | 3, CUXTON ROAD | ROCHESTER | ME2 2BT | Medway | TESCO STORES LTD | Supermarket And Premises | bigbox | 1 | 3973.8 | 42774 | GIA | 435000 | STROOD 132/11KV | inside-area | 0.78 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 6.31 | 358 | 62 | 3298684 | SPN-S000000311532 | 500 | 250 | 40-60% | STROOD 132/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3957 | 0.49083 | SPN-S000000009948 | 8832562000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
268 | 56.3 | UNIT 1, M2 CITY LINK, ANTHONYS WAY | ROCHESTER | ME2 4NW | Medway |  | Builders Merchant And Premises | bigbox | 1 | 3114.06 | 33519 | GIA | 327500 | STROOD 132/11KV | inside-area | 1.08 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 4.95 | 280 | 62 | 3307939 | SPN-S000000324641 | 800 | 560 | 60-80% | STROOD 132/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388787 | General Industrial and Special Industrial Groups | 3121 | B | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2026-04-09 |  | 1 | FALSE | 51.3986 | 0.51511 | SPN-S000000009948 | 13684882000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
269 | 56.3 | UNITS C2-C4, STROOD RETAIL PARK, COMMERCIAL ROAD | ROCHESTER | ME2 2AB | Medway | B & M | Retail Warehouse And Premises | bigbox | 1 | 2361.72 | 25421 | GIA | 467500 | STROOD 132/11KV | inside-area | 0.73 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 3.75 | 213 | 62 | 3316037 | SPN-S000000311554 | 800 | 400 | 40-60% | STROOD 132/11KV | 119 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44052667 | A1/A2 Retail and Financial/Professional services | 387 | B | Natural Gas | 4 |  | Heating and Natural Ventilation | 2017-05-31 |  | 1 | FALSE | 51.3941 | 0.49533 | SPN-S000000009948 | 12652142000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
270 | 56.3 | HOLLYWOOD BOWL, CHARIOT WAY | ROCHESTER | ME2 2SS | Medway |  | Bowling Alley And Premises | bigbox | 1 | 2280 | 24542 | GIA | 195000 | STROOD 132/11KV | inside-area | 2.63 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 3.62 | 182 | 62 | 3316916 | SPN-S000000314434 | 1000 | 300 | 20-40% | STROOD 132/11KV | 222 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3807 | 0.47785 | SPN-S000000009948 | 8967948000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
271 | 56.3 | MEDWAY BUILDERS MERCHANTS, ROYAL EAGLE CLOSE | ROCHESTER | ME2 4NS | Medway |  | Builders Merchants And Premises | bigbox | 1 | 2065.95 | 22238 | GIA | 167000 | STROOD 132/11KV | inside-area | 1.34 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 3.28 | 186 | 62 | 3319220 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44114117 | B2 to B7 General Industrial and Special Industrial Groups | 1152 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-12-08 |  | 0.5 | FALSE | 51.3988 | 0.51893 | SPN-S000000009948 | 13565279000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
272 | 56.3 | BLDG 517, WEST SITE DISCOVERY PARK, RAMSGATE ROAD | SANDWICH | CT13 9NJ | Dover | MYLAN; PFIZERS | Warehouse And Premises; Warehouse, Laboratory And Premises; Workshop And Premises | industrial | 3 | 13134.3 | 141376 | GIA | 2089000 | RICHBOROUGH 33/11KV | inside-area | 2.08 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 62 | 20.87 | 1313 | 29 | 1201642 | SPN-S000000341057 | 1000 | 700 | 60-80% | RICHBOROUGH 33/11KV | 160 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.274 | 1.3408 | SPN-S000000008342 | 9007575000;8582255000;8577558000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
273 | 56.3 | FLAMBEAU EUROPLAST LTD, MANSTON ROAD | RAMSGATE | CT12 6HW | Thanet |  | Factory And Premises | industrial | 1 | 12896.8 | 138820 | GIA | 485000 | RICHBOROUGH 33/11KV | inside-area | 6.15 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 63 | 20.49 | 774 | 29 | 1204198 | SPN-S000000342206 | 800 | 560 | 60-80% | RAMSGATE 33/11KV | 193 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3399 | 1.392 | SPN-S000000008342 | 7199447000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
274 | 56.3 | BLDG 902 235 & 287, EAST SITE DISCOVERY PARK, RAMSGATE ROAD | SANDWICH | CT13 9NJ | Dover |  | Warehouse And Premises; Workshop And Premises | industrial | 3 | 9191 | 98931 | GIA | 954000 | RICHBOROUGH 33/11KV | inside-area | 2.08 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 88 | 14.61 | 414 | 29 | 1244087 | SPN-S000000341057 | 1000 | 700 | 60-80% | RICHBOROUGH 33/11KV | 160 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.274 | 1.3408 | SPN-S000000008342 | 14976057000;9076332000;8777180000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
275 | 56.3 | VANTAGE POINT, SNODLAND BYPASS | SNODLAND | ME6 5SL | Tonbridge & Malling | BIG MOTORING WORLD | Warehouse And Premises | industrial | 2 | 8631.11 | 92904 | GIA | 867000 | HALLING 33/11KV | inside-area | 2.68 | Medway Grid | Kingsnorth | Mid Kent Zone | 12.2 | primary | 12.2 | Green | 24 | 8.5 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 23 | 17.3 | Winter | 64.3478 | 14.8 | Green (Over 5% headroom) | 86988 | 94 | 13.72 | 216 | 3 | 378346 | SPN-S000000392063 | 800 | 560 | 60-80% | HALLING 33/11KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.336 | 0.44605 | SPN-S000000008615 | 10547871000;399576148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
276 | 56.3 | BLDG 281, OLD BAY HOUSE, RIVER ROAD DISCOVERY PARK | SANDWICH | CT13 9FN | Dover |  | Warehouse And Premises | industrial | 1 | 8582.18 | 92378 | GIA | 805000 | RICHBOROUGH 33/11KV | inside-area | 0.65 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 94 | 13.64 | 215 | 29 | 1250640 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.2866 | 1.3485 | SPN-S000000008342 | 13577019000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
277 | 56.3 | AEI COMPOUNDS LTD, SANDWICH INDUSTRIAL ESTATE, RAMSGATE ROAD | SANDWICH | CT13 9LY | Dover |  | Factory And Premises | industrial | 1 | 8422.59 | 90660 | GIA | 310000 | RICHBOROUGH 33/11KV | inside-area | 1.5 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 96 | 13.38 | 505 | 29 | 1252358 | SPN-S000000342599 | 800 | 560 | 60-80% | RICHBOROUGH 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.279 | 1.3505 | SPN-S000000008342 | 7588306000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
278 | 56.3 | UNIT 4, VANTAGE POINT, HOLBOROUGH ROAD | SNODLAND | ME6 5SZ | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 6560.74 | 70619 | GIA | 680000 | HALLING 33/11KV | inside-area | 2.24 | Medway Grid | Kingsnorth | Mid Kent Zone | 12.2 | primary | 12.2 | Green | 24 | 8.5 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 23 | 17.3 | Winter | 64.3478 | 14.8 | Green (Over 5% headroom) | 86988 | 100 | 10.43 | 164 | 3 | 400631 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3399 | 0.44635 | SPN-S000000008615 | 13495442000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
279 | 56.3 | STEVENS & CARLOTTI LTD, RAMSGATE ROAD | SANDWICH | CT13 9ST | Dover |  | Factory And Premises | industrial | 1 | 6344.7 | 68294 | GIA | 360000 | RICHBOROUGH 33/11KV | inside-area | 1.19 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 10.08 | 381 | 29 | 1274724 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062284675 | B2 to B7 General Industrial and Special Industrial Groups | 1236 | C | LPG | 3 |  | Heating and Natural Ventilation | 2014-08-26 |  | 1 | FALSE | 51.303 | 1.3463 | SPN-S000000008342 | 7562868000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
280 | 56.3 | UNIT 4, ARC LOGISTICS PARK, HOLBOROUGH ROAD | SNODLAND | ME6 5SZ | Tonbridge & Malling |  | Warehouse And Premises | industrial | 3 | 5104.08 | 54940 | GIA | 681500 | HALLING 33/11KV | inside-area | 2.24 | Medway Grid | Kingsnorth | Mid Kent Zone | 12.2 | primary | 12.2 | Green | 24 | 8.5 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 23 | 17.3 | Winter | 64.3478 | 14.8 | Green (Over 5% headroom) | 86988 | 100 | 8.11 | 128 | 3 | 416310 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3399 | 0.44635 | SPN-S000000008615 | 13459962000;13439892000;13495676000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
281 | 56.3 | ASH RADAR STATION, MARSHBOROUGH ROAD | SANDWICH | CT13 0PL | Dover |  | Warehouse And Premises | industrial | 1 | 5050.3 | 54361 | GIA | 87500 | RICHBOROUGH 33/11KV | inside-area | 4.13 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 8.03 | 126 | 29 | 1288657 | SPN-R000000834210-000-161Z | 50 | 25 | 40-60% | RICHBOROUGH 33/11KV | 355 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034880209 | B1 Offices and Workshop businesses | 450 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-13 |  | 1 | FALSE | 51.2704 | 1.2991 | SPN-S000000008342 | 511992000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
282 | 56.3 | SENTINEL HOUSE, ARTILLERY WAY, DISCOVERY PARK | SANDWICH | CT13 9FL | Dover |  | Workshop And Premises | industrial | 1 | 4090.56 | 44030 | GIA | 262500 | RICHBOROUGH 33/11KV | inside-area | 0.4 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 6.5 | 184 | 29 | 1298988 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034887538 | B2 to B7 General Industrial and Special Industrial Groups | 1495 | D | Biomass | 4 |  | Mixed-mode with Mechanical Ventilation | 2022-11-01 |  | 1 | FALSE | 51.2888 | 1.3483 | SPN-S000000008342 | 11855932000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
283 | 56.3 | UNITS 51-52, SANDWICH INDUSTRIAL ESTATE, RAMSGATE ROAD | SANDWICH | CT13 9LY | Dover | HOUSE OF ROMNEY | Vehicle Repair Workshop And Premises; Workshop, Offices And Premises | industrial | 2 | 3356.29 | 36127 | GIA | 168000 | RICHBOROUGH 33/11KV | inside-area | 1.5 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 5.33 | 151 | 29 | 1306891 | SPN-S000000342599 | 800 | 560 | 60-80% | RICHBOROUGH 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.279 | 1.3505 | SPN-S000000008342 | 2539247000;125622145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
284 | 56.3 | ARCHITECTURAL VISION SYSTEMS LTD, AMBROSETTI SITE, RAMSGATE ROAD | SANDWICH | CT13 9QN | Dover |  | Workshop And Premises | industrial | 1 | 2291.52 | 24666 | GIA | 138000 | RICHBOROUGH 33/11KV | inside-area | 1.88 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.64 | 103 | 29 | 1318352 | SPN-S000000343069 | 200 | 140 | 60-80% | RICHBOROUGH 33/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3091 | 1.3502 | SPN-S000000008342 | 14894493000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
285 | 56.3 | UNITS B1 AND B2, CHANNEL VIEW ROAD | RAMSGATE | CT12 4EX | Thanet |  | Warehouse, Office And Premises | industrial | 1 | 2284.55 | 24591 | GIA | 135000 | RICHBOROUGH 33/11KV | inside-area | 5.54 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.63 | 160 | 29 | 1318427 | SPN-S000000342155 | 315 | 94 | 20-40% | RICHBOROUGH 33/11KV | 189 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062283961 | B8 Storage or Distribution | 977 | A | Other | 4 |  | Unconditioned | 2020-04-28 |  | 0.5 | FALSE | 51.34 | 1.324 | SPN-S000000008342 | 10862368000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
286 | 56.3 | UNIT B3, CHANNEL VIEW ROAD | RAMSGATE | CT12 4EX | Thanet |  | Warehouse And Premises | industrial | 1 | 2241.74 | 24130 | GIA | 128000 | RICHBOROUGH 33/11KV | inside-area | 5.54 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.56 | 56 | 29 | 1318888 | SPN-S000000342155 | 315 | 94 | 20-40% | RICHBOROUGH 33/11KV | 189 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062283961 | B8 Storage or Distribution | 977 | A | Other | 4 |  | Unconditioned | 2020-04-28 |  | 0.67 | FALSE | 51.34 | 1.324 | SPN-S000000008342 | 10169190000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
287 | 56.3 | UNITS 5A & 5B LOWER SITE OLD TIMBER YARD, MANSTON ROAD | RAMSGATE | CT12 6HJ | Thanet |  | Warehouse And Premises | industrial | 1 | 2195.59 | 23633 | GIA | 137000 | RICHBOROUGH 33/11KV | inside-area | 5.95 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.49 | 55 | 29 | 1319385 | SPN-S000000342575 | 315 | 220 | 60-80% | RAMSGATE 33/11KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013310709 | B8 Storage or Distribution | 929 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-12-02 |  | 1 | FALSE | 51.3394 | 1.3877 | SPN-S000000008342 | 14019653000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
288 | 56.3 | 1, DISCOVERY PARK, MONTAGU ROAD, RAMSGATE ROAD | SANDWICH | CT13 9FA | Dover |  | Warehouse And Premises | industrial | 1 | 2082.7 | 22418 | GIA | 149000 | RICHBOROUGH 33/11KV | inside-area | 0.83 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.31 | 52 | 29 | 1320600 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.288 | 1.3371 | SPN-S000000008342 | 10979363000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
289 | 56.3 | DPH 1N 001 1ST FLR DISCOVERY PARK HOUSE BLDG 530, RAMSGATE ROAD, DISCOVERY PARK | SANDWICH | CT13 9ND | Dover |  | Laboratory And Premises | industrial | 1 | 1953.2 | 21024 | NIA | 367500 | RICHBOROUGH 33/11KV | inside-area | 0.93 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.1 | 195 | 29 | 1321994 | SPN-S000000341051 | 800 | 720 | 80-100% | RICHBOROUGH 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034887858 | General Industrial and Special Industrial Groups | 4597 | A | District Heating | 4 | 3 | Heating and Natural Ventilation | 2022-10-05 |  | 0.5 | FALSE | 51.284 | 1.3457 | SPN-S000000008342 | 15113135000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
290 | 55.7 | CHANNEL HOUSE, CHANNEL VIEW ROAD | DOVER | CT17 9TP | Dover |  | Offices And Premises | office | 1 | 11374.6 | 122435 | NIA | 565000 | DOVER 33/11KV | inside-area | 1.35 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 18.08 | 796 | 39 | 1261986 | SPN-S000000363206 | 800 | 560 | 60-80% | DOVER 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062290113 | B1 Offices and Workshop businesses | 2172 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-10-05 |  | 1 | FALSE | 51.1176 | 1.3053 | SPN-S000000008391 | 127073145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
291 | 55.7 | PRIORY COURT, ST JOHNS ROAD | DOVER | CT17 9SE | Dover |  | Offices And Premises | office | 1 | 7320.86 | 78801 | NIA | 407500 | DOVER 33/11KV | inside-area | 0.65 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 11.63 | 512 | 39 | 1305620 | SPN-S000000364678 | 500 | 250 | 40-60% | DOVER 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1253 | 1.3041 | SPN-S000000008391 | 2254655000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
292 | 55.7 | DOVER DISTRICT COUNCIL, HONEYWOOD CLOSE | DOVER | CT16 3PJ | Dover |  | Offices And Premises | office | 1 | 5285.4 | 56892 | NIA | 307500 | DOVER 33/11KV | inside-area | 3.03 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 8.4 | 370 | 39 | 1327529 | SPN-S000000364215 | 1000 | 700 | 60-80% | DOVER 33/11KV | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1544 | 1.2948 | SPN-S000000008391 | 10584672000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
293 | 55.7 | UNIT 5, CHANNEL VIEW ROAD | DOVER | CT17 9TP | Dover |  | Offices And Premises; Warehouse And Premises | office | 2 | 3777.76 | 40663 | NIA | 240000 | DOVER 33/11KV | inside-area | 1.35 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 6 | 264 | 39 | 1343758 | SPN-S000000363206 | 800 | 560 | 60-80% | DOVER 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062290113 | B1 Offices and Workshop businesses | 2172 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-10-05 |  | 0.67 | FALSE | 51.1176 | 1.3053 | SPN-S000000008391 | 13429074000;14110988000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
294 | 55.7 | OPERATIONS CENTRE, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0LS | Medway | LLOYDS BANKS PLC | Offices And Premises | office | 1 | 3461.22 | 37256 | NIA | 525000 | RAINHAM MARK 33/11KV | inside-area | 0.42 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 5.5 | 242 | 37 | 2350989 | SPN-S000000314028 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 59 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | B1 Offices and Workshop businesses | 4484 | E | Natural Gas | 4 |  | Air Conditioning | 2021-04-27 |  | 1 | FALSE | 51.3662 | 0.57554 | SPN-S000000008525 | 391281147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
295 | 55.7 | 21B, BAILEY COURT, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1800.78 | 19383 | GIA | 185000 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 2.86 | 81 | 37 | 2368862 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000901172 | B2 to B7 General Industrial and Special Industrial Groups | 3458 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-10-23 |  | 0.67 | FALSE | 51.3645 | 0.57398 | SPN-S000000008525 | 389348147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
296 | 55.7 | INTERNATIONAL HOUSE, WHITE CLIFFS BUSINESS PARK, HONEYWOOD CLOSE | DOVER | CT16 3PX | Dover |  | Warehouse And Premises | industrial | 1 | 1425.15 | 15340 | GIA | 138000 | DOVER 33/11KV | inside-area | 2.93 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.26 | 36 | 39 | 1369081 | SPN-S000000364215 | 1000 | 700 | 60-80% | DOVER 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1536 | 1.2953 | SPN-S000000008391 | 8866301000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
297 | 55.7 | FOLKESTONE SCAFFOLDING, ASTLEY AVENUE | DOVER | CT16 2NJ | Dover |  | Workshop And Premises | industrial | 1 | 1421.02 | 15296 | GIA | 52000 | DOVER 33/11KV | inside-area | 1.03 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.26 | 64 | 39 | 1369125 | SPN-S000000363165 | 500 | 250 | 40-60% | DOVER 33/11KV | 163 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1382 | 1.308 | SPN-S000000008391 | 13475324000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
298 | 55.7 | MECHANICA UTILITES LTD, PORT VIEW HOUSE, CHANNEL VIEW ROAD | DOVER | CT17 9TP | Dover |  | Factory And Premises | industrial | 1 | 1393.43 | 14999 | GIA | 85000 | DOVER 33/11KV | inside-area | 1.35 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.21 | 84 | 39 | 1369422 | SPN-S000000363206 | 800 | 560 | 60-80% | DOVER 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062290113 | B1 Offices and Workshop businesses | 2172 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-10-05 |  | 0.5 | FALSE | 51.1176 | 1.3053 | SPN-S000000008391 | 13523766000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
299 | 55.7 | UNITS AT, SOUTH MILITARY ROAD | DOVER | CT17 9UE | Dover |  | Warehouse And Premises | industrial | 1 | 1328.5 | 14300 | GIA | 94500 | DOVER 33/11KV | inside-area | 1.49 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.11 | 33 | 39 | 1370121 | SPN-R000000839118-000-014Z | 100 | 50 | 40-60% | DOVER 33/11KV | 245 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034888913 | Offices and Workshop Businesses | 314 | C | LPG | 3 |  | Heating and Natural Ventilation | 2022-10-18 |  | 1 | FALSE | 51.1169 | 1.3025 | SPN-S000000008391 | 9648788000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
300 | 55.7 | WINCHELSEA WORKS, FOLKESTONE ROAD | DOVER | CT17 9SS | Dover |  | Factory And Premises | industrial | 1 | 1294.5 | 13934 | GIA | 71000 | DOVER 33/11KV | inside-area | 1 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.06 | 78 | 39 | 1370487 | SPN-S000000363218 | 800 | 400 | 40-60% | DOVER 33/11KV | 194 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062290472 | B2 to B7 General Industrial and Special Industrial Groups | 1199 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-01-31 |  | 0.67 | FALSE | 51.1259 | 1.2977 | SPN-S000000008391 | 7704790000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
301 | 55.7 | B C CERAMICS LTD, BLOORS LANE | GILLINGHAM | ME8 7EG | Medway |  | Warehouse And Premises | industrial | 1 | 1283.6 | 13817 | GIA | 71500 | RAINHAM MARK 33/11KV | inside-area | 1.39 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 2.04 | 32 | 37 | 2374428 | SPN-S000000312045 | 750 | 375 | 40-60% | RAINHAM MARK 33/11KV | 108 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062630535 | Storage or Distribution | 1319 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-07-05 |  | 1 | FALSE | 51.3672 | 0.5972 | SPN-S000000008525 | 1679836000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
302 | 55.7 | FREIGHT SEARCH CANOPY, LOWER ROAD WEST, EASTERN DOCKS | DOVER | CT16 1JA | Dover |  | Warehouse And Premises | industrial | 1 | 1277.05 | 13746 | NIA | 30250 | DOVER 33/11KV | inside-area | 1.66 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.03 | 32 | 39 | 1370675 | SPN-R000000839108-000-189Z | 100 | 70 | 60-80% | DOVER 33/11KV | 353 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Offices and Workshop Businesses | 1077 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-12-06 |  | 0.67 | FALSE | 51.1292 | 1.3349 | SPN-S000000008391 | 11909891000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
303 | 55.7 | 5-6, SARACEN CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0QN | Medway |  | Warehouse And Premises | industrial | 1 | 1252.53 | 13482 | GIA | 131000 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 1.99 | 31 | 37 | 2374763 | SPN-S000000314028 | 800 | 560 | 60-80% | RAINHAM MARK 33/11KV | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000901192 | Storage or Distribution | 222 | B | Grid Supplied Electricity | 5 |  | Air Conditioning | 2026-02-04 |  | 1 | FALSE | 51.3658 | 0.57625 | SPN-S000000008525 | 389634147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
304 | 55.7 | PT LOWER GND FLR, TOWN HALL, HIGH STREET | DOVER | CT16 1DL | Dover | DOVER DISTRICT COUNCIL | Store And Premises | industrial | 1 | 1248 | 13433 | GIA | 36500 | DOVER 33/11KV | inside-area | 0.18 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.98 | 31 | 39 | 1370988 | SPN-S000000363170 | 500 | 250 | 40-60% | DOVER 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1282 | 1.309 | SPN-S000000008391 | 3648212000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
305 | 55.7 | GRANVILLE STREET | DOVER | CT16 2LG | Dover | ROYAL MAIL | Sorting Office And Premises | industrial | 1 | 1161.2 | 12499 | GIA | 69500 | DOVER 33/11KV | inside-area | 0.53 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.85 | 81 | 39 | 1371922 | SPN-S000000363176 | 800 | 560 | 60-80% | DOVER 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062289189 | A1/A2 Retail and Financial/Professional services | 1085 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-12-03 |  | 1 | FALSE | 51.1323 | 1.3054 | SPN-S000000008391 | 533982145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
306 | 55.7 | WAREHOUSE F AND G BIG OFFICES WHITECLIFF HOUSE, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 1 | 1148.51 | 12362 | GIA | 73000 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.83 | 29 | 39 | 1372059 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Storage or Distribution | 371 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-03-21 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 15096929000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
307 | 55.7 | COOMBE ROAD | DOVER | CT17 0LQ | Dover | BUCKLAND PRESS LTD | Factory And Premises | industrial | 1 | 1139.6 | 12267 | GIA | 48250 | DOVER 33/11KV | inside-area | 2.15 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.81 | 68 | 39 | 1372154 | SPN-S000000363943 | 315 | 220 | 60-80% | DOVER 33/11KV | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034891787 | B8 Storage or Distribution | 218 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-12-07 |  | 1 | FALSE | 51.1326 | 1.2807 | SPN-S000000008391 | 123947145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
308 | 55.7 | 7-8, SARACEN CLOSE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PY | Medway |  | Workshop And Premises | industrial | 1 | 1129.1 | 12154 | GIA | 117000 | RAINHAM MARK 33/11KV | inside-area | 0.23 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 1.79 | 51 | 37 | 2376091 | SPN-S000000313856 | 1000 | 700 | 60-80% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000901181 | Storage or Distribution | 505 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-08-26 |  | 0.67 | FALSE | 51.3649 | 0.57796 | SPN-S000000008525 | 389635147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
309 | 55.7 | JENKINS & PAIN, WHITE CLIFFS BUSINESS PARK | DOVER | CT16 3EH | Dover |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1089 | 11722 | GIA | 94000 | DOVER 33/11KV | inside-area | 3.08 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.73 | 49 | 39 | 1372699 | SPN-S000000363044 | 500 | 250 | 40-60% | DOVER 33/11KV | 11 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.154 | 1.2916 | SPN-S000000008391 | 1886976000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
310 | 55.7 | WAREHOUSE A BIG OFFICES WHITECLIFF HOUSE, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 1 | 1082.5 | 11652 | GIA | 76500 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.72 | 27 | 39 | 1372769 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Storage or Distribution | 861 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-03-21 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 15096920000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
311 | 55.7 | UNIT 3, MEDWAY DISTRIBUTION CENTRE, COURTENEY ROAD | GILLINGHAM | ME8 0RT | Medway |  | Workshop And Premises | industrial | 1 | 1058.94 | 11398 | GIA | 115000 | RAINHAM MARK 33/11KV | inside-area | 0.15 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 1.68 | 48 | 37 | 2376847 | SPN-S000000311994 | 750 | 675 | 80-100% | RAINHAM MARK 33/11KV | 200 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44012699 | General Industrial and Special Industrial Groups | 1253 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2026-04-20 |  | 1 | FALSE | 51.3633 | 0.58046 | SPN-S000000008525 | 2476548000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
312 | 55.7 | UNITS 1-3, HOLMESTONE ROAD | DOVER | CT17 0UF | Dover |  | Warehouse And Premises | industrial | 1 | 1058.8 | 11397 | GIA | 69500 | DOVER 33/11KV | inside-area | 2.42 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.68 | 26 | 39 | 1373024 | SPN-S000000363982 | 500 | 250 | 40-60% | DOVER 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034877777 | B2 to B7 General Industrial and Special Industrial Groups | 545 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-03-13 |  | 0.5 | FALSE | 51.1319 | 1.2767 | SPN-S000000008391 | 3441343000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
313 | 55.7 | UNITS 2 & 3, POULTON ENGINEERING WORKS, POULTON CLOSE | DOVER | CT17 0HL | Dover |  | Warehouse And Premises | industrial | 1 | 1008.81 | 10859 | GIA | 73500 | DOVER 33/11KV | inside-area | 2.19 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.6 | 25 | 39 | 1373562 | SPN-S000000361065 | 1000 | 500 | 40-60% | DOVER 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062662806 | Storage or Distribution | 115 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-06-26 |  | 1 | FALSE | 51.1313 | 1.2799 | SPN-S000000008391 | 7133812000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
314 | 54.8 | PINEWOOD HOUSE, BEXLEY HOSPITAL, OLD BEXLEY LANE | BEXLEY | DA5 2BW | Dartford |  | Offices And Premises | office | 1 | 1235.62 | 13300 | NIA | 215000 | CRAYFORD | inside-area | 2.16 | Dartford Grid 33kV | Littlebrook | SOUTH EAST | 23.1 | primary | 23.1 | Green | 58.5 | 30.7 | Thermal | 3.8 | 11 | 0 | 14.8 | 14.2 | Dartford Grid A 33kV | 64.9 | GREEN | 139 |  | RED | 2 | 21.5 | 0 | 56.7 | 42.8 | Winter | 47.4427 | 26.9 | Green (Over 5% headroom) | 164706 | 100 | 1.96 | 86 | 0 | 0 | LPN-S000000074105 | 500 | 450 | 80-100% | CRAYFORD | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4333 | 0.17466 | LPN-S000000000715 | 4005833000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
315 | 54.7 | WESTWOOD INDUSTRIAL ESTATE, RAMSGATE ROAD | MARGATE | CT9 4JD | Thanet | B & Q RETAIL LTD | Retail Warehouse And Premises | bigbox | 1 | 4763.6 | 51275 | GIA | 417500 | MARGATE 33/11KV | inside-area | 1.63 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 7.57 | 429 | 24 | 513336 | SPN-S000000343250 | 500 | 350 | 60-80% | THANET 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3672 | 1.3882 | SPN-S000000008655 | 456503145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
316 | 54.7 | 55, ADDINGTON STREET | MARGATE | CT9 1PW | Thanet |  | Retail Warehouse And Premises | bigbox | 1 | 2011.51 | 21652 | GIA | 211000 | MARGATE 33/11KV | inside-area | 0.88 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 3.2 | 181 | 24 | 542959 | SPN-S000000341985 | 500 | 350 | 60-80% | MARGATE 33/11KV | 150 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100061117885 | A1/A2 Retail and Financial/Professional services | 2149 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-04-12 |  | 0.5 | FALSE | 51.3878 | 1.3854 | SPN-S000000008655 | 9687968000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
317 | 54.7 | HILTON ROAD | ASHFORD | TN23 1EW | Ashford | D G MORTIMER & CO LTD; M J ALLEN LTD | Factory And Premises; Warehouse And Premises | industrial | 3 | 8228.98 | 88576 | GIA | 491000 | SINGLETON 33/6.6KV | inside-area | 0.69 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 89 | 13.08 | 494 | 24 | 659538 | SPN-S000000364905 | 500 | 350 | 60-80% | SINGLETON 33/6.6KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004391112 | B8 Storage or Distribution | 6211 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2015-05-13 |  | 1 | FALSE | 51.1506 | 0.8544 | SPN-S000000008610 | 403374148;532933145;13607041000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
318 | 54.7 | LEACON ROAD | ASHFORD | TN23 4TU | Ashford | GRIFFIN & BRAND (EUROPEAN) LTD | Warehouse And Premises | industrial | 1 | 4768.87 | 51332 | GIA | 387500 | SINGLETON 33/6.6KV | inside-area | 0.63 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 7.58 | 119 | 24 | 696782 | SPN-S000000363944 | 1000 | 700 | 60-80% | SINGLETON 33/6.6KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004391625 | B8 Storage or Distribution | 108 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2016-03-02 |  | 1 | FALSE | 51.1467 | 0.85614 | SPN-S000000008610 | 329071148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
319 | 54.7 | MPT HOUSE, BRUNSWICK ROAD | ASHFORD | TN23 1EL | Ashford |  | Factory And Premises | industrial | 1 | 4574.1 | 49235 | GIA | 236000 | SINGLETON 33/6.6KV | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 7.27 | 274 | 24 | 698879 | SPN-S000000361812 | 1000 | 500 | 40-60% | SINGLETON 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004396262 | General Industrial and Special Industrial Groups | 4649 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2025-06-05 |  | 1 | FALSE | 51.1493 | 0.85381 | SPN-S000000008610 | 6429877000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
320 | 54.7 | PT GND & 1ST FLR BAY 2 UNIT 2, BRUNSWICK ROAD | ASHFORD | TN23 1EH | Ashford |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 4469.55 | 48110 | NIA | 219000 | SINGLETON 33/6.6KV | inside-area | 0.73 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 7.1 | 201 | 24 | 700004 | SPN-S000000362211 | 500 | 350 | 60-80% | SINGLETON 33/6.6KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012875494 | General Assembly and Leisure, Night Clubs, and Theatres | 1152 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-11-21 |  | 0.5 | FALSE | 51.1494 | 0.85636 | SPN-S000000008610 | 12024638000;526289145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
321 | 54.7 | UNIT 7, COBBS WOOD INDUSTRIAL ESTATE, BRUNSWICK ROAD | ASHFORD | TN23 1EH | Ashford |  | Workshop, Office & Premises | industrial | 1 | 4189.8 | 45099 | GIA | 320000 | SINGLETON 33/6.6KV | inside-area | 0.73 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 6.66 | 189 | 24 | 703015 | SPN-S000000362211 | 500 | 350 | 60-80% | SINGLETON 33/6.6KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1494 | 0.85636 | SPN-S000000008610 | 1485954000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
322 | 54.7 | V J TECHNOLOGY LTD, BRUNSWICK ROAD | ASHFORD | TN23 1EN | Ashford |  | Warehouse And Premises | industrial | 1 | 4169.5 | 44880 | GIA | 163000 | SINGLETON 33/6.6KV | inside-area | 0.62 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 6.63 | 104 | 24 | 703234 | SPN-S000000361812 | 1000 | 500 | 40-60% | SINGLETON 33/6.6KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004396244 | B1 Offices and Workshop businesses | 338 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-06-03 |  | 1 | FALSE | 51.1503 | 0.85339 | SPN-S000000008610 | 2303833000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
323 | 54.7 | VATRE TERRACOTTA LTD, LEACON ROAD | ASHFORD | TN23 4FH | Ashford |  | Warehouse And Premises | industrial | 1 | 4030.9 | 43388 | GIA | 262500 | SINGLETON 33/6.6KV | inside-area | 0.86 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 6.41 | 101 | 24 | 704726 | SPN-S000000364587 | 800 | 560 | 60-80% | SINGLETON 33/6.6KV | 41 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1463 | 0.85945 | SPN-S000000008610 | 11374006000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
324 | 54.7 | UNITS 3 & 4, COBBS WOOD INDUSTRIAL ESTATE, BRUNSWICK ROAD | ASHFORD | TN23 1EL | Ashford |  | Factory And Premises; Warehouse And Premises | industrial | 2 | 3871.09 | 41668 | GIA | 280000 | SINGLETON 33/6.6KV | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 6.15 | 232 | 24 | 706446 | SPN-S000000361812 | 1000 | 500 | 40-60% | SINGLETON 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004396248 | General Industrial and Special Industrial Groups | 1971 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2023-04-28 |  | 0.75 | FALSE | 51.1493 | 0.85381 | SPN-S000000008610 | 3713384000;8169345000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
325 | 54.7 | UNIT 1, FAIRWOOD INDUSTRIAL PARK, LEACON ROAD | ASHFORD | TN23 4TT | Ashford |  | Warehouse And Premises | industrial | 1 | 3046.6 | 32793 | GIA | 203000 | SINGLETON 33/6.6KV | inside-area | 0.76 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 4.84 | 76 | 24 | 715321 | SPN-S000000364492 | 1000 | 700 | 60-80% | SINGLETON 33/6.6KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062617947 | General Industrial and Special Industrial Groups | 2375 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-07-12 |  | 1 | FALSE | 51.1472 | 0.85804 | SPN-S000000008610 | 331570148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
326 | 54.7 | ASPIRE LANDSCAPE MANAGEMENT, CARLTON BUSINESS PARK, CARLTON ROAD | ASHFORD | TN23 1EF | Ashford |  | Storage Depot And Premises | industrial | 1 | 2545.99 | 27405 | OTH | 67000 | SINGLETON 33/6.6KV | inside-area | 0.94 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 4.05 | 64 | 24 | 720709 | SPN-S000000371615 | 1000 | 700 | 60-80% | SINGLETON 33/6.6KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1495 | 0.85965 | SPN-S000000008610 | 10567390000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
327 | 54.7 | TOP WORKSHOP, CHART LEACON DEPOT, BRUNSWICK ROAD | ASHFORD | TN23 1EL | Ashford |  | Workshop And Premises | industrial | 1 | 2144.27 | 23081 | GIA | 129000 | SINGLETON 33/6.6KV | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 3.41 | 96 | 24 | 725033 | SPN-S000000361812 | 1000 | 500 | 40-60% | SINGLETON 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062558194 | Offices and Workshop Businesses | 1785 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-03-10 |  | 0.67 | FALSE | 51.1493 | 0.85381 | SPN-S000000008610 | 14759366000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
328 | 54.7 | UNITS A & B AT 6-7, HILTON ROAD | ASHFORD | TN23 1EW | Ashford |  | Warehouse And Premises | industrial | 1 | 2039.88 | 21957 | GIA | 106000 | SINGLETON 33/6.6KV | inside-area | 0.69 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 3.24 | 51 | 24 | 726157 | SPN-S000000364905 | 500 | 350 | 60-80% | SINGLETON 33/6.6KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012860608 | General Industrial and Special Industrial Groups | 572 | B | Other | 3 |  | Unconditioned | 2022-11-08 |  | 1 | FALSE | 51.1506 | 0.8544 | SPN-S000000008610 | 9825391000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
329 | 54.7 | NUMBER ONE, CARLTON ROAD | ASHFORD | TN23 1DP | Ashford |  | Warehouse And Premises | industrial | 1 | 1999.9 | 21527 | GIA | 200000 | SINGLETON 33/6.6KV | inside-area | 0.91 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 3.18 | 50 | 24 | 726587 | SPN-S000000371615 | 1000 | 700 | 60-80% | SINGLETON 33/6.6KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004391085 | Storage or Distribution | 1695 | A | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-08-07 |  | 0.67 | FALSE | 51.15 | 0.8588 | SPN-S000000008610 | 15117377000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
330 | 54.3 | DAVID LLOYD LEISURE LTD, DARENTH ROAD | DARTFORD | DA1 1NJ | Dartford |  | Leisure Centre And Premises | bigbox | 1 | 9605.7 | 103395 | GIA | 425000 | DARTFORD GRID B 11KV | inside-area | 1.49 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 15.26 | 768 | 54 | 2669354 | LPN-S000000072212 | 750 | 525 | 60-80% | DARTFORD GRID B 11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10009428525 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 9436 | B | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2016-05-17 |  | 1 | FALSE | 51.4391 | 0.22536 | LPN-S000000000716 | 15147307000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
331 | 54.3 | NEXT GENERATION, DARENTH ROAD | DARTFORD | DA1 1NJ | Dartford |  | Leisure Centre And Premises | bigbox | 1 | 9605.7 | 103395 | GIA | 425000 | DARTFORD GRID B 11KV | inside-area | 1.49 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 15.26 | 768 | 54 | 2669354 | LPN-S000000072212 | 750 | 525 | 60-80% | DARTFORD GRID B 11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4391 | 0.22536 | LPN-S000000000716 | 8675203000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
332 | 54.3 | HAWLEY GARDEN CENTRE, HAWLEY ROAD | DARTFORD | DA2 7RB | Dartford |  | Garden Centre And Premises | bigbox | 1 | 5410.72 | 58240 | NIA | 93000 | DARTFORD GRID B 11KV | inside-area | 3.42 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 8.6 | 487 | 54 | 2714509 | SPN-S000000324404 | 315 | 158 | 40-60% | DARTFORD 132/11KV | 178 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000538763 | Retail/Financial and Professional Services | 2714 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-01-13 |  | 1 | FALSE | 51.4214 | 0.23119 | LPN-S000000000716 | 168102147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
333 | 54.3 | HOMEBASE LTD, PRINCES ROAD | DARTFORD | DA1 1LA | Dartford |  | Retail Warehouse And Premises | bigbox | 1 | 4532.53 | 48788 | GIA | 490000 | DARTFORD GRID B 11KV | inside-area | 1.43 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 7.2 | 408 | 54 | 2723961 | LPN-S000000073568 | 500 | 250 | 40-60% | DARTFORD GRID B 11KV | 183 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4375 | 0.2185 | LPN-S000000000716 | 11098682000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
334 | 54.3 | SAINSBURYS PLC, PRIORY SHOPPING CENTRE | DARTFORD | DA1 2HL | Dartford |  | Superstore And Premises | bigbox | 1 | 4241.98 | 45660 | GIA | 900000 | DARTFORD GRID B 11KV | inside-area | 0.71 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 6.74 | 382 | 54 | 2727089 | LPN-S000000073724 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 14 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000533539 | A1/A2 Retail and Financial/Professional services | 4263 | D | Natural Gas | 4 |  | Air Conditioning | 2017-12-13 |  | 0.67 | FALSE | 51.4438 | 0.21546 | LPN-S000000000716 | 14708186000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
335 | 54.3 | OVERY STREET | DARTFORD | DA1 1UP | Dartford | WICKES | Retail Warehouse And Premises | bigbox | 1 | 3641.14 | 39193 | GIA | 467500 | DARTFORD GRID B 11KV | inside-area | 0.8 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 5.79 | 328 | 54 | 2733556 | LPN-S000000072063 | 750 | 525 | 60-80% | DARTFORD GRID B 11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 100060870555 | A3/A4/A5 Restaurant and Cafes/Drinking Establishments and Hot Food takeaways | 247 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-02-22 |  | 1 | FALSE | 51.4452 | 0.22136 | LPN-S000000000716 | 67204000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
336 | 54.3 | 370, PRINCES ROAD | DARTFORD | DA1 1LN | Dartford |  | Car Showroom And Premises | bigbox | 1 | 3454.19 | 37181 | GIA | 520000 | DARTFORD GRID B 11KV | inside-area | 1.43 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 5.49 | 311 | 54 | 2735568 | LPN-S000000073568 | 500 | 250 | 40-60% | DARTFORD GRID B 11KV | 147 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 100062308091 | Retail/Financial and Professional Services | 3564 | C | Natural Gas | 4 |  | Heating and Natural Ventilation | 2026-03-12 |  | 1 | FALSE | 51.4373 | 0.21645 | LPN-S000000000716 | 400138000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
337 | 54.3 | 47-49, HIGH STREET | DARTFORD | DA1 1DJ | Dartford |  | Supermarket And Premises | bigbox | 1 | 2496.46 | 26872 | GIA | 180000 | DARTFORD GRID B 11KV | inside-area | 0.86 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.97 | 225 | 54 | 2745877 | LPN-S000000072002 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 83 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000532112 | Retail/Financial and Professional Services | 2685 | D | Grid Supplied Electricity | 3 | 3 | Air Conditioning | 2022-11-15 |  | 1 | FALSE | 51.4437 | 0.21998 | LPN-S000000000716 | 2840361000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
338 | 54.3 | 171-173, THE BRENT | DARTFORD | DA2 6DG | Dartford |  | Car Showroom And Premises | bigbox | 1 | 2158.3 | 23232 | GIA | 210000 | DARTFORD GRID B 11KV | inside-area | 2.06 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.43 | 194 | 54 | 2749517 | LPN-S000000072132 | 500 | 150 | 20-40% | DARTFORD GRID B 11KV | 166 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4424 | 0.23973 | LPN-S000000000716 | 18263147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
339 | 54.3 | UNITS 1A & 1B, DARTFORD HEATH RETAIL PARK, HEATH LANE | DARTFORD | DA1 2DS | Dartford |  | Retail Warehouse And Premises | bigbox | 1 | 2071.05 | 22293 | GIA | 377500 | DARTFORD GRID B 11KV | inside-area | 1.38 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 3.29 | 186 | 54 | 2750456 | LPN-S000000073575 | 750 | 375 | 40-60% | DARTFORD GRID B 11KV | 184 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10009429741 | Retail/Financial and Professional Services | 3957 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-05-28 |  | 0.6 | FALSE | 51.439 | 0.2027 | LPN-S000000000716 | 7990073000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
340 | 53.8 | ELM COURT GARDEN CENTRE, ELM COURT, CAPSTONE ROAD | GILLINGHAM | ME7 3JQ | Medway |  | Garden Centre And Premises | bigbox | 1 | 8875.24 | 95532 | GIA | 195000 | LORDSWOOD 33/11KV | inside-area | 1.29 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 100 | 14.1 | 799 | 6 | 362154 | SPN-S000000311920 | 500 | 250 | 40-60% | LORDSWOOD 33/11KV | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44040785 | A1/A2 Retail and Financial/Professional services | 101 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2018-04-20 |  | 1 | FALSE | 51.3402 | 0.55816 | SPN-S000000008646 | 13448390000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
341 | 53.3 | COPENHAGEN CANDLE COMPANY LTD, MAIDSTONE ROAD | TONBRIDGE | TN12 7HA | Tunbridge Wells |  | Warehouse And Premises Distribution | industrial | 1 | 2822.07 | 30376 | GIA | 227000 | TUNBRIDGE WELLS GRID 132/11 | inside-area | 5.63 | Tunbridge Wells Total | Northfleet | West Kent Zone | 10 | primary | 10 | Green | 38.1 | 26.5 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 36.2 | 28.5 | Winter | 30.3867 | 11 | Green (Over 5% headroom) | 71301 | 100 | 4.48 | 71 | 1 | 26604 | SPN-S000000442066 | 200 | 20 | 0-20% | PADDOCK WOOD 33/11KV | 139 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008659166 | Offices and Workshop Businesses | 175 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-09-09 |  | 1 | FALSE | 51.139 | 0.35373 | SPN-S000000009351 | 11072901000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
342 | 53.3 | DISTRIBUTION CENTRE, HASTINGS ROAD | TONBRIDGE | TN12 7HF | Tunbridge Wells |  | Storage Depot And Premises | industrial | 1 | 2471.6 | 26604 | GIA | 176000 | TUNBRIDGE WELLS GRID 132/11 | inside-area | 5.89 | Tunbridge Wells Total | Northfleet | West Kent Zone | 10 | primary | 10 | Green | 38.1 | 26.5 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 36.2 | 28.5 | Winter | 30.3867 | 11 | Green (Over 5% headroom) | 71301 | 100 | 3.93 | 62 | 1 | 30376 | SPN-R000000935108-000-146Z | 100 | 70 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 255 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1323 | 0.35568 | SPN-S000000009351 | 8305771000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
343 | 52.9 | CHARLES RIVER UK LTD, MANSTON ROAD | MARGATE | CT9 4LT | Thanet |  | Laboratory And Premises | industrial | 1 | 5940.96 | 63948 | GIA | 252500 | THANET 33/11KV | inside-area | 2.61 | Thanet Grid | Richborough | East Kent Zone | 9.7 | primary | 9.7 | Green | 26 | 12.9 | Thermal | 1 | 2.1 | 0 | 3.1 | 8.7 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | Green (Over 5% headroom) | 69162 | 100 | 9.44 | 594 | 5 | 166332 | SPN-S000000343208 | 500 | 450 | 80-100% | THANET 33/11KV | 122 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3546 | 1.3587 | SPN-S000000008349 | 11445721000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
344 | 52.9 | CHARLES ANTONY HOUSE, MANSTON ROAD | MARGATE | CT9 4JW | Thanet |  | Warehouse, Office , Storage Land And Premises | industrial | 1 | 2364.3 | 25449 | GIA | 228000 | THANET 33/11KV | inside-area | 2.46 | Thanet Grid | Richborough | East Kent Zone | 9.7 | primary | 9.7 | Green | 26 | 12.9 | Thermal | 1 | 2.1 | 0 | 3.1 | 8.7 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | Green (Over 5% headroom) | 69162 | 100 | 3.76 | 166 | 5 | 204831 | SPN-S000000343208 | 500 | 450 | 80-100% | THANET 33/11KV | 191 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3575 | 1.3585 | SPN-S000000008349 | 9815444000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
345 | 52.9 | SECURE STORAGE SOLUTIONS, MANSTON ROAD | MARGATE | CT9 4JW | Thanet |  | Warehouse And Premises | industrial | 1 | 2232.97 | 24035 | GIA | 171000 | THANET 33/11KV | inside-area | 2.46 | Thanet Grid | Richborough | East Kent Zone | 9.7 | primary | 9.7 | Green | 26 | 12.9 | Thermal | 1 | 2.1 | 0 | 3.1 | 8.7 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | Green (Over 5% headroom) | 69162 | 100 | 3.55 | 56 | 5 | 206245 | SPN-S000000343208 | 500 | 450 | 80-100% | THANET 33/11KV | 191 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3575 | 1.3585 | SPN-S000000008349 | 12171727000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
346 | 52.7 | WILL ADAMS WAY | GILLINGHAM | ME8 6BY | Medway | B & Q | Retail Warehouse And Premises | bigbox | 1 | 14744.26 | 158706 | GIA | 1460000 | RAINHAM MARK 33/11KV | inside-area | 0.9 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 87 | 23.43 | 1327 | 37 | 2229539 | SPN-S000000313972 | 300 | 150 | 40-60% | CHATHAM HILL 33/11KV | 202 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44115381 | C1 Hotels | 2499 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-08-24 |  | 1 | FALSE | 51.3691 | 0.57003 | SPN-S000000008525 | 4941414000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
347 | 52.7 | PHILLIPS HOUSE & EYNSHAM HOUSE, CRESCENT ROAD | TUNBRIDGE WELLS | TN1 2LY | Tunbridge Wells |  | Offices And Premises | office | 1 | 5644.49 | 60757 | NIA | 865000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.9 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 8.97 | 395 | 13 | 353299 | SPN-S000000444011 | 500 | 350 | 60-80% | TUNBRIDGE WELLS TOWN 132/6.6kV | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1316 | 0.26549 | SPN-S000000009251 | 385505148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
348 | 52.7 | 22, MOUNT EPHRAIM | TUNBRIDGE WELLS | TN4 8AS | Tunbridge Wells |  | Offices And Premises | office | 1 | 3547.34 | 38183 | NIA | 975000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.66 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 5.64 | 248 | 13 | 375873 | SPN-S000000442322 | 500 | 50 | 0-20% | TUNBRIDGE WELLS TOWN 132/6.6kV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024138838 | Offices and Workshop Businesses | 3684 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2026-08-10 |  | 1 | FALSE | 51.1368 | 0.26103 | SPN-S000000009251 | 10687665000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
349 | 52.7 | HEATHERVALE HOUSE 2-4, VALE AVENUE | TUNBRIDGE WELLS | TN1 1DJ | Tunbridge Wells |  | Offices And Premises | office | 1 | 2632.79 | 28339 | NIA | 730000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 1.21 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 4.18 | 184 | 13 | 385717 | SPN-S000000443039 | 800 | 560 | 60-80% | TUNBRIDGE WELLS TOWN 132/6.6kV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008660551 | B1 Offices and Workshop businesses | 2918 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2021-04-12 |  | 1 | FALSE | 51.13 | 0.26089 | SPN-S000000009251 | 12461790000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
350 | 52.7 | AXA PPP HEALTHCARE JUBILEE HOUSE, VALE ROAD | TUNBRIDGE WELLS | TN1 1BJ | Tunbridge Wells |  | Offices And Premises | office | 1 | 2358.9 | 25391 | NIA | 540000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 1.27 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 3.75 | 165 | 13 | 388665 | SPN-S000000441917 | 1000 | 300 | 20-40% | TUNBRIDGE WELLS TOWN 11KV | 25 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008660600 | B1 Offices and Workshop businesses | 3154 | D | Natural Gas | 4 |  | Air Conditioning | 2014-02-07 |  | 0.67 | FALSE | 51.129 | 0.26192 | SPN-S000000009251 | 10222935000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
351 | 52.7 | 17, ST JOHNS ROAD | TUNBRIDGE WELLS | TN4 9TJ | Tunbridge Wells | BRITISH TELECOMMUNICATIONS PLC | Offices And Premises | office | 1 | 2285.71 | 24603 | NIA | 362500 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.61 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 3.63 | 160 | 13 | 389453 | SPN-S000000442322 | 500 | 50 | 0-20% | TUNBRIDGE WELLS TOWN 132/6.6kV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1378 | 0.26125 | SPN-S000000009251 | 409301148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
352 | 52.7 | TOWN SQUARE TOWN HALL, MOUNT PLEASANT ROAD | TUNBRIDGE WELLS | TN1 1RS | Tunbridge Wells |  | Offices And Premises | office | 1 | 2138.88 | 23023 | NIA | 285000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 3.4 | 150 | 13 | 391033 | SPN-S000000441369 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS TOWN 132/6.6kV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008660629 | B1 Offices and Workshop businesses | 5321 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-06-16 |  | 0.8 | FALSE | 51.1326 | 0.26395 | SPN-S000000009251 | 15098138000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
353 | 52.4 | W E ROBERTS LTD, GROVE ROAD | GRAVESEND | DA11 9AX | Gravesham |  | Workshop And Premises | industrial | 1 | 6904.53 | 74320 | GIA | 250000 | GRAVESEND WEST 33/11KV | inside-area | 0.23 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 89 | 10.97 | 311 | 19 | 403321 | SPN-S000000311077 | 800 | 240 | 20-40% | EBBSFLEET 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4508 | 0.32417 | SPN-S000000008511 | 5544845000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
354 | 52.4 | COURT LODGE FARM, DALE ROAD | GRAVESEND | DA13 9NX | Dartford |  | Factory And Premises | industrial | 1 | 5469.77 | 58876 | GIA | 233000 | LONGFIELD 33/11KV | inside-area | 2.66 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 23 | 10 | Thermal | 0 | 0 | 0 | 0 | 13.3 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23 | 17.1 | Summer | 56.1404 | 9.6 | Green (Over 5% headroom) | 66310 | 100 | 8.69 | 328 | 1 | 27788 | SPN-R000000865601-000-053Z | 200 | 180 | 80-100% | GRAVESEND SOUTH 33/11KV | 348 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4206 | 0.3194 | SPN-S000000008656 | 14754713000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
355 | 52.4 | K1-K5, NORTHFLEET INDUSTRIAL ESTATE, LOWER ROAD | GRAVESEND | DA11 9BL | Gravesham |  | Warehouse And Premises | industrial | 1 | 5442.2 | 58579 | GIA | 275000 | GRAVESEND WEST 33/11KV | inside-area | 0.13 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 8.65 | 136 | 19 | 419062 | SPN-S000000312297 | 500 | 150 | 20-40% | GRAVESEND WEST 33/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4515 | 0.32171 | SPN-S000000008511 | 1665420000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
356 | 52.4 | BLUE HAWK HOUSE A1-A2, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Warehouse And Premises | industrial | 1 | 3232.11 | 34790 | GIA | 290000 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 5.14 | 81 | 19 | 442851 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537754 | B8 Storage or Distribution | 3100 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-12-04 |  | 0.6 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 11294806000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
357 | 52.4 | UNITS 1-4, NORTHFLEET INDUSTRIAL ESTATE, LOWER ROAD | GRAVESEND | DA11 9SN | Gravesham |  | Warehouse And Premises | industrial | 1 | 2466 | 26544 | GIA | 236000 | GRAVESEND WEST 33/11KV | inside-area | 0.25 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 3.92 | 62 | 19 | 451097 | SPN-S000000313723 | 300 | 30 | 0-20% | GRAVESEND WEST 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062310930 | Storage or Distribution | 2863 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-03-20 |  | 1 | FALSE | 51.4517 | 0.31774 | SPN-S000000008511 | 14059944000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
358 | 52.4 | UNITS J4 & J5 TOWER WORKS, LOWER ROAD | GRAVESEND | DA11 9BB | Gravesham |  | Workshop And Premises | industrial | 1 | 2441.2 | 26277 | GIA | 221000 | GRAVESEND WEST 33/11KV | inside-area | 1.09 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 3.88 | 110 | 19 | 451364 | SPN-R000000851106-000-023Z | 500 | 350 | 60-80% | GRAVESEND WEST 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4597 | 0.31515 | SPN-S000000008511 | 392735147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
359 | 52.4 | R4, NORTHFLEET INDUSTRIAL ESTATE, LOWER ROAD | GRAVESEND | DA11 9SW | Dartford | WATNEY TRUMAN | Warehouse And Premises | industrial | 1 | 1961.36 | 21112 | GIA | 135000 | GRAVESEND WEST 33/11KV | inside-area | 0.4 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 3.12 | 49 | 19 | 456529 | SPN-S000000314678 | 1000 | 700 | 60-80% | GRAVESEND WEST 33/11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4509 | 0.31511 | SPN-S000000008511 | 167208147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
360 | 52.3 | MORRISONS SUPERMARKET PLC, THOMSETT WAY | QUEENBOROUGH | ME11 5AR | Swale |  | Superstore And Premises | bigbox | 1 | 5163.63 | 55581 | GIA | 1250000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.81 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 8.21 | 465 | 15 | 1084471 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4107 | 0.7579 | SPN-S000000008368 | 14788979000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
361 | 52.3 | UNIT 3, NEATS COURT | QUEENBOROUGH | ME11 5AR | Swale |  | Retail Warehouse And Premises | bigbox | 1 | 2619.83 | 28200 | GIA | 272500 | QUEENBOROUGH 33/6.6KV | inside-area | 0.81 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 4.16 | 236 | 15 | 1111852 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023203594 | Retail/Financial and Professional Services | 1994 | A | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2026-07-29 |  | 1 | FALSE | 51.4107 | 0.7579 | SPN-S000000008368 | 9467085000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
362 | 52.1 | SAINSBURY 19, MILITARY ROAD | HYTHE | CT21 5AS | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 5358.37 | 57677 | GIA | 1350000 | HYTHE MAIN 33/11KV | inside-area | 1.15 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 8.51 | 482 | 7 | 149678 | SPN-S000000363914 | 315 | 220 | 60-80% | HYTHE MAIN 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50124825 | Retail/Financial and Professional Services | 5175 | B | Biomass | 4 |  | Heating and Mechanical Ventilation | 2023-10-04 |  | 1 | FALSE | 51.072 | 1.0765 | SPN-S000000008421 | 11345450000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
363 | 52.1 | WAITROSE, PROSPECT ROAD | HYTHE | CT21 5NH | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 3203.1 | 34478 | GIA | 680000 | HYTHE MAIN 33/11KV | inside-area | 0.29 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 5.09 | 288 | 7 | 172877 | SPN-S000000361952 | 800 | 400 | 40-60% | HYTHE MAIN 33/11KV | 127 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50017898 | Retail/Financial and Professional Services | 3154 | C | Natural Gas | 5 | 2 | Air Conditioning | 2023-10-02 |  | 1 | FALSE | 51.072 | 1.089 | SPN-S000000008421 | 9235512000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
364 | 51.8 | UNIT 1B, LONDON MEDWAY COMMERCIAL PARK, JAMES SWALLOW WAY | ROCHESTER | ME3 9GX | Medway |  | Warehouse And Premises | industrial | 1 | 35345.05 | 380451 | GIA | 1740000 | KINGSNORTH GRID 11KV | inside-area | 1.55 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 41 | 56.17 | 884 | 12 | 953217 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44062049 | B8 Storage or Distribution | 34266 | A | Grid Supplied Electricity | 5 | 3 | Air Conditioning | 2018-10-23 |  | 0.83 | FALSE | 51.4335 | 0.60735 | SPN-S000000009525 | 13624439000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
365 | 51.8 | UNIT 1A, LONDON MEDWAY COMMERCIAL PARK, JAMES SWALLOW WAY | ROCHESTER | ME3 9GX | Medway |  | Warehouse And Premises | industrial | 1 | 34015.7 | 366142 | GIA | 3170000 | KINGSNORTH GRID 11KV | inside-area | 1.55 | KINGSNORTH GRID 11KV | Kingsnorth | Mid Kent Zone | 22 | primary | 22 | Green | 38.1 | 9.3 | Thermal | 0 | 14.2 | 5.9 | 14.2 | 22.4 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | Green (Over 5% headroom) | 156863 | 43 | 54.05 | 850 | 12 | 967526 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44062049 | B8 Storage or Distribution | 34266 | A | Grid Supplied Electricity | 5 | 3 | Air Conditioning | 2018-10-23 |  | 0.83 | FALSE | 51.4335 | 0.60735 | SPN-S000000009525 | 11710806000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
366 | 51.7 | UNIT 60, CLAIRE CAUSEWAY, CROSSWAYS BOULEVARD | DARTFORD | DA2 6QA | Dartford |  | Warehouse And Premises | industrial | 2 | 11979.95 | 128951 | GIA | 1260000 | STONE MARSHES 33/11KV | inside-area | 1.23 | Northfleet East | Northfleet | West Kent Zone | 8.8 | primary | 8.8 | Green | 27.8 | 13.8 | Thermal | 1.5 | 1 | 0 | 2.5 | 7.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 26.7 | 20.5 | Summer | 40 | 8.2 | Green (Over 5% headroom) | 62745 | 49 | 19.04 | 299 | 2 | 77565 | SPN-S000000314562 | 500 | 350 | 60-80% | CROSSWAYS | 122 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 |  | General Industrial and Special Industrial Groups | 6907 | D | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2022-08-12 |  | 0.75 | FALSE | 51.4527 | 0.26534 | SPN-S000000008544 | 1853510000;1853511000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
367 | 51.7 | TILMANSTONE SALADS, MILLYARD WAY | DOVER | CT15 4NL | Dover |  | Factory And Premises | industrial | 1 | 11956.9 | 128703 | GIA | 835000 | BETTESHANGER LOCAL 33/11KV | inside-area | 5.57 | Betteshanger Grid | Sellindge | East Kent Zone | 8.8 | primary | 8.8 | Green | 24 | 14.4 | Thermal | 0 | 0 | 0 | 0 | 8.2 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.5 | 17.1 | Winter | 40 | 9.4 | Green (Over 5% headroom) | 62745 | 49 | 19 | 717 | 5 | 148032 | SPN-R000000865802-000-055Z | 200 | 180 | 80-100% | LIGHTWEIGHT AGGREGATES | 384 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034875334 | General Industrial and Special Industrial Groups | 10828 | C | Natural Gas | 4 | 3 | Heating and Mechanical Ventilation | 2025-03-23 |  | 1 | FALSE | 51.206 | 1.2721 | SPN-S000000008304 | 14705822000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
368 | 51.7 | UNIT 1, MILLYARD WAY, PIKE ROAD | DOVER | CT15 4ND | Dover |  | Warehouse And Premises | industrial | 1 | 7733.51 | 83243 | GIA | 422500 | BETTESHANGER LOCAL 33/11KV | inside-area | 5.3 | Betteshanger Grid | Sellindge | East Kent Zone | 8.8 | primary | 8.8 | Green | 24 | 14.4 | Thermal | 0 | 0 | 0 | 0 | 8.2 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.5 | 17.1 | Winter | 40 | 9.4 | Green (Over 5% headroom) | 62745 | 75 | 12.29 | 193 | 5 | 193492 | SPN-R000000830407-000-134Z | 200 | 100 | 40-60% | BETTESHANGER LOCAL 33/11KV | 119 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2079 | 1.275 | SPN-S000000008304 | 15035361000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
369 | 51.7 | 1, QUADRANT COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA9 9AY | Dartford |  | Warehouse And Premises | industrial | 3 | 6164.05 | 66349 | GIA | 857000 | STONE MARSHES 33/11KV | inside-area | 1.54 | Northfleet East | Northfleet | West Kent Zone | 8.8 | primary | 8.8 | Green | 27.8 | 13.8 | Thermal | 1.5 | 1 | 0 | 2.5 | 7.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 26.7 | 20.5 | Summer | 40 | 8.2 | Green (Over 5% headroom) | 62745 | 95 | 9.8 | 154 | 2 | 140167 | SPN-S000000324279 | 1000 | 700 | 60-80% | STONE MARSHES 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10009431607 | B2 to B7 General Industrial and Special Industrial Groups | 2441 | C | Natural Gas | 3 | 2 | Air Conditioning | 2019-06-27 |  | 1 | FALSE | 51.4532 | 0.27119 | SPN-S000000008544 | 5897524000;11094765000;5897547000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
370 | 51.7 | UNIT B1 COLLIERY BUSINESS PARK, PIKE ROAD | DOVER | CT15 4FE | Dover |  | Warehouse And Premises | industrial | 1 | 2429.5 | 26151 | GIA | 134000 | BETTESHANGER LOCAL 33/11KV | inside-area | 5.43 | Betteshanger Grid | Sellindge | East Kent Zone | 8.8 | primary | 8.8 | Green | 24 | 14.4 | Thermal | 0 | 0 | 0 | 0 | 8.2 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.5 | 17.1 | Winter | 40 | 9.4 | Green (Over 5% headroom) | 62745 | 100 | 3.86 | 61 | 5 | 250584 | SPN-R000000830407-000-134Z | 200 | 100 | 40-60% | BETTESHANGER LOCAL 33/11KV | 276 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2067 | 1.2738 | SPN-S000000008304 | 8984394000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
371 | 51.5 | SURESTORE SELF STORAGE, NORTH FARM ROAD | TUNBRIDGE WELLS | TN2 3DP | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 9058.53 | 97505 | GIA | 462500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.18 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 63 | 14.39 | 226 | 50 | 1725411 | SPN-S000000441897 | 800 | 560 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1509 | 0.27818 | SPN-S000000008504 | 15032845000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
372 | 51.5 | NORTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SR | Medway | HYTEN; STREET FUEL LTD | Workshop And Premises; Workshops And Premises | industrial | 2 | 8653.97 | 93150 | GIA | 610000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 66 | 13.75 | 389 | 25 | 1022592 | SPN-S000000324509 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 366 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4012 | 0.54713 | SPN-S000000008645 | 12265502000;12394444000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
373 | 51.5 | BIG YELLOW SELF STORAGE CO LTD, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3UE | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 8092.92 | 87111 | GIA | 362500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.78 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 70 | 12.86 | 202 | 50 | 1735805 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 312 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000068521 | B8 Storage or Distribution | 151 | B | Grid Supplied Electricity | 5 | 1 | Air Conditioning | 2018-03-26 |  | 1 | FALSE | 51.1566 | 0.29451 | SPN-S000000008504 | 4837273000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
374 | 51.5 | WAREHOUSE, NORTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SR | Medway | PDMR | Warehouse And Premises | industrial | 1 | 7133.5 | 76784 | GIA | 500000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 80 | 11.34 | 178 | 25 | 1038958 | SPN-S000000324509 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 366 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4012 | 0.54713 | SPN-S000000008645 | 12394437000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
375 | 51.5 | EASISTORE, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EY | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 6229.61 | 67055 | GIA | 310000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 91 | 9.9 | 156 | 50 | 1755861 | SPN-S000000443773 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554168 | Storage or Distribution | 8636 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-07-29 |  | 1 | FALSE | 51.1549 | 0.28851 | SPN-S000000008504 | 2777119000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
376 | 51.5 | STORMONT TRUCKS, LONDON ROAD | TONBRIDGE | TN11 8NB | Tonbridge & Malling |  | Vehicle Repair Workshop And Premises | industrial | 1 | 4108.48 | 44223 | GIA | 410000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 3.87 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 6.53 | 185 | 50 | 1778693 | SPN-S000000442366 | 315 | 94 | 20-40% | TONBRIDGE TOWN 33/6.6KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2177 | 0.22694 | SPN-S000000008504 | 514565000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
377 | 51.5 | UNITS 6 & 9 AT 12-13, DRAYTON ROAD | TONBRIDGE | TN9 2BE | Tonbridge & Malling |  | Factory And Premises; Warehouse And Premises | industrial | 3 | 3800.13 | 40904 | GIA | 193000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 1.21 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 6.04 | 228 | 50 | 1782012 | SPN-S000000441570 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100061170088 | Storage or Distribution | 413 | C | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2023-06-14 |  | 1 | FALSE | 51.1868 | 0.27646 | SPN-S000000008504 | 9060157000;405627148;404724148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
378 | 51.5 | 31, SECOND AVENUE | CHATHAM | ME4 5AU | Medway |  | Warehouse And Premises | industrial | 2 | 3770.75 | 40588 | GIA | 179500 | CHATHAM HILL 33/11KV | inside-area | 0.92 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 5.99 | 94 | 25 | 1075154 | SPN-S000000311837 | 500 | 150 | 20-40% | CHATHAM HILL 33/11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44061332 | Retail/Financial and Professional Services | 2664 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-09-05 |  | 1 | FALSE | 51.3694 | 0.54294 | SPN-S000000008645 | 408426147;4034407000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
379 | 51.5 | CHATHAM FREIGHT STATION LTD, NORTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SW | Medway |  | Warehouse And Premises | industrial | 1 | 3761.62 | 40490 | GIA | 80000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 5.98 | 94 | 25 | 1075252 | SPN-S000000311882 | 200 | 60 | 20-40% | CHATHAM HILL 33/11KV | 376 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4005 | 0.55166 | SPN-S000000008645 | 7291715000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
380 | 51.5 | GADS HILL | GILLINGHAM | ME7 2RA | Medway | L ROBINSON & CO (GILLINGHAM) LTD | Factory And Premises | industrial | 1 | 3204.1 | 34489 | GIA | 154000 | CHATHAM HILL 33/11KV | inside-area | 2.48 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 5.09 | 192 | 25 | 1081253 | SPN-S000000311957 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 119 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3919 | 0.56793 | SPN-S000000008645 | 63928147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
381 | 51.5 | DOWDING WAY | TUNBRIDGE WELLS | TN2 3UY | Tunbridge Wells | CASTELLI DIARIES LTD | Warehouse And Premises | industrial | 1 | 3116.7 | 33548 | GIA | 302500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.81 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.95 | 78 | 50 | 1789368 | SPN-S000000451043 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000069863 | A1/A2 Retail and Financial/Professional services | 1365 | C | Natural Gas | 3 |  | Air Conditioning | 2016-07-19 |  | 1 | FALSE | 51.1546 | 0.28361 | SPN-S000000008504 | 2338082000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
382 | 51.5 | BERTH 6 & 7 WAREHOUSE PT REAR, NORTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SR | Medway |  | Warehouse And Premises | industrial | 1 | 3012.93 | 32431 | GIA | 237000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 4.79 | 75 | 25 | 1083311 | SPN-S000000324509 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 366 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4012 | 0.54713 | SPN-S000000008645 | 14652995000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
383 | 51.5 | TUNBRIDGE WELLS BC COUNCIL DEPOT, NORTH FARM LANE | TUNBRIDGE WELLS | TN2 3EE | Tunbridge Wells |  | Warehouse, Office And Premises | industrial | 1 | 2993.15 | 32218 | GIA | 272500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.41 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.76 | 210 | 50 | 1790698 | SPN-S000000451313 | 1000 | 900 | 80-100% | TUNBRIDGE WELLS TOWN 11KV | 150 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065729 | B2 to B7 General Industrial and Special Industrial Groups | 2528 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-03-19 |  | 0.86 | FALSE | 51.1596 | 0.29178 | SPN-S000000008504 | 6371621000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
384 | 51.5 | 2, CHAPMAN WAY | TUNBRIDGE WELLS | TN2 3EF | Tunbridge Wells |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 2845.27 | 30626 | GIA | 265000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.97 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.52 | 128 | 50 | 1792290 | SPN-S000000443398 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 59 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008663304 | Offices and Workshop Businesses | 1481 | B | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2023-02-15 |  | 1 | FALSE | 51.1527 | 0.27694 | SPN-S000000008504 | 153946148;153947148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
385 | 51.5 | 1, CHAPMAN WAY | TUNBRIDGE WELLS | TN2 3EG | Tunbridge Wells | SPA ALUMINIUM LTD | Workshop And Premises | industrial | 1 | 2674.1 | 28784 | GIA | 238000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.78 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.25 | 120 | 50 | 1794132 | SPN-S000000441041 | 500 | 250 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008663269 | B2 to B7 General Industrial and Special Industrial Groups | 2708 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-03-21 |  | 1 | FALSE | 51.1545 | 0.27914 | SPN-S000000008504 | 153945148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
386 | 51.5 | PARAGON MATERIALS LTD, SOUTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SR | Medway |  | Warehouse And Premises | industrial | 1 | 2505.11 | 26965 | GIA | 175000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.98 | 63 | 25 | 1088777 | SPN-S000000324509 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 366 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4012 | 0.54713 | SPN-S000000008645 | 3504173000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
387 | 51.5 | 36, SECOND AVENUE | CHATHAM | ME4 5AY | Medway |  | Factory And Premises | industrial | 1 | 2262.57 | 24354 | GIA | 135000 | CHATHAM HILL 33/11KV | inside-area | 0.96 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.6 | 136 | 25 | 1091388 | SPN-S000000311837 | 500 | 150 | 20-40% | CHATHAM HILL 33/11KV | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3691 | 0.54328 | SPN-S000000008645 | 7634911000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
388 | 51.5 | 3, STAG ROAD | TUNBRIDGE WELLS | TN2 3BQ | Tunbridge Wells |  | Vehicle Repair Workshop And Premises | industrial | 1 | 2240.9 | 24121 | GIA | 229000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.83 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.56 | 101 | 50 | 1798795 | SPN-S000000451020 | 500 | 350 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 131 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000072237 | B8 Storage or Distribution | 2212 | D | Oil | 3 |  | Heating and Natural Ventilation | 2014-01-24 |  | 1 | FALSE | 51.1547 | 0.28606 | SPN-S000000008504 | 9627022000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
389 | 51.5 | 115, HOPEWELL DRIVE | CHATHAM | ME5 7NP | Medway |  | Warehouse And Premises | industrial | 2 | 2152.15 | 23166 | GIA | 172500 | CHATHAM HILL 33/11KV | inside-area | 1.42 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.42 | 54 | 25 | 1092576 | SPN-S000000311853 | 500 | 350 | 60-80% | CHATHAM HILL 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062392782 | B2 to B7 General Industrial and Special Industrial Groups | 989 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-26 |  | 1 | FALSE | 51.3654 | 0.54671 | SPN-S000000008645 | 7799613000;406286147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
390 | 51.5 | UNIT 1 OWENS WAY, GADS HILL | GILLINGHAM | ME7 2RR | Medway |  | Factory And Premises | industrial | 2 | 2150 | 23142 | GIA | 136000 | CHATHAM HILL 33/11KV | inside-area | 2.68 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.42 | 129 | 25 | 1092600 | SPN-S000000311961 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3909 | 0.57283 | SPN-S000000008645 | 13557151000;13557150000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
391 | 51.5 | LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EY | Tunbridge Wells | BELLINGHAM & STANLEY LTD | Factory And Premises | industrial | 1 | 2070.89 | 22291 | GIA | 136000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.29 | 124 | 50 | 1800625 | SPN-S000000443773 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000064458 | B8 Storage or Distribution | 2072 | C | Natural Gas | 3 | 2 | Heating and Mechanical Ventilation | 2013-04-29 |  | 1 | FALSE | 51.1549 | 0.28851 | SPN-S000000008504 | 161805148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
392 | 51.5 | SHED 7, NORTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SR | Medway |  | Warehouse And Premises | industrial | 1 | 1983.35 | 21349 | GIA | 207000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.15 | 50 | 25 | 1094393 | SPN-S000000324509 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 366 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4012 | 0.54713 | SPN-S000000008645 | 12274286000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
393 | 51.5 | S E TYRES, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EY | Tunbridge Wells |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1921.98 | 20688 | GIA | 152000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.05 | 86 | 50 | 1802228 | SPN-S000000443773 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000066066 | A1/A2 Retail and Financial/Professional services | 1917 | E | Natural Gas | 3 | 2 | Heating and Mechanical Ventilation | 2014-05-02 |  | 0.5 | FALSE | 51.1549 | 0.28851 | SPN-S000000008504 | 4464220000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
394 | 51.5 | WELLWOOD, NORTH FARM ROAD | TUNBRIDGE WELLS | TN2 3DR | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1883.6 | 20275 | GIA | 167000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.01 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.99 | 47 | 50 | 1802641 | SPN-S000000442197 | 800 | 560 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000068078 | B8 Storage or Distribution | 822 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-06-25 |  | 0.67 | FALSE | 51.1525 | 0.2797 | SPN-S000000008504 | 7469153000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
395 | 51.4 | HOMELEIGH 79, ALBERT ROAD | DEAL | CT14 9RA | Dover | HUTCHINGS TIMBER | Builders Merchants And Premises | bigbox | 1 | 4475.38 | 48173 | GIA | 162000 | DEAL 33/11KV | inside-area | 0.49 | Betteshanger Grid | Sellindge | East Kent Zone | 12.3 | primary | 12.3 | Green | 24 | 11.7 | Thermal | 0 | 0 | 0 | 0 | 9.7 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.3 | 18.6 | Winter | 51.1211 | 11.4 | Green (Over 5% headroom) | 87701 | 100 | 7.11 | 403 | 4 | 78706 | SPN-S000000362943 | 500 | 250 | 40-60% | DEAL 33/11KV | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2263 | 1.3968 | SPN-S000000008389 | 131062145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
396 | 51.4 | J SAINSBURY, WEST STREET | DEAL | CT14 6AH | Dover |  | Superstore And Premises | bigbox | 1 | 3879.9 | 41763 | GIA | 885000 | DEAL 33/11KV | inside-area | 0.75 | Betteshanger Grid | Sellindge | East Kent Zone | 12.3 | primary | 12.3 | Green | 24 | 11.7 | Thermal | 0 | 0 | 0 | 0 | 9.7 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.3 | 18.6 | Winter | 51.1211 | 11.4 | Green (Over 5% headroom) | 87701 | 100 | 6.17 | 349 | 4 | 85116 | SPN-S000000362931 | 1000 | 500 | 40-60% | DEAL 33/11KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2244 | 1.4001 | SPN-S000000008389 | 8786373000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
397 | 51.3 | TRANSIT (MEDWAY) LIMITED, CROWN WHARF | ROCHESTER | ME2 4EP | Medway |  | Factory And Premises | industrial | 1 | 25729.43 | 276949 | GIA | 670000 | STROOD 132/11KV | inside-area | 1.15 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 41 | 40.89 | 1544 | 62 | 3064509 | SPN-S000000316940 | 500 | 250 | 40-60% | STROOD 132/11KV | 96 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3935 | 0.51245 | SPN-S000000009948 | 12080603000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
398 | 51.3 | MEDWAY MAIL CENTRE 1, KNIGHT ROAD | ROCHESTER | ME2 2EE | Medway |  | Warehouse And Premises | industrial | 1 | 16605.76 | 178743 | GIA | 1390000 | STROOD 132/11KV | inside-area | 1.82 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 64 | 26.39 | 415 | 62 | 3162715 | SPN-S000000311110 | 500 | 150 | 20-40% | STROOD 132/11KV | 266 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44014007 | Storage or Distribution | 15999 | B | Natural Gas | 4 |  | Mixed-mode with Mechanical Ventilation | 2023-12-01 |  | 1 | FALSE | 51.3865 | 0.48527 | SPN-S000000009948 | 8159225000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
399 | 51.3 | NURALITE INDUSTRIAL ESTATE, CANAL ROAD | ROCHESTER | ME3 7JA | Gravesham |  | Factory And Premises | industrial | 1 | 16164.8 | 173996 | GIA | 355000 | STROOD 132/11KV | inside-area | 5.6 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 66 | 25.69 | 970 | 62 | 3167462 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10012033338 | Offices and Workshop Businesses | 194 | C | Other | 3 |  | Unconditioned | 2024-03-27 |  | 1 | FALSE | 51.4379 | 0.44644 | SPN-S000000009948 | 3144241000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
400 | 51.3 | R SWAIN & SONS LTD, PRIORY ROAD | ROCHESTER | ME2 2BD | Medway |  | Factory And Premises | industrial | 1 | 14165.9 | 152480 | GIA | 432500 | STROOD 132/11KV | inside-area | 1.12 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 75 | 22.51 | 850 | 62 | 3188978 | SPN-S000000314354 | 315 | 158 | 40-60% | STROOD 132/11KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44004347 | B1 Offices and Workshop businesses | 187 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-04-29 |  | 1 | FALSE | 51.3919 | 0.49036 | SPN-S000000009948 | 12011856000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
401 | 51.3 | INDEPENDENT HOUSE 13, ARNOLDE CLOSE, SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4QW | Medway |  | Warehouse And Premises | industrial | 1 | 1824.57 | 19639 | GIA | 175000 | STROOD 132/11KV | inside-area | 1.39 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.9 | 46 | 62 | 3321819 | SPN-S000000316763 | 1000 | 300 | 20-40% | STROOD 132/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3933 | 0.51655 | SPN-S000000009948 | 7025429000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
402 | 51.3 | 1, PHOENIX INDUSTRIAL ESTATE, COMMISSIONERS ROAD | ROCHESTER | ME2 4EQ | Medway |  | Factory And Premises | industrial | 1 | 1772.7 | 19081 | GIA | 139000 | STROOD 132/11KV | inside-area | 0.67 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.82 | 106 | 62 | 3322377 | SPN-S000000311625 | 800 | 400 | 40-60% | STROOD 132/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | Storage or Distribution | 1794 | B | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2025-10-23 |  | 1 | FALSE | 51.3974 | 0.50844 | SPN-S000000009948 | 171214147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
403 | 51.3 | UNIT A & B, GOLD STAR CENTRE, NEPTUNE CLOSE | ROCHESTER | ME2 4LT | Medway |  | Warehouse And Premises | industrial | 1 | 1724.58 | 18563 | GIA | 188000 | STROOD 132/11KV | inside-area | 1.43 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.74 | 43 | 62 | 3322895 | SPN-S000000316834 | 800 | 400 | 40-60% | STROOD 132/11KV | 27 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44111190 | B2 to B7 General Industrial and Special Industrial Groups | 1779 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-07-27 |  | 1 | FALSE | 51.3938 | 0.51769 | SPN-S000000009948 | 7206795000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
404 | 51.3 | H1, KNIGHTS PARK, KNIGHT ROAD | ROCHESTER | ME2 2LS | Medway |  | Warehouse And Premises | industrial | 1 | 1710.91 | 18416 | GIA | 144000 | STROOD 132/11KV | inside-area | 1.36 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.72 | 43 | 62 | 3323042 | SPN-S000000316869 | 1000 | 700 | 60-80% | STROOD 132/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3904 | 0.48765 | SPN-S000000009948 | 9368203000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
405 | 51.3 | UNITS B1 & B2, KNIGHTS PARK, KNIGHT ROAD | ROCHESTER | ME2 2LS | Medway |  | Warehouse And Premises | industrial | 1 | 1684.29 | 18130 | GIA | 150000 | STROOD 132/11KV | inside-area | 1.36 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.68 | 42 | 62 | 3323328 | SPN-S000000316869 | 1000 | 700 | 60-80% | STROOD 132/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000896362 | B8 Storage or Distribution | 1005 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-11-17 |  | 1 | FALSE | 51.3904 | 0.48765 | SPN-S000000009948 | 14057072000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
406 | 51.3 | A3, PHOENIX INDUSTRIAL ESTATE, COMMISSIONERS ROAD | ROCHESTER | ME2 4EF | Medway |  | Warehouse And Premises | industrial | 1 | 1666.5 | 17938 | GIA | 109000 | STROOD 132/11KV | inside-area | 0.7 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.65 | 42 | 62 | 3323520 | SPN-S000000311625 | 800 | 400 | 40-60% | STROOD 132/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3971 | 0.50866 | SPN-S000000009948 | 402800147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
407 | 51.3 | PRIORY ROAD | ROCHESTER | ME2 2BD | Medway | DANA | Workshop And Premises | industrial | 1 | 1583.09 | 17040 | GIA | 116000 | STROOD 132/11KV | inside-area | 1.12 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.52 | 71 | 62 | 3324418 | SPN-S000000314354 | 315 | 158 | 40-60% | STROOD 132/11KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44004347 | B1 Offices and Workshop businesses | 187 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-04-29 |  | 1 | FALSE | 51.3919 | 0.49036 | SPN-S000000009948 | 4837051000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
408 | 51.3 | PHARAOH HOUSE, ARNOLDE CLOSE | ROCHESTER | ME2 4DN | Medway |  | Warehouse And Premises | industrial | 1 | 1564.58 | 16841 | GIA | 167000 | STROOD 132/11KV | inside-area | 1.22 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.49 | 39 | 62 | 3324617 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3979 | 0.51697 | SPN-S000000009948 | 1683383000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
409 | 51.3 | UNIT 2, ENTERPRISE CLOSE | ROCHESTER | ME2 4JW | Medway |  | Workshop And Premises | industrial | 1 | 1355.71 | 14593 | GIA | 143000 | STROOD 132/11KV | inside-area | 0.89 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.15 | 61 | 62 | 3326865 | SPN-S000000316841 | 1000 | 700 | 60-80% | STROOD 132/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44029279 | B1 Offices and Workshop businesses | 2071 | D | Oil | 3 | 1 | Heating and Natural Ventilation | 2018-04-04 |  | 1 | FALSE | 51.3994 | 0.51246 | SPN-S000000009948 | 9226238000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
410 | 51.3 | 2, ARDEN BUSINESS PARK, CHAUCER CLOSE | ROCHESTER | ME2 4LY | Medway |  | Warehouse Used As Roller Skating Rink And Premises | industrial | 1 | 1334.21 | 14361 | GIA | 131000 | STROOD 132/11KV | inside-area | 1.01 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.12 | 33 | 62 | 3327097 | SPN-S000000314025 | 500 | 250 | 40-60% | STROOD 132/11KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3981 | 0.51392 | SPN-S000000009948 | 9692759000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
411 | 51.3 | G3, KNIGHTS PARK, KNIGHT ROAD | ROCHESTER | ME2 2LS | Medway |  | Warehouse And Premises | industrial | 1 | 1238.67 | 13333 | GIA | 86000 | STROOD 132/11KV | inside-area | 1.36 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.97 | 31 | 62 | 3328125 | SPN-S000000316869 | 1000 | 700 | 60-80% | STROOD 132/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388496 | B8 Storage or Distribution | 1261 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-05-28 |  | 1 | FALSE | 51.3904 | 0.48765 | SPN-S000000009948 | 3275571000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
412 | 51.3 | HANSON TOWER LTD, HANSON HOUSE, KNIGHT ROAD | ROCHESTER | ME2 2JH | Medway |  | Factory And Premises | industrial | 1 | 1233.1 | 13273 | GIA | 84000 | STROOD 132/11KV | inside-area | 0.98 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.96 | 74 | 62 | 3328185 | SPN-S000000314354 | 315 | 158 | 40-60% | STROOD 132/11KV | 10 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388289 | General Industrial and Special Industrial Groups | 1551 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-06-04 |  | 0.67 | FALSE | 51.393 | 0.49138 | SPN-S000000009948 | 9039468000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
413 | 51.3 | 5-7, VICTORY PARK, TRIDENT CLOSE | ROCHESTER | ME2 4EW | Medway |  | Workshop And Premises | industrial | 1 | 1221.24 | 13145 | GIA | 124000 | STROOD 132/11KV | inside-area | 0.9 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.94 | 55 | 62 | 3328313 | SPN-S000000311654 | 300 | 90 | 20-40% | STROOD 132/11KV | 104 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3976 | 0.51211 | SPN-S000000009948 | 8933845000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
414 | 51.3 | 1, ARDEN BUSINESS PARK, CHAUCER CLOSE | ROCHESTER | ME2 4DN | Medway |  | Warehouse And Premises. | industrial | 1 | 1136.8 | 12236 | GIA | 122000 | STROOD 132/11KV | inside-area | 1.22 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.81 | 28 | 62 | 3329222 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3979 | 0.51697 | SPN-S000000009948 | 408543147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
415 | 51.3 | 9 & 10, LAKESIDE PARK, NEPTUNE CLOSE | ROCHESTER | ME2 4LT | Medway |  | Warehouse And Premises | industrial | 1 | 1122.44 | 12082 | GIA | 114000 | STROOD 132/11KV | inside-area | 1.43 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.78 | 28 | 62 | 3329376 | SPN-S000000316834 | 800 | 400 | 40-60% | STROOD 132/11KV | 27 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000898486 | B1 Offices and Workshop businesses | 639 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-04-30 |  | 1 | FALSE | 51.3938 | 0.51769 | SPN-S000000009948 | 15093620000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
416 | 51.3 | MEDWAY BUILDERS MERCHANTS, GEORGE SUMMERS CLOSE | ROCHESTER | ME2 4NS | Medway |  | Warehouse And Premises | industrial | 1 | 1108.85 | 11936 | GIA | 111000 | STROOD 132/11KV | inside-area | 1.34 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.76 | 28 | 62 | 3329522 | SPN-S000000316795 | 800 | 240 | 20-40% | STROOD 132/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44114117 | B2 to B7 General Industrial and Special Industrial Groups | 1152 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-12-08 |  | 0.67 | FALSE | 51.3988 | 0.51893 | SPN-S000000009948 | 8525797000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
417 | 51.3 | UNIT B8 SAXON PLACE, MEDWAY VALLEY PARK, NORMAN CLOSE | ROCHESTER | ME2 2NW | Medway |  | Workshop And Premises | industrial | 1 | 1064.2 | 11455 | GIA | 113000 | STROOD 132/11KV | inside-area | 2.05 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.69 | 48 | 62 | 3330003 | SPN-S000000316782 | 800 | 560 | 60-80% | STROOD 132/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3852 | 0.48239 | SPN-S000000009948 | 14329773000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
418 | 51.3 | NORMAN CLOSE | ROCHESTER | ME2 2JU | Medway | BRITISH OXYGEN CO | Storage Depot And Premises | industrial | 1 | 1052 | 11324 | GIA | 35500 | STROOD 132/11KV | inside-area | 1.98 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.67 | 26 | 62 | 3330134 | SPN-S000000316782 | 800 | 560 | 60-80% | STROOD 132/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3853 | 0.48385 | SPN-S000000009948 | 390005147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
419 | 51.3 | G2, KNIGHTS PARK, KNIGHT ROAD | ROCHESTER | ME2 2LS | Medway |  | Warehouse And Premises | industrial | 1 | 1043.91 | 11237 | GIA | 91000 | STROOD 132/11KV | inside-area | 1.36 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.66 | 26 | 62 | 3330221 | SPN-S000000316869 | 1000 | 700 | 60-80% | STROOD 132/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44013554 | Offices and Workshop Businesses | 1253 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-01-27 |  | 1 | FALSE | 51.3904 | 0.48765 | SPN-S000000009948 | 3275567000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
420 | 51.3 | EAGLE HOUSE, SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4DU | Medway |  | Workshop And Premises | industrial | 1 | 1031.4 | 11102 | GIA | 103000 | STROOD 132/11KV | inside-area | 1.46 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.64 | 46 | 62 | 3330356 | SPN-S000000316799 | 800 | 560 | 60-80% | STROOD 132/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062388773 | B2 to B7 General Industrial and Special Industrial Groups | 570 | D | Natural Gas | 3 | 1 | Air Conditioning | 2018-08-07 |  | 0.75 | FALSE | 51.391 | 0.51498 | SPN-S000000009948 | 404075147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
421 | 51.3 | TESCO STORES LTD, MANSTON ROAD | RAMSGATE | CT12 6NT | Thanet |  | Superstore And Premises | bigbox | 1 | 4799.73 | 51664 | GIA | 1060000 | RICHBOROUGH 33/11KV | inside-area | 6.07 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 7.63 | 432 | 29 | 1291354 | SPN-S000000343627 | 1000 | 700 | 60-80% | RAMSGATE 33/11KV | 212 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10091688921 | A1/A2 Retail and Financial/Professional services | 5369 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2020-08-17 |  | 1 | FALSE | 51.3404 | 1.3884 | SPN-S000000008342 | 14402114000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
422 | 51.3 | ARCHERS LOW NURSERY, ASH ROAD | SANDWICH | CT13 9JB | Dover |  | Garden Centre And Premises | bigbox | 1 | 4119.42 | 44341 | NIA | 19750 | RICHBOROUGH 33/11KV | inside-area | 1.97 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 6.55 | 371 | 29 | 1298677 | SPN-R000000834210-000-013Z | 100 | 70 | 60-80% | RICHBOROUGH 33/11KV | 99 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.2793 | 1.3276 | SPN-S000000008342 | 511708145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
423 | 51.3 | BAYPOINT CLUB, RAMSGATE ROAD | SANDWICH | CT13 9QL | Dover |  | Leisure Centre And Premises | bigbox | 1 | 2253.02 | 24251 | GIA | 109000 | RICHBOROUGH 33/11KV | inside-area | 2.12 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.58 | 180 | 29 | 1318767 | SPN-S000000343653 | 315 | 220 | 60-80% | RICHBOROUGH 33/11KV | 299 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034886786 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 2145 | C | Natural Gas | 3 | 1 | Heating and Mechanical Ventilation | 2015-06-17 |  | 1 | FALSE | 51.311 | 1.3527 | SPN-S000000008342 | 14974644000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
424 | 50.9 | EPS LOGISTICS TECHNOLOGY LTD 150, STAPLEHURST ROAD | SITTINGBOURNE | ME10 1XS | Swale |  | Factory And Premises | industrial | 2 | 12786.8 | 137636 | GIA | 670000 | SITTINGBOURNE WEST 33/11KV | inside-area | 0.52 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 42 | 20.32 | 767 | 25 | 1077741 | SPN-S000000391715 | 500 | 350 | 60-80% | SITTINGBOURNE WEST 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3453 | 0.71917 | SPN-S000000008444 | 11964075000;11964075000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
425 | 50.9 | CANTERBURY ROAD | FAVERSHAM | ME13 8LY | Swale | KENT COUNTY COUNCIL DEPOT | Storage Depot And Premises | industrial | 1 | 12375 | 133203 | OTH | 97500 | FAVERSHAM 33/11KV | inside-area | 1.42 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 44 | 19.66 | 309 | 21 | 960832 | SPN-S000000393100 | 300 | 150 | 40-60% | FAVERSHAM 33/11KV | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10034900652 | B2 to B7 General Industrial and Special Industrial Groups | 88 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-06-16 |  | 1 | FALSE | 51.3078 | 0.89271 | SPN-S000000008405 | 216280147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
426 | 50.9 | DISTRIBUTION CENTRE, WESTERN LINK ROAD | FAVERSHAM | ME13 7TZ | Swale |  | Warehouse And Premises | industrial | 1 | 9975.05 | 107370 | GIA | 497500 | FAVERSHAM 33/11KV | inside-area | 2.83 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 54 | 15.85 | 249 | 21 | 986665 | SPN-S000000391877 | 500 | 350 | 60-80% | FAVERSHAM 33/11KV | 309 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3257 | 0.87668 | SPN-S000000008405 | 4631697000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
427 | 50.9 | UNITS 19-20, CRAFT MARSH TRADING ESTATE, GAS ROAD | SITTINGBOURNE | ME10 2QB | Swale |  | Warehouse And Premises | industrial | 2 | 9426.84 | 101470 | GIA | 735000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.84 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 58 | 14.98 | 236 | 25 | 1113907 | SPN-S000000393383 | 1000 | 700 | 60-80% |  | 197 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3486 | 0.73897 | SPN-S000000008444 | 10953806000;11027714000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
428 | 50.9 | SWEEEP KUUSAKOSKI, GAS ROAD | SITTINGBOURNE | ME10 2QD | Swale |  | Warehouse And Premises | industrial | 1 | 9016.59 | 97054 | GIA | 317500 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.47 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 60 | 14.33 | 225 | 25 | 1118323 | SPN-S000000400170 | 800 | 560 | 60-80% | SITTINGBOURNE WEST 33/11KV | 35 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3464 | 0.73481 | SPN-S000000008444 | 10123848000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
429 | 50.9 | UNITS 1-3 & 6-8, WATERHAM BUSINESS PARK, HIGH STREET ROAD | FAVERSHAM | ME13 9EJ | Swale |  | Warehouse And Premises | industrial | 1 | 7998.77 | 86098 | GIA | 300000 | FAVERSHAM 33/11KV | inside-area | 4.9 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 68 | 12.71 | 200 | 21 | 1007937 | SPN-S000000342968 | 500 | 250 | 40-60% | FAVERSHAM 33/11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3258 | 0.97884 | SPN-S000000008405 | 5581827000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
430 | 50.9 | WESTON WORKS, BRENT HILL | FAVERSHAM | ME13 7EB | Swale |  | Factory And Premises | industrial | 1 | 7680.7 | 82674 | GIA | 382500 | FAVERSHAM 33/11KV | inside-area | 1.7 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 71 | 12.21 | 461 | 21 | 1011361 | SPN-S000000391881 | 500 | 350 | 60-80% | FAVERSHAM 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3184 | 0.88897 | SPN-S000000008405 | 14535125000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
431 | 50.9 | 1-2, MILLEN ROAD INDUSTRIAL ESTATE, MILLEN ROAD | SITTINGBOURNE | ME10 2AA | Swale |  | Factory And Premises | industrial | 2 | 5785.1 | 62270 | GIA | 508000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.29 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 94 | 9.19 | 347 | 25 | 1153107 | SPN-S000000391696 | 500 | 250 | 40-60% | SITTINGBOURNE WEST 33/11KV | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3461 | 0.73216 | SPN-S000000008444 | 14799918000;14835976000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
432 | 50.9 | BENNETT OPIE, CHALKWELL ROAD | SITTINGBOURNE | ME10 2LD | Swale |  | Factory And Premises | industrial | 1 | 5496.17 | 59160 | GIA | 260000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.03 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 99 | 8.73 | 330 | 25 | 1156217 | SPN-S000000391695 | 315 | 32 | 0-20% | SITTINGBOURNE WEST 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3465 | 0.7275 | SPN-S000000008444 | 9104995000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
433 | 50.9 | ARCOLA HOUSE, STAPLEHURST ROAD | SITTINGBOURNE | ME10 2NH | Swale |  | Factory And Premises | industrial | 1 | 5123.2 | 55146 | GIA | 260000 | SITTINGBOURNE WEST 33/11KV | inside-area | 0.6 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 8.14 | 307 | 25 | 1160231 | SPN-S000000391715 | 500 | 350 | 60-80% | SITTINGBOURNE WEST 33/11KV | 144 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.71904 | SPN-S000000008444 | 14076747000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
434 | 50.9 | BUILDING 1040 & 1100, GALLEY DRIVE, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8GA | Swale |  | Laboratory ,Offices And Premises | industrial | 1 | 3983.75 | 42881 | NIA | 432500 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.18 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 6.33 | 398 | 25 | 1172496 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002531338 | B2 to B7 General Industrial and Special Industrial Groups | 1115 | D | District Heating | 4 | 1 | Heating and Mechanical Ventilation | 2013-10-15 |  | 1 | FALSE | 51.3134 | 0.72532 | SPN-S000000008444 | 5788695000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
435 | 50.9 | FOURAYES FARM, BREDGAR LANE | SITTINGBOURNE | ME9 8BJ | Maidstone |  | Factory And Premises | industrial | 1 | 3907.09 | 42056 | GIA | 142000 | SITTINGBOURNE WEST 33/11KV | inside-area | 5.48 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 6.21 | 234 | 25 | 1173321 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3041 | 0.66335 | SPN-S000000008444 | 1108867000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
436 | 50.9 | BUILDINGS 760 770 & 780, GUILLAT AVENUE, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8GU | Swale |  | Warehouse And Premises | industrial | 1 | 2912.57 | 31351 | GIA | 138000 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.33 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 4.63 | 73 | 25 | 1184026 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023202012 | B2 to B7 General Industrial and Special Industrial Groups | 2970 | E | District Heating | 4 | 1 | Heating and Mechanical Ventilation | 2013-10-15 |  | 0.75 | FALSE | 51.3121 | 0.72601 | SPN-S000000008444 | 5768484000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
437 | 50.9 | 29, ASHFORD ROAD | FAVERSHAM | ME13 8XN | Swale |  | Warehouse And Premises | industrial | 1 | 2618.34 | 28184 | GIA | 119000 | FAVERSHAM 33/11KV | inside-area | 1.75 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 4.16 | 65 | 21 | 1065851 | SPN-S000000394302 | 500 | 250 | 40-60% | FAVERSHAM 33/11KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062380001 | General Industrial and Special Industrial Groups | 1972 | C | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2026-05-22 |  | 1 | FALSE | 51.306 | 0.88872 | SPN-S000000008405 | 215476147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
438 | 50.9 | MARCO INDUSTRIES LTD GF WORKSHOP & OFFICES 1A - 7A 152, STAPLEHURST ROAD | SITTINGBOURNE | ME10 1XS | Swale |  | Factory And Premises | industrial | 1 | 2487.34 | 26773 | GIA | 159000 | SITTINGBOURNE WEST 33/11KV | inside-area | 0.52 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 3.95 | 149 | 25 | 1188604 | SPN-S000000391715 | 500 | 350 | 60-80% | SITTINGBOURNE WEST 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3453 | 0.71917 | SPN-S000000008444 | 14343974000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
439 | 50.9 | NATURAL BORN MOVERS - THUNDERHILL BUSINESS PARK, HICKMANS GREEN | FAVERSHAM | ME13 9NT | Swale |  | Warehouse And Premises | industrial | 1 | 2286.94 | 24616 | GIA | 74000 | FAVERSHAM 33/11KV | inside-area | 4.02 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 3.63 | 57 | 21 | 1069419 | SPN-R000000840510-000-067Z | 100 | 70 | 60-80% | FAVERSHAM 33/11KV | 184 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.2895 | 0.95596 | SPN-S000000008405 | 8679205000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
440 | 50.9 | NORTH LANE | FAVERSHAM | ME13 7DY | Swale | SHEPHERD NEAME LTD | Warehouse And Premises | industrial | 1 | 2265.4 | 24385 | GIA | 100000 | FAVERSHAM 33/11KV | inside-area | 1.73 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 3.6 | 57 | 21 | 1069650 | SPN-S000000394288 | 800 | 560 | 60-80% | FAVERSHAM 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 |  | Retail/Financial and Professional Services | 2663 | D | Natural Gas | 4 | 2 | Air Conditioning | 2023-07-19 |  | 1 | FALSE | 51.317 | 0.8877 | SPN-S000000008405 | 536834145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
441 | 50.9 | THE FORMER COLD STORE DARGATE FARM, PLUM PUDDING LANE | FAVERSHAM | ME13 9HB | Swale |  | Warehouse And Premises | industrial | 1 | 2010.78 | 21644 | GIA | 47000 | FAVERSHAM 33/11KV | inside-area | 5.28 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 3.2 | 50 | 21 | 1072391 | SPN-R000000840509-000-259Z | 100 | 50 | 40-60% | FAVERSHAM 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10093085250 | B8 Storage or Distribution | 2272 | F | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-06-03 |  | 1 | FALSE | 51.3151 | 0.98739 | SPN-S000000008405 | 10644603000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
442 | 50.9 | WAREHOUSING STREET FARM POND FARM ROAD | SITTINGBOURNE | ME9 8JR | Swale |  | Warehouse And Premises | industrial | 1 | 1880 | 20236 | GIA | 95000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.28 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.99 | 47 | 25 | 1195141 | SPN-R000000844414-000-217Z | 200 | 100 | 40-60% | SITTINGBOURNE WEST 33/11KV | 115 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3341 | 0.70087 | SPN-S000000008444 | 14949903000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
443 | 50.3 | LITTLEBROOK DC2, SHIELD ROAD | DARTFORD | DA1 5UR | Dartford |  | Warehouse And Premises | industrial | 1 | 4418.68 | 47562 | GIA | 740000 | PURFLEET PRIMARY | inside-area | 1.88 | Purfleet Grid 33 | Warley | HAROLD HILL | 7.7 | primary | 7.7 | Green | 21.2 | 11.9 | Thermal | 0 | 0 | 0 | 0 | 8.1 | Purfleet Grid 33kV | 23.5 | GREEN | 36.6 | 19.8 | GREEN | 10 | 1007.5 | 2 | 20.4 | 17 | Summer | 43.5294 | 7.4 | Green (Over 5% headroom) | 54902 | 100 | 7.02 | 110 | 1 | 299945 | [9 empty] | Warley | WARLEY | 8 | 1710.9 | 1710.9 | 0 | 0 | 205.9 | 2027-08 | 10023437857 | B8 Storage or Distribution | 4374 | A | Natural Gas | 5 |  | Heating and Natural Ventilation | 2020-04-01 |  | 1 | FALSE | 51.4633 | 0.24357 | EPN-S0000000H7013 | 13184062000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
444 | 49.7 | NETWORK CENTRE, CAMPUS WAY, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0PZ | Medway |  | Offices And Premises | office | 1 | 1812.5 | 19510 | NIA | 297500 | RAINHAM MARK 33/11KV | inside-area | 0.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 100 | 2.88 | 127 | 37 | 2368735 | SPN-S000000316786 | 500 | 250 | 40-60% | RAINHAM MARK 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3645 | 0.57398 | SPN-S000000008525 | 4300930000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
445 | 49.7 | PASSENGER INSPECTION FACILITY, PASSENGER TERMINAL BUILDING, EASTERN DOCKS | DOVER | CT16 1JA | Dover |  | Offices And Premises | office | 1 | 1614.96 | 17383 | GIA | 132000 | DOVER 33/11KV | inside-area | 1.66 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.57 | 113 | 39 | 1367038 | SPN-R000000839108-000-189Z | 100 | 70 | 60-80% | DOVER 33/11KV | 353 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10096170994 | Others: Passenger Terminals | 5332 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-07-02 |  | 0.8 | FALSE | 51.1292 | 1.3349 | SPN-S000000008391 | 11909852000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
446 | 49.7 | 109-111, LONDON ROAD | DOVER | CT17 0TH | Dover |  | Offices And Premises | office | 1 | 1440.6 | 15506 | NIA | 102000 | DOVER 33/11KV | inside-area | 0.99 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 2.29 | 101 | 39 | 1368915 | SPN-S000000363188 | 500 | 50 | 0-20% | DOVER 33/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062289642 | B1 Offices and Workshop businesses | 1543 | D | Natural Gas | 3 | 3 | Heating and Natural Ventilation | 2021-01-26 |  | 0.67 | FALSE | 51.1348 | 1.3001 | SPN-S000000008391 | 928688000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
447 | 49.7 | THISTLEY HILL, MELBOURNE AVENUE | DOVER | CT16 2JH | Dover |  | Offices And Premises | office | 1 | 1126.2 | 12122 | NIA | 78500 | DOVER 33/11KV | inside-area | 2.09 | Folkestone Total | Sellindge | East Kent Zone | 19.3 | primary | 19.3 | Green | 51.8 | 32.5 | Thermal | 0 | 0 | 4.2 | 0 | 10.2 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | Green (Over 5% headroom) | 137611 | 100 | 1.79 | 79 | 39 | 1372299 | SPN-S000000363035 | 500 | 350 | 60-80% | DOVER 33/11KV | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1473 | 1.3035 | SPN-S000000008391 | 6998509000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
448 | 49.7 | CECIL STREET | MARGATE | CT9 1XZ | Thanet | THANET DISTRICT COUNCIL | Offices And Premises | office | 1 | 3960 | 42625 | NIA | 188000 | MARGATE 33/11KV | inside-area | 0.81 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 6.29 | 277 | 24 | 521986 | SPN-S000000342127 | 500 | 150 | 20-40% | MARGATE 33/11KV | 145 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3869 | 1.3858 | SPN-S000000008655 | 455131145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
449 | 49.7 | OFFICES UNIT H1, WESTWOOD INDUSTRIAL ESTATE, ENTERPRISE ROAD | MARGATE | CT9 4JX | Thanet |  | Offices And Premises | office | 1 | 1988.58 | 21405 | NIA | 120000 | MARGATE 33/11KV | inside-area | 1.74 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 3.16 | 139 | 24 | 543206 | SPN-S000000342996 | 315 | 94 | 20-40% | THANET 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3673 | 1.3922 | SPN-S000000008655 | 14333086000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
450 | 49.7 | UNIT R1, CONTINENTAL APPROACH, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JL | Thanet |  | Workshop And Premises | industrial | 1 | 1574 | 16942 | GIA | 85500 | MARGATE 33/11KV | inside-area | 1.94 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.5 | 71 | 24 | 547669 | SPN-S000000341999 | 500 | 350 | 60-80% | THANET 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3648 | 1.3907 | SPN-S000000008655 | 1229848000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
451 | 49.7 | R G SCOTTS THE OLD ICE WORKS, BATH PLACE | MARGATE | CT9 2BN | Thanet |  | Workshop And Premises | industrial | 1 | 1521.48 | 16377 | GIA | 35250 | MARGATE 33/11KV | inside-area | 1.15 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.42 | 68 | 24 | 548234 | SPN-S000000341983 | 800 | 240 | 20-40% | MARGATE 33/11KV | 18 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3889 | 1.3897 | SPN-S000000008655 | 7438598000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
452 | 49.7 | UNITS J2 AND J3 CHANNEL ROAD, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JS | Thanet |  | Warehouse And Premises | industrial | 1 | 1518.55 | 16346 | GIA | 83500 | MARGATE 33/11KV | inside-area | 1.88 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.41 | 38 | 24 | 548265 | SPN-S000000341999 | 500 | 350 | 60-80% | THANET 33/11KV | 156 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 |  | B1 Offices and Workshop businesses | 1820 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2021-02-12 |  | 0.75 | FALSE | 51.3658 | 1.3919 | SPN-S000000008655 | 11299726000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
453 | 49.7 | UNIT J7, CHANNEL ROAD, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JS | Thanet |  | Warehouse And Premises | industrial | 1 | 1436.3 | 15460 | GIA | 70000 | MARGATE 33/11KV | inside-area | 1.88 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.28 | 36 | 24 | 549151 | SPN-S000000341999 | 500 | 350 | 60-80% | THANET 33/11KV | 156 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10012956494 | B8 Storage or Distribution | 1477 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-11-30 |  | 1 | FALSE | 51.3658 | 1.3919 | SPN-S000000008655 | 4885056000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
454 | 49.7 | UNIT 14, ENTERPRISE WAY | MARGATE | CT9 4JF | Thanet |  | Warehouse And Premises | industrial | 1 | 1378.8 | 14841 | GIA | 213000 | MARGATE 33/11KV | inside-area | 1.48 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.19 | 34 | 24 | 549770 | SPN-R000000834910-000-001Z | 200 | 140 | 60-80% | MARGATE 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003079328 | General Industrial and Special Industrial Groups | 1238 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-08-27 |  | 1 | FALSE | 51.3689 | 1.3891 | SPN-S000000008655 | 5320902000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
455 | 49.7 | 18-20, DANE ROAD | MARGATE | CT9 2AA | Thanet |  | Workshop And Premises | industrial | 1 | 1351 | 14542 | GIA | 43500 | MARGATE 33/11KV | inside-area | 1.02 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.15 | 61 | 24 | 550069 | SPN-S000000343002 | 315 | 158 | 40-60% | MARGATE 33/11KV | 96 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3872 | 1.3899 | SPN-S000000008655 | 455416145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
456 | 49.7 | UNIT A, TIVOLI BROOKS | MARGATE | CT9 5TB | Thanet |  | Warehouse And Premises | industrial | 1 | 1341.29 | 14438 | GIA | 103000 | MARGATE 33/11KV | inside-area | 0.24 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2.13 | 34 | 24 | 550173 | SPN-S000000343679 | 1000 | 700 | 60-80% | MARGATE 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013310198 | B8 Storage or Distribution | 1866 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-09-17 |  | 0.67 | FALSE | 51.383 | 1.3792 | SPN-S000000008655 | 6453828000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
457 | 49.7 | 62, ADDISCOMBE ROAD | MARGATE | CT9 2SU | Thanet | NORTHDOWN WINDOWS | Workshop And Premises | industrial | 1 | 1258.5 | 13546 | GIA | 37750 | MARGATE 33/11KV | inside-area | 0.83 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2 | 57 | 24 | 551065 | SPN-S000000342808 | 500 | 350 | 60-80% | MARGATE 33/11KV | 139 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062306903 | Retail/Financial and Professional Services | 714 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-04-18 |  | 1 | FALSE | 51.3825 | 1.3912 | SPN-S000000008655 | 535950145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
458 | 49.7 | UNIT C, TIVOLI BROOKS | MARGATE | CT9 5TB | Thanet |  | Warehouse, Office And Premises | industrial | 1 | 1255.68 | 13516 | GIA | 101000 | MARGATE 33/11KV | inside-area | 0.24 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 2 | 88 | 24 | 551095 | SPN-S000000343679 | 1000 | 700 | 60-80% | MARGATE 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013310198 | B8 Storage or Distribution | 1866 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-09-17 |  | 1 | FALSE | 51.383 | 1.3792 | SPN-S000000008655 | 8603242000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
459 | 49.7 | 4-12, HAROLD ROAD | MARGATE | CT9 2HT | Thanet |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1223.1 | 13165 | GIA | 44750 | MARGATE 33/11KV | inside-area | 1.71 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 1.94 | 55 | 24 | 551446 | SPN-S000000343534 | 1000 | 700 | 60-80% | MARGATE 33/11KV | 97 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062095764 | Offices and Workshop Businesses | 1573 | G | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-09-10 |  | 0.67 | FALSE | 51.3895 | 1.3997 | SPN-S000000008655 | 9821444000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
460 | 49.7 | ADAMS GAS, STRASBOURG STREET, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JJ | Thanet |  | Warehouse, Office And Premises | industrial | 1 | 1130.93 | 12173 | GIA | 69000 | MARGATE 33/11KV | inside-area | 1.45 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 1.8 | 79 | 24 | 552438 | SPN-S000000341949 | 500 | 350 | 60-80% | THANET 33/11KV | 203 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3694 | 1.3895 | SPN-S000000008655 | 10469052000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
461 | 49.7 | 52, ATHELSTAN ROAD | MARGATE | CT9 2BB | Thanet | F L PETTMAN LTD | Warehouse And Premises | industrial | 1 | 1126.35 | 12124 | GIA | 21750 | MARGATE 33/11KV | inside-area | 1.34 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 1.79 | 28 | 24 | 552487 | SPN-S000000341983 | 800 | 240 | 20-40% | MARGATE 33/11KV | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3904 | 1.3912 | SPN-S000000008655 | 458551145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
462 | 49.7 | UNITS Y1-Y2, CONTINENTAL APPROACH, WESTWOOD INDUSTRIAL ESTATE | MARGATE | CT9 4JG | Thanet |  | Factory And Premises | industrial | 1 | 1006.81 | 10837 | GIA | 48500 | MARGATE 33/11KV | inside-area | 1.53 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 1.6 | 60 | 24 | 553774 | SPN-R000000834910-000-001Z | 200 | 140 | 60-80% | MARGATE 33/11KV | 118 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.368 | 1.3877 | SPN-S000000008655 | 1282855000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
463 | 49.7 | MATALAN RETAIL LTD, BROOKFIELD ROAD | ASHFORD | TN23 4YW | Ashford |  | Retail Warehouse And Premises | bigbox | 1 | 3715.3 | 39991 | GIA | 362500 | SINGLETON 33/6.6KV | inside-area | 0.07 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 5.9 | 334 | 24 | 708123 | SPN-S000000363810 | 750 | 525 | 60-80% | SINGLETON 33/6.6KV | 251 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012844265 | A1/A2 Retail and Financial/Professional services | 3738 | B | Natural Gas | 3 | 2 | Air Conditioning | 2022-02-21 |  | 1 | FALSE | 51.1468 | 0.84792 | SPN-S000000008610 | 13352276000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
464 | 49.7 | 1, SIR BERNARD PAGET AVENUE | ASHFORD | TN23 3RT | Ashford |  | Superstore And Premises | bigbox | 1 | 2767.34 | 29787 | GIA | 505000 | SINGLETON 33/6.6KV | inside-area | 1.18 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 4.4 | 249 | 24 | 718327 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1552 | 0.85649 | SPN-S000000008610 | 7041915000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
465 | 49.6 | BOND HOUSE, NEW ROAD | SHEERNESS | ME12 1BB | Swale | BOND SHOPFITTERS LTD | Factory And Premises | industrial | 1 | 8836.68 | 95117 | GIA | 437500 | SHEERNESS 33/6.6KV | inside-area | 0.39 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 54 | 14.04 | 530 | 19 | 734027 | SPN-S000000393994 | 800 | 560 | 60-80% | SHEERNESS 33/6.6KV | 173 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10032881501 | B2 to B7 General Industrial and Special Industrial Groups | 7985 | F | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-11-16 |  | 0.5 | FALSE | 51.4337 | 0.74927 | SPN-S000000008483 | 1528384000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
466 | 49.6 | UNIT E, DORSET ROAD | SHEERNESS | ME12 1LP | Swale | BOND SHOPFITTERS | Warehouse And Premises | industrial | 1 | 5401.5 | 58141 | GIA | 265000 | SHEERNESS 33/6.6KV | inside-area | 0.74 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 88 | 8.58 | 135 | 19 | 771003 | SPN-S000000393724 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062377007 | General Industrial and Special Industrial Groups | 2990 | C | Natural Gas | 3 | 1 | Air Conditioning | 2022-11-28 |  | 0.5 | FALSE | 51.4307 | 0.75117 | SPN-S000000008483 | 3262206000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
467 | 49.6 | THAMES REINFORCEMENTS LTD, NEW ROAD | SHEERNESS | ME12 1LZ | Swale |  | Warehouse And Premises | industrial | 1 | 5202.42 | 55998 | GIA | 540000 | SHEERNESS 33/6.6KV | inside-area | 0.41 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 92 | 8.27 | 130 | 19 | 773146 | SPN-S000000393994 | 800 | 560 | 60-80% | SHEERNESS 33/6.6KV | 201 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4336 | 0.75078 | SPN-S000000008483 | 5699081000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
468 | 49.6 | UNIT 1 REGIS HOUSE, NEW ROAD | SHEERNESS | ME12 1HW | Swale |  | Factory And Premises | industrial | 1 | 4925.44 | 53017 | GIA | 267500 | SHEERNESS 33/6.6KV | inside-area | 0.25 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 97 | 7.83 | 296 | 19 | 776127 | SPN-S000000392990 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062376999 | B2 to B7 General Industrial and Special Industrial Groups | 5894 | B | Biomass | 3 | 2 | Heating and Natural Ventilation | 2019-12-11 |  | 1 | FALSE | 51.435 | 0.74981 | SPN-S000000008483 | 14460887000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
469 | 49.6 | WESTMINSTER PACKING LTD, NEW ROAD | SHEERNESS | ME12 1LN | Swale |  | Factory And Premises | industrial | 1 | 3785.4 | 40746 | GIA | 162000 | SHEERNESS 33/6.6KV | inside-area | 0.68 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 6.02 | 227 | 19 | 788398 | SPN-S000000393786 | 315 | 158 | 40-60% | SHEERNESS 33/6.6KV | 144 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4312 | 0.74706 | SPN-S000000008483 | 391535147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
470 | 49.6 | UNITS 1 & 2, BULLDOZER HOUSE, NEW ROAD | SHEERNESS | ME12 1LN | Swale |  | Factory And Premises; Warehouse And Premises | industrial | 2 | 3750.6 | 40371 | GIA | 232000 | SHEERNESS 33/6.6KV | inside-area | 0.68 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 5.96 | 225 | 19 | 788773 | SPN-S000000393786 | 315 | 158 | 40-60% | SHEERNESS 33/6.6KV | 144 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4312 | 0.74706 | SPN-S000000008483 | 528532145;528239145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
471 | 49.6 | BOND RETAIL SERVICES LTD, DORSET ROAD | SHEERNESS | ME12 1LP | Swale |  | Warehouse And Premises | industrial | 1 | 3062.19 | 32961 | GIA | 161000 | SHEERNESS 33/6.6KV | inside-area | 0.74 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 4.87 | 77 | 19 | 796183 | SPN-S000000393724 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062377007 | General Industrial and Special Industrial Groups | 2990 | C | Natural Gas | 3 | 1 | Air Conditioning | 2022-11-28 |  | 0.5 | FALSE | 51.4307 | 0.75117 | SPN-S000000008483 | 2014990000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
472 | 49.6 | CHECKMATE LTD, NEW ROAD | SHEERNESS | ME12 1PZ | Swale |  | Factory And Premises | industrial | 1 | 2592.36 | 27904 | GIA | 109000 | SHEERNESS 33/6.6KV | inside-area | 0.51 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 4.12 | 156 | 19 | 801240 | SPN-S000000393994 | 800 | 560 | 60-80% | SHEERNESS 33/6.6KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023197295 | General Industrial and Special Industrial Groups | 2479 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2024-04-10 |  | 1 | FALSE | 51.4326 | 0.7482 | SPN-S000000008483 | 7000437000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
473 | 49.6 | ALLBART ENGLAND COMPANY LTD, NEW ROAD | SHEERNESS | ME12 1AU | Swale |  | Factory And Premises | industrial | 1 | 2435.62 | 26217 | GIA | 115000 | SHEERNESS 33/6.6KV | inside-area | 0.26 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 3.87 | 146 | 19 | 802927 | SPN-S000000393155 | 500 | 150 | 20-40% | SHEERNESS 33/6.6KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002531386 | B2 to B7 General Industrial and Special Industrial Groups | 2489 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-04-11 |  | 0.5 | FALSE | 51.4361 | 0.75251 | SPN-S000000008483 | 6129535000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
474 | 49.6 | PTC SOUTH EAST LTD, BRIELLE WAY | SHEERNESS | ME12 1YW | Swale |  | Road Haulage Depot And Premises | industrial | 1 | 1945.15 | 20937 | GIA | 34250 | SHEERNESS 33/6.6KV | inside-area | 0.64 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 3.09 | 49 | 19 | 808207 | SPN-S000000391526 | 300 | 150 | 40-60% | SHEERNESS 33/6.6KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002529314 | Offices and Workshop Businesses | 1396 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-06-03 |  | 0.5 | FALSE | 51.4317 | 0.74596 | SPN-S000000008483 | 8192334000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
475 | 49.5 | 223, TONBRIDGE ROAD | TONBRIDGE | TN12 5LA | Tonbridge & Malling | BRYMOR LTD | Factory And Premises | industrial | 1 | 12806.02 | 137843 | GIA | 407500 | MEREWORTH 33/11KV | inside-area | 5.29 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 37 | 20.35 | 768 | 30 | 866503 | SPN-R000000864309-000-089Z | 100 | 30 | 20-40% | MEREWORTH 33/11KV | 204 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2077 | 0.3698 | SPN-S000000008643 | 137088148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
476 | 49.5 | UNIT 1, ARNOLDS BUSINESS PARK, BRANBRIDGES ROAD | TONBRIDGE | TN12 5LG | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 4111.9 | 44260 | GIA | 235000 | MEREWORTH 33/11KV | inside-area | 5.22 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 6.53 | 103 | 30 | 960086 | SPN-S000000391434 | 750 | 525 | 60-80% | MEREWORTH 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000966776 | B8 Storage or Distribution | 4115 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-09-22 |  | 1 | FALSE | 51.2107 | 0.3941 | SPN-S000000008643 | 8333337000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
477 | 49.5 | UNIT 4, ARNOLDS BUSINESS PARK, BRANBRIDGES ROAD | TONBRIDGE | TN12 5HE | Tonbridge & Malling |  | Factory And Premises; Workshop And Premises | industrial | 2 | 3661.73 | 39414 | GIA | 271000 | MEREWORTH 33/11KV | inside-area | 5.25 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 5.82 | 220 | 30 | 964932 | SPN-S000000391435 | 800 | 400 | 40-60% | MEREWORTH 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2109 | 0.39636 | SPN-S000000008643 | 228922000;188687000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
478 | 49.5 | MERLIN HOUSE, SEVEN MILE LANE | SEVENOAKS | TN15 8QY | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2150.22 | 23145 | GIA | 106000 | MEREWORTH 33/11KV | inside-area | 2.78 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 3.42 | 54 | 30 | 981201 | SPN-R000000864305-000-020Z | 50 | 15 | 20-40% | MEREWORTH 33/11KV | 96 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002907569 | Storage or Distribution | 1989 | B | Biomass | 3 | 2 | Heating and Natural Ventilation | 2025-08-12 |  | 1 | FALSE | 51.278 | 0.35389 | SPN-S000000008643 | 8214248000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
479 | 49.3 | COUNCIL OFFICES, HOME GARDENS | DARTFORD | DA1 1EQ | Dartford | DARTFORD BOROUGH COUNCIL | Offices And Premises | office | 1 | 5281.2 | 56846 | NIA | 505000 | DARTFORD GRID B 11KV | inside-area | 0.86 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 8.39 | 370 | 54 | 2715903 | LPN-S000000073726 | 800 | 720 | 80-100% | DARTFORD GRID B 11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4425 | 0.21651 | LPN-S000000000716 | 168108147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
480 | 49.3 | SITE F, RIVERSIDE INDUSTRIAL ESTATE | DARTFORD | DA1 5BS | Dartford |  | Factory And Premises | industrial | 1 | 1815.8 | 19545 | GIA | 214000 | DARTFORD GRID B 11KV | inside-area | 0.53 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.89 | 109 | 54 | 2753204 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4517 | 0.21963 | LPN-S000000000716 | 168143147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
481 | 49.3 | KPT HOUSE, SANDPIT ROAD | DARTFORD | DA1 5BU | Dartford |  | Factory And Premises | industrial | 1 | 1629.2 | 17537 | GIA | 204000 | DARTFORD GRID B 11KV | inside-area | 0.84 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.59 | 98 | 54 | 2755212 | LPN-S000000073854 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4565 | 0.20713 | LPN-S000000000716 | 13407623000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
482 | 49.3 | UNIT 1 CHRISTOPHER HOUSE, PRINCES ROAD | DARTFORD | DA2 6EF | Dartford |  | Warehouse And Premises | industrial | 1 | 1482.05 | 15953 | GIA | 80500 | DARTFORD GRID B 11KV | inside-area | 2.92 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.36 | 37 | 54 | 2756796 | LPN-S000000072127 | 500 | 350 | 60-80% | DARTFORD GRID B 11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10023447138 | Retail/Financial and Professional Services | 1495 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-05-10 |  | 1 | FALSE | 51.4385 | 0.25062 | LPN-S000000000716 | 10345634000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
483 | 49.3 | THE OLD POWDER MILL, POWDER MILL LANE | DARTFORD | DA1 1NT | Dartford |  | Workshop And Premises | industrial | 1 | 1474.24 | 15869 | GIA | 130000 | DARTFORD GRID B 11KV | inside-area | 1.87 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.34 | 66 | 54 | 2756880 | SPN-S000000314395 | 1000 | 500 | 40-60% | DARTFORD 132/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000533812 | B2 to B7 General Industrial and Special Industrial Groups | 264 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-11-17 |  | 1 | FALSE | 51.4335 | 0.21863 | LPN-S000000000716 | 14536537000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
484 | 49.3 | J, RIVERSIDE INDUSTRIAL ESTATE | DARTFORD | DA1 5BS | Dartford |  | Factory And Premises | industrial | 1 | 1427.21 | 15362 | GIA | 176000 | DARTFORD GRID B 11KV | inside-area | 0.53 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.27 | 86 | 54 | 2757387 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4517 | 0.21963 | LPN-S000000000716 | 168159147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
485 | 49.3 | CHURCH HILL | DARTFORD | DA2 7DZ | Dartford | CLUBB ESTATES LTD | Workshop And Premises | industrial | 1 | 1377.9 | 14832 | GIA | 139000 | DARTFORD GRID B 11KV | inside-area | 2.02 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.19 | 62 | 54 | 2757917 | SPN-S000000314393 | 500 | 350 | 60-80% | DARTFORD 132/11KV | 207 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10023439194 | Storage or Distribution | 348 | E | Other | 3 |  | Unconditioned | 2025-08-27 |  | 1 | FALSE | 51.4318 | 0.21579 | LPN-S000000000716 | 7338935000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
486 | 49.3 | UNITS 38-41, PEARSON WAY, QUESTOR | DARTFORD | DA1 1JN | Dartford |  | Factory And Premises | industrial | 1 | 1343.04 | 14456 | GIA | 151000 | DARTFORD GRID B 11KV | inside-area | 1.88 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.13 | 81 | 54 | 2758293 | SPN-S000000316355 | 200 | 60 | 20-40% | DARTFORD 132/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000543642 | Offices and Workshop Businesses | 433 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-02-08 |  | 1 | FALSE | 51.4344 | 0.2237 | LPN-S000000000716 | 12653387000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
487 | 49.3 | 23B, FAWKES AVENUE, QUESTOR | DARTFORD | DA1 1JQ | Dartford |  | Warehouse And Premises | industrial | 1 | 1308.45 | 14084 | GIA | 238000 | DARTFORD GRID B 11KV | inside-area | 2 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.08 | 33 | 54 | 2758665 | SPN-S000000314400 | 500 | 250 | 40-60% | DARTFORD 132/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10094155487 | B8 Storage or Distribution | 1348 | A | Natural Gas | 5 |  | Air Conditioning | 2019-06-14 |  | 1 | FALSE | 51.4328 | 0.22185 | LPN-S000000000716 | 12269517000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
488 | 49.3 | UNIT 4 & UNIT 6A, SAUNDERS WAY, QUESTOR | DARTFORD | DA1 1JS | Dartford |  | Warehouse And Premises | industrial | 1 | 1273.93 | 13712 | GIA | 153000 | DARTFORD GRID B 11KV | inside-area | 2.02 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.02 | 32 | 54 | 2759037 | SPN-S000000316389 | 1000 | 500 | 40-60% | DARTFORD 132/11KV | 99 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4334 | 0.22478 | LPN-S000000000716 | 15037424000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
489 | 49.3 | 7, AVERY WAY, QUESTOR | DARTFORD | DA1 1JZ | Dartford |  | Warehouse And Premises | industrial | 1 | 1220.52 | 13138 | GIA | 144000 | DARTFORD GRID B 11KV | inside-area | 1.99 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 1.94 | 31 | 54 | 2759611 | SPN-S000000316389 | 1000 | 500 | 40-60% | DARTFORD 132/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000538633 | Offices and Workshop Businesses | 1177 | B | Natural Gas | 3 |  | Air Conditioning | 2023-12-05 |  | 1 | FALSE | 51.4331 | 0.22266 | LPN-S000000000716 | 12471631000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
490 | 49.3 | G2 - G4, RIVERSIDE INDUSTRIAL ESTATE | DARTFORD | DA1 5BS | Dartford |  | Warehouse And Premises | industrial | 1 | 1178.2 | 12682 | GIA | 144000 | DARTFORD GRID B 11KV | inside-area | 0.53 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 1.87 | 29 | 54 | 2760067 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000542252 | B8 Storage or Distribution | 314 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-03-27 |  | 1 | FALSE | 51.4517 | 0.21963 | LPN-S000000000716 | 15050774000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
491 | 49.3 | GND FLR 19, ST VINCENTS ROAD | DARTFORD | DA1 1XF | Dartford |  | Storage Depot And Premises | industrial | 1 | 1082.68 | 11654 | GIA | 20250 | DARTFORD GRID B 11KV | inside-area | 1.59 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 1.72 | 27 | 54 | 2761095 | LPN-S000000072003 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10002025001 | Offices and Workshop Businesses | 301 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-06-02 |  | 1 | FALSE | 51.4433 | 0.23301 | LPN-S000000000716 | 13444284000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
492 | 49.3 | UNITS 4-5, VICTORIA INDUSTRIAL ESTATE, VICTORIA ROAD | DARTFORD | DA1 5AJ | Dartford |  | Warehouse And Premises | industrial | 1 | 1062.11 | 11432 | GIA | 76500 | DARTFORD GRID B 11KV | inside-area | 0.29 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 1.69 | 27 | 54 | 2761317 | LPN-S000000073812 | 800 | 560 | 60-80% | DARTFORD GRID B 11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 200000542485 | General Industrial and Special Industrial Groups | 155 | E | Dual Fuel Appliances (Mineral + Wood) | 3 |  | Heating and Mechanical Ventilation | 2023-03-08 |  | 1 | FALSE | 51.4508 | 0.21645 | LPN-S000000000716 | 15012346000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
493 | 49.3 | UNIT 11, ELLIS WAY, QUESTOR | DARTFORD | DA1 1JX | Dartford |  | Warehouse And Premises | industrial | 1 | 1057.33 | 11381 | GIA | 125000 | DARTFORD GRID B 11KV | inside-area | 2.15 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 1.68 | 26 | 54 | 2761368 | SPN-S000000316177 | 1000 | 500 | 40-60% | DARTFORD 132/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10009429054 | Storage or Distribution | 1048 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-11-27 |  | 0.67 | FALSE | 51.4322 | 0.22516 | LPN-S000000000716 | 2100341000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
494 | 49.3 | TESCO DISTRIBUTION WAREHOUSE, MILLS ROAD, PRIORY PARK, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 13393.28 | 144164 | GIA | 1130000 | AYLESFORD 33/6.6KV | inside-area | 1.23 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 35 | 21.28 | 335 | 85 | 4921530 | SPN-S000000394509 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2898 | 0.46402 | SPN-S000000008312 | 6467516000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
495 | 49.3 | UNIT 2, WOOD CLOSE, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7UB | Tonbridge & Malling |  | Car Showroom And Premises; Warehouse And Premises | industrial | 5 | 11402.11 | 122731 | GIA | 1600000 | AYLESFORD 33/6.6KV | inside-area | 1.03 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 41 | 18.12 | 1026 | 85 | 4942963 | SPN-S000000394248 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2915 | 0.46935 | SPN-S000000008312 | 946267000;389838148;2382965000;398619148;8461994000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
496 | 49.3 | LHS UNIT 6, UPPER MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 8121.4 | 87418 | GIA | 385000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 57 | 12.91 | 203 | 85 | 4978276 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2915 | 0.47299 | SPN-S000000008312 | 7684359000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
497 | 49.3 | UNIT 7, UPPER MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 7893.36 | 84963 | GIA | 535000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 59 | 12.54 | 355 | 85 | 4980731 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2915 | 0.47299 | SPN-S000000008312 | 393202148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
498 | 49.3 | 188, FORSTAL ROAD | AYLESFORD | ME20 7AU | Tonbridge & Malling |  | Factory And Premises | industrial | 1 | 6917.85 | 74463 | GIA | 275000 | AYLESFORD 33/6.6KV | inside-area | 1.16 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 67 | 10.99 | 415 | 85 | 4991231 | SPN-S000000392171 | 300 | 150 | 40-60% | AYLESFORD 33/6.6KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3037 | 0.48339 | SPN-S000000008312 | 10370541000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
499 | 49.3 | ENTERPRISE FORWARDING LTD, NEW HYTHE BUSINESS PARK, BELLINGHAM WAY | AYLESFORD | ME20 6XS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 6781.4 | 72994 | GIA | 540000 | AYLESFORD 33/6.6KV | inside-area | 1.35 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 68 | 10.78 | 170 | 85 | 4992700 | SPN-S000000394449 | 500 | 350 | 60-80% | TOWNSEND HOOK 33/6.6KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002908828 | Storage or Distribution | 5538 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2025-02-12 |  | 0.75 | FALSE | 51.307 | 0.45078 | SPN-S000000008312 | 530908000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
500 | 49.3 | CONSOLIDATED PAPER HOUSE, FORSTAL ROAD | AYLESFORD | ME20 7AE | Maidstone |  | Warehouse And Premises | industrial | 1 | 6690.1 | 72012 | GIA | 327500 | AYLESFORD 33/6.6KV | inside-area | 2.05 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 69 | 10.63 | 167 | 85 | 4993682 | SPN-S000000392272 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3013 | 0.49678 | SPN-S000000008312 | 405390148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
501 | 49.3 | UNITS 14B-17, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 6172.99 | 66445 | GIA | 382500 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 75 | 9.81 | 154 | 85 | 4999249 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000966285 | B1 Offices and Workshop businesses | 5441 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-02-09 |  | 1 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 10643638000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
502 | 49.3 | UNIT 3, WESTMEAD, WEST POINT BUSINESS PARK, NEW HYTHE LANE | AYLESFORD | ME20 6SB | Tonbridge & Malling |  | Factory And Premises; Warehouse And Premises | industrial | 3 | 6147.22 | 66168 | GIA | 670500 | AYLESFORD 33/6.6KV | inside-area | 1.73 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 75 | 9.77 | 369 | 85 | 4999526 | SPN-S000000392198 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3126 | 0.45138 | SPN-S000000008312 | 10396354000;10362977000;10362980000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
503 | 49.3 | UNIT 1A & UNIT 1B, LARKFIELD MILL, BELLINGHAM WAY | AYLESFORD | ME20 6SQ | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 6108.2 | 65748 | GIA | 498500 | AYLESFORD 33/6.6KV | inside-area | 1.25 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 76 | 9.71 | 153 | 85 | 4999946 | SPN-S000000400184 | 1000 | 900 | 80-100% | AYLESFORD 33/6.6KV | 190 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013921860 | Storage or Distribution | 3048 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-07-30 |  | 1 | FALSE | 51.3061 | 0.45161 | SPN-S000000008312 | 6330500000;6330500000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
504 | 49.3 | UNIT 5, LINK 20 ESTATE, BELLINGHAM WAY | AYLESFORD | ME20 6XS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 3 | 6037.71 | 64989 | GIA | 665000 | AYLESFORD 33/6.6KV | inside-area | 1.35 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 77 | 9.59 | 151 | 85 | 5000705 | SPN-S000000394449 | 500 | 350 | 60-80% | TOWNSEND HOOK 33/6.6KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.307 | 0.45078 | SPN-S000000008312 | 2353882000;2353885000;2355302000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
505 | 49.3 | BROADMEAD HOUSE, BELLINGHAM WAY | AYLESFORD | ME20 6XS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 5131.18 | 55232 | GIA | 585000 | AYLESFORD 33/6.6KV | inside-area | 1.35 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 90 | 8.15 | 128 | 85 | 5010462 | SPN-S000000394449 | 500 | 350 | 60-80% | TOWNSEND HOOK 33/6.6KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002908828 | Storage or Distribution | 5538 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2025-02-12 |  | 1 | FALSE | 51.307 | 0.45078 | SPN-S000000008312 | 4921498000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
506 | 49.3 | UNIT 4, MILLS ROAD, PRIORY PARK, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7PP | Tonbridge & Malling |  | Factory And Premises; Warehouse And Premises | industrial | 2 | 5003.75 | 53860 | GIA | 593500 | AYLESFORD 33/6.6KV | inside-area | 1.23 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 93 | 7.95 | 300 | 85 | 5011834 | SPN-S000000394509 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013915616 | B8 Storage or Distribution | 2247 | D | Grid Supplied Electricity | 3 |  | Air Conditioning | 2020-02-29 |  | 1 | FALSE | 51.2898 | 0.46402 | SPN-S000000008312 | 2109940000;4848774000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
507 | 49.3 | PROSPECT HOUSE UNIT 5, CLICK AYLESFORD, FRANK SANDO WAY | AYLESFORD | ME20 7NY | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 4597 | 49482 | GIA | 475000 | AYLESFORD 33/6.6KV | inside-area | 1.58 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 7.31 | 115 | 85 | 5016212 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094699105 | B8 Storage or Distribution | 1198 | A+ | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2024-10-02 |  | 1 | FALSE | 51.298 | 0.48968 | SPN-S000000008312 | 15165145000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
508 | 49.3 | KENT HOUSE, MILLS ROAD, PRIORY PARK, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7PP | Tonbridge & Malling | KENT FROZEN FOODS LTD | Cold Store And Premises | industrial | 1 | 4437.08 | 47760 | GIA | 475000 | AYLESFORD 33/6.6KV | inside-area | 1.23 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 7.05 | 532 | 85 | 5017934 | SPN-S000000394509 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2898 | 0.46402 | SPN-S000000008312 | 4081611000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
509 | 49.3 | UNIT 1A, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 3994.7 | 42999 | GIA | 375000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 6.35 | 100 | 85 | 5022695 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10022895514 | B1 Offices and Workshop businesses | 1138 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-01-07 |  | 0.5 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 9680431000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
510 | 49.3 | UNIT 6C, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Warehouse | industrial | 1 | 3820.5 | 41123 | GIA | 335000 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 6.07 | 96 | 85 | 5024571 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000969997 | A1/A2 Retail and Financial/Professional services | 2199 | D | Natural Gas | 3 |  | Heating and Mechanical Ventilation | 2018-07-09 |  | 0.75 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 7206379000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
511 | 49.3 | UNIT 4B &4C, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3750.72 | 40372 | GIA | 325000 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.96 | 94 | 85 | 5025322 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002908233 | Storage or Distribution | 4167 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-10-13 |  | 1 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 12952494000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
512 | 49.3 | UNIT 18, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3585.94 | 38599 | GIA | 342500 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.7 | 90 | 85 | 5027095 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000969997 | A1/A2 Retail and Financial/Professional services | 2199 | D | Natural Gas | 3 |  | Heating and Mechanical Ventilation | 2018-07-09 |  | 0.75 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 14860802000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
513 | 49.3 | UNIT 3 AT 3, SHELDON WAY | AYLESFORD | ME20 6SF | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 3377.16 | 36351 | GIA | 313000 | AYLESFORD 33/6.6KV | inside-area | 1.67 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.37 | 84 | 85 | 5029343 | SPN-S000000393251 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3063 | 0.44497 | SPN-S000000008312 | 253191000;253188000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
514 | 49.3 | UNIT 14A, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3361.45 | 36182 | GIA | 307500 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.34 | 84 | 85 | 5029512 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000969997 | A1/A2 Retail and Financial/Professional services | 2199 | D | Natural Gas | 3 |  | Heating and Mechanical Ventilation | 2018-07-09 |  | 0.75 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 10643637000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
515 | 49.3 | M C GROUP LTD, BEDDOW WAY | AYLESFORD | ME20 7BT | Tonbridge & Malling |  | Vehicle Repair Workshop And Premises | industrial | 1 | 3354.1 | 36103 | GIA | 167000 | AYLESFORD 33/6.6KV | inside-area | 1.78 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.33 | 151 | 85 | 5029591 | SPN-S000000392305 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.303 | 0.49266 | SPN-S000000008312 | 406121148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
516 | 49.3 | UNIT 4D, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3296.49 | 35483 | GIA | 305000 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.24 | 82 | 85 | 5030211 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 |  | Storage or Distribution | 3662 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-10-13 |  | 1 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 2118108000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
517 | 49.3 | UNIT F1 & F2, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 3162.6 | 34042 | GIA | 292500 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.03 | 79 | 85 | 5031652 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003720351 | Storage or Distribution | 3052 | D | Natural Gas | 5 |  | Heating and Natural Ventilation | 2024-03-18 |  | 1 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 412614148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
518 | 49.3 | UNITS 8-9, BURNT ASH ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 3110.76 | 33484 | GIA | 340000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 4.94 | 78 | 85 | 5032210 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10092973155 | Storage or Distribution | 1049 | C | Natural Gas | 5 |  | Heating and Natural Ventilation | 2023-02-24 |  | 1 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 9737114000;8076880000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
519 | 49.3 | OLD MILL LANE | AYLESFORD | ME20 7DT | Maidstone | DAVID PAYNE & SON COACH BUILDERS LTD; FERCELL ENGINEERING | Warehouse And Premises; Workshop And Premises | industrial | 2 | 3056.2 | 32897 | GIA | 198000 | AYLESFORD 33/6.6KV | inside-area | 2.2 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 4.86 | 138 | 85 | 5032797 | SPN-S000000392172 | 800 | 560 | 60-80% | AYLESFORD 33/6.6KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003662558 | B1 Offices and Workshop businesses | 508 | E | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2017-10-11 |  | 1 | FALSE | 51.3056 | 0.49801 | SPN-S000000008312 | 198567148;412541148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
520 | 49.3 | UNIT 4A, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3020 | 32507 | GIA | 282500 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 4.8 | 76 | 85 | 5033187 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013922409 | Retail/Financial and Professional Services | 1175 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-09-13 |  | 0.5 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 14996075000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
521 | 49.3 | 1A, DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2642.2 | 28440 | GIA | 223000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 4.2 | 66 | 85 | 5037254 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002916044 | B8 Storage or Distribution | 1602 | C | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2022-07-22 |  | 1 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 186420148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
522 | 49.3 | UNIT 2 ACCESS 4:20, NEW HYTHE BUSINESS PARK, BELLINGHAM WAY | AYLESFORD | ME20 7HP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 2556.43 | 27517 | GIA | 281000 | AYLESFORD 33/6.6KV | inside-area | 1.41 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 4.06 | 64 | 85 | 5038177 | SPN-S000000394875 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002918578 | B8 Storage or Distribution | 3736 | B | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2022-04-14 |  | 1 | FALSE | 51.3044 | 0.44796 | SPN-S000000008312 | 5168240000;5168247000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
523 | 49.3 | UNIT 4A, MILLS ROAD, PRIORY PARK, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7PP | Tonbridge & Malling |  | Vehicle Repair Workshop And Premises | industrial | 1 | 2429.22 | 26148 | GIA | 247000 | AYLESFORD 33/6.6KV | inside-area | 1.23 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.86 | 109 | 85 | 5039546 | SPN-S000000394509 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002909799 | General Industrial and Special Industrial Groups | 952 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-11-09 |  | 0.67 | FALSE | 51.2898 | 0.46402 | SPN-S000000008312 | 2110045000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
524 | 49.3 | HALL ROAD | AYLESFORD | ME20 7QZ | Tonbridge & Malling | T N T ROAD FREIGHT | Warehouse And Premises | industrial | 1 | 2377.6 | 25592 | GIA | 282500 | AYLESFORD 33/6.6KV | inside-area | 0.57 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.78 | 59 | 85 | 5040102 | SPN-S000000392193 | 300 | 150 | 40-60% | AYLESFORD 33/6.6KV | 152 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062389922 | B8 Storage or Distribution | 1562 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2018-07-03 |  | 1 | FALSE | 51.2986 | 0.47485 | SPN-S000000008312 | 55274148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
525 | 49.3 | UNIT G-H, FORSTAL TRADING ESTATE, ST MICHAELS CLOSE | MAIDSTONE | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 2346.67 | 25259 | GIA | 227000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.73 | 59 | 85 | 5040435 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003719024 | Storage or Distribution | 3992 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-01-18 |  | 0.67 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 15074799000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
526 | 49.3 | UNIT E1, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone | LIN PAC PLASTICS LTD | Warehouse And Premises | industrial | 2 | 2287 | 24617 | GIA | 283000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.63 | 57 | 85 | 5041077 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003720384 | Storage or Distribution | 1163 | C | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2024-03-18 |  | 1 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 55969148;55969148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
527 | 49.3 | UNIT 1, BELLINGHAM WAY | AYLESFORD | ME20 6XS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2216.68 | 23860 | GIA | 255000 | AYLESFORD 33/6.6KV | inside-area | 1.35 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.52 | 55 | 85 | 5041834 | SPN-S000000394449 | 500 | 350 | 60-80% | TOWNSEND HOOK 33/6.6KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.307 | 0.45078 | SPN-S000000008312 | 1906651000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
528 | 49.3 | AYLESFORD MTW, LARKFIELD MILL, NEW HYTHE BUSINESS PARK, BELLINGHAM WAY | AYLESFORD | ME20 7SZ | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 2171.67 | 23376 | GIA | 285000 | AYLESFORD 33/6.6KV | inside-area | 1.24 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.45 | 98 | 85 | 5042318 | SPN-S000000400184 | 1000 | 900 | 80-100% | AYLESFORD 33/6.6KV | 291 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.307 | 0.45266 | SPN-S000000008312 | 7369730000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
529 | 49.3 | JAYAR HOUSE, FORSTAL ROAD | AYLESFORD | ME20 7AF | Maidstone |  | Warehouse And Premises | industrial | 1 | 2138.56 | 23019 | GIA | 148000 | AYLESFORD 33/6.6KV | inside-area | 1.98 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.4 | 53 | 85 | 5042675 | SPN-S000000394614 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3017 | 0.4958 | SPN-S000000008312 | 14697465000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
530 | 49.3 | UNIT 3 PART C, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2134.08 | 22971 | GIA | 149000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.39 | 53 | 85 | 5042723 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013921884 | Storage or Distribution | 1929 | B | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-02-24 |  | 0.6 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 14806771000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
531 | 49.3 | PRESTON HALL FARM, HALL ROAD | AYLESFORD | ME20 7QZ | Tonbridge & Malling | ARTHUR HEATH & COMPANY LTD | Warehouse And Premises | industrial | 1 | 2123.1 | 22853 | GIA | 174000 | AYLESFORD 33/6.6KV | inside-area | 0.57 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.37 | 53 | 85 | 5042841 | SPN-S000000392193 | 300 | 150 | 40-60% | AYLESFORD 33/6.6KV | 152 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2986 | 0.47485 | SPN-S000000008312 | 186417148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
532 | 49.3 | UNIT 4, ST MICHAELS CLOSE | AYLESFORD | ME20 7XE | Maidstone |  | Warehouse And Premises | industrial | 1 | 2023 | 21775 | OTH | 44750 | AYLESFORD 33/6.6KV | inside-area | 2.43 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.21 | 51 | 85 | 5043919 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 176 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.305 | 0.50155 | SPN-S000000008312 | 12858141000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
533 | 49.3 | UNIT 6A, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2015.76 | 21697 | GIA | 134000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.2 | 50 | 85 | 5043997 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013922409 | Retail/Financial and Professional Services | 1175 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-09-13 |  | 0.67 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 15031417000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
534 | 49.3 | UNIT 3C & 3D PRIORY PARK MILLS ROAD QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1972.71 | 21234 | GIA | 225000 | AYLESFORD 33/6.6KV | inside-area | 1.23 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.13 | 49 | 85 | 5044460 | SPN-S000000394509 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000965789 | General Industrial and Special Industrial Groups | 836 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-01-20 |  | 1 | FALSE | 51.2898 | 0.46402 | SPN-S000000008312 | 15025248000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
535 | 49.3 | 3A & 3B, DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1959.73 | 21094 | GIA | 149000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.11 | 49 | 85 | 5044600 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062628305 | B8 Storage or Distribution | 999 | C | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2022-07-27 |  | 1 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 2118389000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
536 | 49.3 | M20 MAINTENANCE COMPOUND, COLDHARBOUR LANE | AYLESFORD | ME20 7NS | Tonbridge & Malling |  | Storage Depot And Premises | industrial | 1 | 1959.08 | 21087 | GIA | 205000 | AYLESFORD 33/6.6KV | inside-area | 1.28 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.11 | 49 | 85 | 5044607 | SPN-S000000394906 | 200 | 60 | 20-40% | AYLESFORD 33/6.6KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2984 | 0.48535 | SPN-S000000008312 | 894028000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
537 | 49.3 | UNITS 7A-7B, MILLS ROAD, PRIORY PARK, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1915.22 | 20615 | GIA | 231000 | AYLESFORD 33/6.6KV | inside-area | 1.23 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.04 | 48 | 85 | 5045079 | SPN-S000000394509 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002909917 | General Industrial and Special Industrial Groups | 1058 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-07-18 |  | 1 | FALSE | 51.2898 | 0.46402 | SPN-S000000008312 | 14649715000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
538 | 49.3 | UNIT 4, DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1913.02 | 20592 | GIA | 161000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.04 | 48 | 85 | 5045102 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062389918 | B8 Storage or Distribution | 1785 | C | Grid Supplied Electricity | 5 |  | Air Conditioning | 2022-07-27 |  | 1 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 6161765000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
539 | 49.3 | UNIT 3 PART A, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1874.13 | 20173 | GIA | 131000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.98 | 47 | 85 | 5045521 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013921884 | Storage or Distribution | 1929 | B | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-02-24 |  | 0.6 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 14806769000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
540 | 49.2 | STATION ROAD | DARTFORD | DA4 9HQ | Dartford | G K N STEELSTOCK LTD | Warehouse And Premises | industrial | 1 | 13007.68 | 140013 | GIA | 575000 | FARNINGHAM 33/11KV | inside-area | 3.24 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 35 | 20.67 | 325 | 7 | 131995 | SPN-S000000316031 | 500 | 250 | 40-60% | FARNINGHAM 33/11KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4089 | 0.23737 | SPN-S000000008403 | 168958147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
541 | 49.2 | THE FLAGPOLE, DARENTH HILL | DARTFORD | DA2 7QY | Dartford | FRUIT DISTRIBUTION CENTRE | Warehouse And Premises | industrial | 1 | 3097.02 | 33336 | GIA | 220000 | FARNINGHAM 33/11KV | inside-area | 4.28 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 4.92 | 77 | 7 | 238672 | SPN-S000000316852 | 315 | 158 | 40-60% | FARNINGHAM 33/11KV | 350 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4178 | 0.24405 | SPN-S000000008403 | 2273193000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
542 | 49.1 | PARK FARM ROAD | FOLKESTONE | CT19 5EY | Folkestone & Hythe | BOOKER CASH & CARRY | Warehouse And Premises | industrial | 1 | 2800.3 | 30142 | GIA | 176000 | FOLKESTONE EAST 33/11KV | inside-area | 1.16 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 4.45 | 70 | 7 | 321068 | SPN-S000000371760 | 500 | 250 | 40-60% | MOREHALL 132/11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | B1 Offices and Workshop businesses | 177 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-03-03 |  | 1 | FALSE | 51.0931 | 1.1718 | SPN-S000000008660 | 88806145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
543 | 49.1 | 94, FOORD ROAD | FOLKESTONE | CT19 5AB | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2657.5 | 28605 | GIA | 58000 | FOLKESTONE EAST 33/11KV | inside-area | 0.53 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 4.22 | 66 | 7 | 322605 | SPN-S000000361387 | 500 | 150 | 20-40% | MOREHALL 132/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.085 | 1.1778 | SPN-S000000008660 | 7118715000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
544 | 49.1 | BROOMFIELD WORKS, FERNFIELD LANE | FOLKESTONE | CT18 7AW | Dover |  | Factory And Premises | industrial | 1 | 2494.7 | 26853 | GIA | 85500 | FOLKESTONE EAST 33/11KV | inside-area | 4.14 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 3.96 | 150 | 7 | 324357 | SPN-S000000361412 | 315 | 158 | 40-60% | FOLKESTONE EAST 33/11KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10034875454 | B2 to B7 General Industrial and Special Industrial Groups | 2287 | D | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2016-08-05 |  | 1 | FALSE | 51.1232 | 1.1734 | SPN-S000000008660 | 123579145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
545 | 49.1 | 218, DOVER ROAD | FOLKESTONE | CT19 6NJ | Folkestone & Hythe | C WHITEHEAD & CO LTD | Factory And Premises | industrial | 1 | 2394.25 | 25771 | GIA | 55000 | FOLKESTONE EAST 33/11KV | inside-area | 0.37 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 3.8 | 144 | 7 | 325439 | SPN-S000000361392 | 500 | 250 | 40-60% | FOLKESTONE EAST 33/11KV | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50106429 | Offices and Workshop Businesses | 35 | D | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2025-11-09 |  | 1 | FALSE | 51.0887 | 1.189 | SPN-S000000008660 | 532366145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
546 | 49.1 | PLAMIL HOUSE, BOWLES WELL GARDENS | FOLKESTONE | CT19 6PQ | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2278.16 | 24522 | GIA | 83000 | FOLKESTONE EAST 33/11KV | inside-area | 0.67 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 3.62 | 57 | 7 | 326688 | SPN-S000000362083 | 750 | 525 | 60-80% | FOLKESTONE EAST 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50049238 | General Industrial and Special Industrial Groups | 112 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-06-13 |  | 1 | FALSE | 51.0906 | 1.1922 | SPN-S000000008660 | 14427898000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
547 | 49.1 | UNITS 5-6, BOWLES WELL GARDENS | FOLKESTONE | CT19 6PQ | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1874.1 | 20173 | GIA | 79500 | FOLKESTONE EAST 33/11KV | inside-area | 0.67 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 2.98 | 47 | 7 | 331037 | SPN-S000000362083 | 750 | 525 | 60-80% | FOLKESTONE EAST 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0906 | 1.1922 | SPN-S000000008660 | 3053928000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
548 | 48.9 | THE JOHN GRAY CENTRE HORTONS WAY & UNITS E & F, THE FLYERS WAY | WESTERHAM | TN16 1DE | Sevenoaks |  | Factory, Warehouse And Premises | industrial | 1 | 3521.06 | 37900 | GIA | 350000 | SUNDRIDGE 33/11KV | inside-area | 4.22 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 5.6 | 211 | 9 | 266535 | SPN-S000000446811 | 1000 | 700 | 60-80% |  | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062688459 | B8 Storage or Distribution | 1865 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-04-22 |  | 1 | FALSE | 51.2707 | 0.075057 | SPN-S000000008496 | 13777441000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
549 | 48.9 | DUNBRICK DEPOT 2, MAIN ROAD | SEVENOAKS | TN14 6EP | Sevenoaks |  | Factory And Premises | industrial | 1 | 2189 | 23562 | GIA | 97500 | SUNDRIDGE 33/11KV | inside-area | 0.42 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 3.48 | 131 | 9 | 280873 | SPN-S000000446965 | 315 | 220 | 60-80% |  | 152 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2807 | 0.13985 | SPN-S000000008496 | 2306745000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
550 | 48.8 | 2, BADGER ROAD | CHATHAM | ME5 8TZ | Medway | MACKAYS OF CHATHAM | Factory And Premises | industrial | 1 | 14821.31 | 159535 | GIA | 715000 | LORDSWOOD 33/11KV | inside-area | 1.39 | Chatham Grid | Kingsnorth | Mid Kent Zone | 14.1 | primary | 14.1 | Green | 23.9 | 9.8 | Thermal | 0 | 4.8 | 0 | 4.8 | 13.5 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | Green (Over 5% headroom) | 100535 | 63 | 23.55 | 889 | 6 | 298151 | SPN-S000000312225 | 800 | 560 | 60-80% | CHATHAM WEST 33/11KV (OLD) | 48 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3353 | 0.54366 | SPN-S000000008646 | 129339000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
551 | 48.8 | TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells | GABRIEL CHEMIE UK LTD; MACK MULTIPLES DIVISION | Factory And Premises; Warehouse And Premises | industrial | 2 | 13472.38 | 145015 | GIA | 1122000 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 32 | 21.41 | 808 | 38 | 1786101 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000068208 | B8 Storage or Distribution | 2093 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2013-04-12 |  | 1 | FALSE | 51.1857 | 0.39037 | SPN-S000000008454 | 188892148;371998148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
552 | 48.8 | ADRIAN SCRIPPS LTD AT MOAT FARM | TONBRIDGE | TN12 6RR | Tunbridge Wells |  | Fruit Packing Depot And Premises (Part Exempt) | industrial | 1 | 13076.1 | 140750 | GIA | 365000 | PADDOCK WOOD 33/11KV | inside-area | 2.93 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 33 | 20.78 | 327 | 38 | 1790366 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10090053323 | B1 Offices and Workshop businesses | 213 | D | LPG | 3 |  | Heating and Natural Ventilation | 2020-03-31 |  | 1 | FALSE | 51.1883 | 0.35433 | SPN-S000000008454 | 13174371000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
553 | 48.8 | 3663 LTD, TRANSFESA ROAD | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Cold Store And Premises | industrial | 1 | 11647.87 | 125377 | GIA | 1090000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 38 | 18.51 | 1398 | 38 | 1805739 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1841 | 0.39815 | SPN-S000000008454 | 6945289000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
554 | 48.8 | UNITS 1B & 1C, THE INTERCHANGE, WESTED LANE | SWANLEY | BR8 8TE | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 10931.45 | 117665 | GIA | 1030000 | SWANLEY 33/11KV | inside-area | 2.93 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 40 | 17.37 | 273 | 18 | 954988 | SPN-S000000314549 | 800 | 560 | 60-80% | SWANLEY 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013771437 | Storage or Distribution | 10671 | A | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-02-24 |  | 0.75 | FALSE | 51.3862 | 0.18913 | SPN-S000000008528 | 6449760000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
555 | 48.8 | STIRLING HOUSE CLIPPER CLOSE, COLUMBUS AVENUE, MANSTON PARK | RAMSGATE | CT12 5GG | Thanet |  | Warehouse And Premises | industrial | 1 | 8906.23 | 95866 | GIA | 530000 | WESTGATE 33/11KV | inside-area | 2.66 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 49 | 14.15 | 223 | 16 | 719414 | SPN-S000000343511 | 800 | 560 | 60-80% | MANSTON 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3511 | 1.3224 | SPN-S000000008510 | 11555987000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
556 | 48.8 | NORTH SIDE, HENLEY ROAD | TONBRIDGE | TN12 6DQ | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 8235.95 | 88651 | GIA | 337500 | PADDOCK WOOD 33/11KV | inside-area | 0.7 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 53 | 13.09 | 206 | 38 | 1842465 | SPN-S000000442222 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 167 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1835 | 0.38948 | SPN-S000000008454 | 13930969000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
557 | 48.8 | 8, THE INTERCHANGE, WESTED LANE | SWANLEY | BR8 8TE | Sevenoaks |  | Warehouse And Premises | industrial | 4 | 8162.21 | 87857 | GIA | 993000 | SWANLEY 33/11KV | inside-area | 2.93 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 54 | 12.97 | 204 | 18 | 984796 | SPN-S000000314549 | 800 | 560 | 60-80% | SWANLEY 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002016851 | B2 to B7 General Industrial and Special Industrial Groups | 1515 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2020-08-05 |  | 1 | FALSE | 51.3862 | 0.18913 | SPN-S000000008528 | 6605252000;14784203000;14660766000;8472927000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
558 | 48.8 | THE TEARDROP CENTRE, LONDON ROAD | SWANLEY | BR8 8TS | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 6112.9 | 65799 | GIA | 550000 | SWANLEY 33/11KV | inside-area | 3.37 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 72 | 9.71 | 153 | 18 | 1006854 | SPN-R000000840309-000-018Z | 200 | 180 | 80-100% | FARNINGHAM 33/11KV | 266 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002019646 | Storage or Distribution | 6979 | B | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2025-12-03 |  | 1 | FALSE | 51.3867 | 0.19814 | SPN-S000000008528 | 188789148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
559 | 48.8 | 6, WESTED LANE | SWANLEY | BR8 8EE | Sevenoaks |  | Store And Premises; Warehouse And Premises | industrial | 2 | 5636.34 | 60669 | GIA | 426000 | SWANLEY 33/11KV | inside-area | 2.86 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 78 | 8.96 | 141 | 18 | 1011984 | SPN-S000000314549 | 800 | 560 | 60-80% | SWANLEY 33/11KV | 117 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002017525 | B2 to B7 General Industrial and Special Industrial Groups | 2373 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-05-26 |  | 1 | FALSE | 51.3877 | 0.19 | SPN-S000000008528 | 7092742000;12581517000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
560 | 48.8 | UNIT 1 MERLIN HOUSE, MERLIN WAY, MONKTON | RAMSGATE | CT12 5FE | Thanet |  | Warehouse Office And Premises | industrial | 1 | 5331.51 | 57388 | GIA | 277500 | WESTGATE 33/11KV | inside-area | 3.09 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 82 | 8.47 | 373 | 16 | 757892 | SPN-S000000343772 | 1000 | 700 | 60-80% | MANSTON 33/11KV | 326 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3474 | 1.3268 | SPN-S000000008510 | 14531596000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
561 | 48.8 | UNITS S T & W, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 5316.2 | 57223 | GIA | 397500 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 82 | 8.45 | 133 | 38 | 1873893 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065015 | B8 Storage or Distribution | 1381 | C | Other | 3 |  | Unconditioned | 2021-05-06 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 14434684000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
562 | 48.8 | UNITS 1 & 2, SOUTHERN CROSS, LONDON ROAD | SWANLEY | BR8 8DE | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 5231.23 | 56308 | GIA | 645000 | SWANLEY 33/11KV | inside-area | 2.63 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 84 | 8.31 | 131 | 18 | 1016345 | SPN-S000000316174 | 500 | 350 | 60-80% | SWANLEY 33/11KV | 212 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3904 | 0.18925 | SPN-S000000008528 | 9243176000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
563 | 48.8 | 14-20, ELDON WAY | TONBRIDGE | TN12 6BE | Tunbridge Wells |  | Factory And Premises; Warehouse And Premises | industrial | 3 | 5063.49 | 54503 | GIA | 509000 | PADDOCK WOOD 33/11KV | inside-area | 0.93 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 86 | 8.05 | 304 | 38 | 1876613 | SPN-S000000441277 | 800 | 400 | 40-60% | PADDOCK WOOD 33/11KV | 160 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062545697 | Storage or Distribution | 994 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-10-09 |  | 1 | FALSE | 51.1836 | 0.38368 | SPN-S000000008454 | 145329148;185441148;395799148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
564 | 48.8 | THE LOOP, MANSTON PARK | RAMSGATE | CT12 5DE | Thanet | COHLINE UK LTD | Factory And Premises | industrial | 1 | 4993.5 | 53750 | GIA | 302500 | WESTGATE 33/11KV | inside-area | 2.66 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 88 | 7.94 | 300 | 16 | 761530 | SPN-S000000343772 | 1000 | 700 | 60-80% | MANSTON 33/11KV | 221 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10022965711 | B2 to B7 General Industrial and Special Industrial Groups | 1574 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-04-30 |  | 1 | FALSE | 51.3512 | 1.3276 | SPN-S000000008510 | 6293021000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
565 | 48.8 | UNITS V X AND Y, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 4939.39 | 53167 | GIA | 340000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 89 | 7.85 | 123 | 38 | 1877949 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008665039 | Storage or Distribution | 1115 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-01-15 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 11323874000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
566 | 48.8 | UNIT 1A, THE INTERCHANGE, WESTED LANE | SWANLEY | BR8 8TE | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 4487.56 | 48304 | GIA | 505000 | SWANLEY 33/11KV | inside-area | 2.93 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 97 | 7.13 | 112 | 18 | 1024349 | SPN-S000000314549 | 800 | 560 | 60-80% | SWANLEY 33/11KV | 85 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013771972 | Storage or Distribution | 4801 | D | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2025-04-14 |  | 1 | FALSE | 51.3862 | 0.18913 | SPN-S000000008528 | 6449908000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
567 | 48.8 | UNITS G H I AND K, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 4061.65 | 43719 | GIA | 300000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 6.45 | 102 | 38 | 1887397 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065004 | Storage or Distribution | 1682 | G | Oil | 3 |  | Heating and Natural Ventilation | 2025-04-17 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 14609571000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
568 | 48.8 | UNITS R & U AND UNITS M & O, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 4010.42 | 43168 | GIA | 310000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 6.37 | 100 | 38 | 1887948 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065016 | B8 Storage or Distribution | 1265 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-05-21 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 14340511000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
569 | 48.8 | 29A & R/O 31, MAIDSTONE ROAD | TONBRIDGE | TN12 6DR | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 3967.2 | 42703 | GIA | 246000 | PADDOCK WOOD 33/11KV | inside-area | 0.95 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 6.3 | 99 | 38 | 1888413 | SPN-S000000442222 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 84 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1857 | 0.38874 | SPN-S000000008454 | 5159598000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
570 | 48.8 | SOUTHSIDE, HENLEY ROAD | TONBRIDGE | TN12 6DQ | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 3598.86 | 38738 | GIA | 241000 | PADDOCK WOOD 33/11KV | inside-area | 0.7 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 5.72 | 90 | 38 | 1892378 | SPN-S000000442222 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 167 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024137616 | General Industrial and Special Industrial Groups | 3294 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-01-06 |  | 0.5 | FALSE | 51.1835 | 0.38948 | SPN-S000000008454 | 3463936000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
571 | 48.8 | UNIT A, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 3327.83 | 35820 | GIA | 270000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 5.29 | 83 | 38 | 1895296 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008665035 | Storage or Distribution | 3350 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2025-04-13 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 7876446000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
572 | 48.8 | UNITS 3 AND 4 THE HANGAR, THE LOOP, MANSTON PARK | RAMSGATE | CT12 5DE | Thanet |  | Warehouse And Premises | industrial | 2 | 3316.41 | 35698 | GIA | 124000 | WESTGATE 33/11KV | inside-area | 2.66 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 5.27 | 83 | 16 | 779582 | SPN-S000000343772 | 1000 | 700 | 60-80% | MANSTON 33/11KV | 221 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10022965711 | B2 to B7 General Industrial and Special Industrial Groups | 1574 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-04-30 |  | 0.75 | FALSE | 51.3512 | 1.3276 | SPN-S000000008510 | 10850173000;13529427000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
573 | 48.8 | NORMAN COLLETT HOUSE & PROGRESSIVE HOUSE, TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 3258.16 | 35071 | GIA | 310000 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 5.18 | 81 | 38 | 1896045 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000068208 | B8 Storage or Distribution | 2093 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2013-04-12 |  | 1 | FALSE | 51.1857 | 0.39037 | SPN-S000000008454 | 10671969000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
574 | 48.8 | UNIT 2 AND 3, ORCHARD BUSINESS PARK, BADSELL ROAD | TONBRIDGE | TN12 6QU | Tunbridge Wells |  | Warehouse And Premises | industrial | 2 | 3092.38 | 33286 | GIA | 232000 | PADDOCK WOOD 33/11KV | inside-area | 1.99 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 4.91 | 77 | 38 | 1897830 | SPN-S000000451461 | 315 | 220 | 60-80% | PADDOCK WOOD 33/11KV | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062545632 | B8 Storage or Distribution | 1565 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-04-04 |  | 1 | FALSE | 51.1795 | 0.36431 | SPN-S000000008454 | 11432933000;11432929000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
575 | 48.8 | ALEXANDRA SECURITY PRODUCTS, WHETSTED ROAD | TONBRIDGE | TN12 6RT | Maidstone |  | Workshop And Premises | industrial | 1 | 2964.36 | 31908 | GIA | 156000 | PADDOCK WOOD 33/11KV | inside-area | 2.32 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 4.71 | 133 | 38 | 1899208 | SPN-R000000845408-000-015Z | 50 | 25 | 40-60% | PADDOCK WOOD 33/11KV | 155 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1858 | 0.36217 | SPN-S000000008454 | 5186205000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
576 | 48.8 | UNITS 1D-1E AND UNITS 2-3, MARK WAY | SWANLEY | BR8 8NJ | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 2858.63 | 30770 | GIA | 355000 | SWANLEY 33/11KV | inside-area | 2.71 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 4.54 | 71 | 18 | 1041883 | SPN-S000000316174 | 500 | 350 | 60-80% | SWANLEY 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013772464 | B8 Storage or Distribution | 592 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2015-11-20 |  | 1 | FALSE | 51.3881 | 0.18775 | SPN-S000000008528 | 12330403000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
577 | 48.8 | UNITS R & U, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 2845.39 | 30627 | GIA | 223000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 4.52 | 71 | 38 | 1900489 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065016 | B8 Storage or Distribution | 1265 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-05-21 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 15120733000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
578 | 48.8 | UNITS 2A AND 2B SAPPHIRE HOUSE, SAPPHIRE WAY | RAMSGATE | CT12 5FE | Thanet |  | Warehouse, Office And Premises | industrial | 1 | 2805.58 | 30199 | GIA | 171000 | WESTGATE 33/11KV | inside-area | 3.09 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 4.46 | 196 | 16 | 785081 | SPN-S000000343772 | 1000 | 700 | 60-80% | MANSTON 33/11KV | 326 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10022966495 | B2 to B7 General Industrial and Special Industrial Groups | 4870 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-08-23 |  | 0.5 | FALSE | 51.3474 | 1.3268 | SPN-S000000008510 | 9530790000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
579 | 48.8 | AREA A HANGAR 1, KENT INTERNATIONAL AIRPORT | RAMSGATE | CT12 5BL | Thanet |  | Workshop And Premises | industrial | 1 | 2659.49 | 28626 | GIA | 67000 | WESTGATE 33/11KV | inside-area | 4.05 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 4.23 | 120 | 16 | 786654 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10022966017 | B2 to B7 General Industrial and Special Industrial Groups | 5309 | G | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-04-29 |  | 0.83 | FALSE | 51.3451 | 1.3571 | SPN-S000000008510 | 9833759000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
580 | 48.8 | AREA B2 HANGAR 1, KENT INTERNATIONAL AIRPORT | RAMSGATE | CT12 5BL | Thanet |  | Warehouse And Premises | industrial | 1 | 2484.6 | 26744 | GIA | 96500 | WESTGATE 33/11KV | inside-area | 4.05 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 3.95 | 62 | 16 | 788536 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10022966017 | B2 to B7 General Industrial and Special Industrial Groups | 5309 | G | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-04-29 |  | 0.83 | FALSE | 51.3451 | 1.3571 | SPN-S000000008510 | 9976356000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
581 | 48.8 | VIKING FIREWORKS LTD, THE LOOP, MANSTON BUSINESS PARK | RAMSGATE | CT12 5DE | Thanet |  | Factory And Premises | industrial | 1 | 2316.9 | 24939 | OTH | 26000 | WESTGATE 33/11KV | inside-area | 2.66 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 3.68 | 139 | 16 | 790341 | SPN-S000000343772 | 1000 | 700 | 60-80% | MANSTON 33/11KV | 221 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10022965711 | B2 to B7 General Industrial and Special Industrial Groups | 1574 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-04-30 |  | 0.5 | FALSE | 51.3512 | 1.3276 | SPN-S000000008510 | 9300978000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
582 | 48.8 | 1 GATEWAY TRADING ESTATE, LONDON ROAD | SWANLEY | BR8 8GA | Sevenoaks |  | Warehouse And Premises | industrial | 2 | 2273.1 | 24467 | GIA | 323000 | SWANLEY 33/11KV | inside-area | 2.75 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.61 | 57 | 18 | 1048186 | SPN-S000000316174 | 500 | 350 | 60-80% | SWANLEY 33/11KV | 235 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035182142 | Storage or Distribution | 1251 | C | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2025-01-09 |  | 1 | FALSE | 51.39 | 0.19091 | SPN-S000000008528 | 11188084000;14440793000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
583 | 48.8 | UNIT B & PT 1ST FLR C, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 2149 | 23132 | GIA | 175000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.42 | 54 | 38 | 1907984 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065003 | Storage or Distribution | 2023 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-13 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 411067148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
584 | 48.8 | UNIT D, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Storage Depot And Premises | industrial | 1 | 2089.5 | 22491 | GIA | 167000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.32 | 52 | 38 | 1908625 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024135365 | Storage or Distribution | 2210 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-13 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 5391202000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
585 | 48.8 | UNIT C, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 2044.92 | 22011 | GIA | 162000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.25 | 51 | 38 | 1909105 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065003 | Storage or Distribution | 2023 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-13 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 5458488000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
586 | 48.8 | AREAS 1 & 2 UNIT 12, THE PACK HOUSE, WANTSUM WAY | BIRCHINGTON | CT7 0NE | Thanet |  | Warehouse And Premises | industrial | 1 | 2006.19 | 21594 | GIA | 53500 | WESTGATE 33/11KV | inside-area | 5.71 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 3.19 | 50 | 16 | 793686 | SPN-R000000851008-000-100Z | 200 | 180 | 80-100% | WESTGATE 33/11KV | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3576 | 1.2467 | SPN-S000000008510 | 14167726000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
587 | 48.8 | THREE TAX FARM, OLD HAY | TONBRIDGE | TN12 7DG | Tunbridge Wells |  | Factory And Premises | industrial | 1 | 1995.18 | 21476 | GIA | 110000 | PADDOCK WOOD 33/11KV | inside-area | 2.43 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.17 | 120 | 38 | 1909640 | SPN-S000000451303 | 100 | 10 | 0-20% | PADDOCK WOOD 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1705 | 0.42577 | SPN-S000000008454 | 188896148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
588 | 48.8 | UNIT 6, MARK WAY | SWANLEY | BR8 8NJ | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1989.63 | 21416 | GIA | 162000 | SWANLEY 33/11KV | inside-area | 2.71 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.16 | 50 | 18 | 1051237 | SPN-S000000316174 | 500 | 350 | 60-80% | SWANLEY 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062276799 | Storage or Distribution | 1877 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-07-27 |  | 1 | FALSE | 51.3881 | 0.18775 | SPN-S000000008528 | 8095787000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
589 | 48.8 | UNIT 1 WATSON YARD | RAMSGATE | CT12 5HL | Thanet |  | Factory And Premises | industrial | 1 | 1934.9 | 20827 | GIA | 150000 | WESTGATE 33/11KV | inside-area | 2.73 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 3.07 | 116 | 16 | 794453 | SPN-S000000343511 | 800 | 560 | 60-80% | MANSTON 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10095804447 | General Industrial and Special Industrial Groups | 131 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-07-28 |  | 1 | FALSE | 51.3507 | 1.3202 | SPN-S000000008510 | 14371104000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
590 | 48.7 | WESTERHAM HEIGHTS GARDEN CENTRE, MAIN ROAD | WESTERHAM | TN16 2HW | Sevenoaks |  | Garden Centre And Premises | bigbox | 1 | 4485.83 | 48285 | NIA | 24250 | BIGGIN HILL 33/11KV | inside-area | 2.94 | Addington Grid | Beddington | Croydon Zone | 10.3 | primary | 10.3 | Green | 22.3 | 12 | Thermal | 0 | 0 | 5.5 | 0 | 7.5 | Addington Grid 33kV | 13.9 | GREEN | 0 |  | RED | 7 | 94.8 | 1 | 21.2 | 19.6 | Winter | 46.2264 | 9.8 | Green (Over 5% headroom) | 73440 | 100 | 7.13 | 404 | 0 | 0 | SPN-R000000832207-000-041Z | 100 | 50 | 40-60% | BIGGIN HILL 33/11KV | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Beddington (_J) | [20 empty] | 51.2951 | 0.054083 | SPN-S000000008322 | 14231663000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
591 | 48.5 | UNITS 19 AND 20, STIRLING PARK, LAKER ROAD | ROCHESTER | ME1 3QR | Medway |  | Warehouse And Premises | industrial | 6 | 7695.29 | 82831 | GIA | 873000 | MEDWAY 33/11KV | inside-area | 2.83 | Medway Grid | Kingsnorth | Mid Kent Zone | 6.4 | primary | 6.4 | Green | 22.8 | 16.5 | Thermal | 0 | 0 | 0 | 0 | -2.4 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 21.9 | 16.6 | Winter | 27.8539 | 6.1 | Green (Over 5% headroom) | 45633 | 55 | 12.23 | 192 | 4 | 223329 | SPN-S000000316796 | 800 | 720 | 80-100% | MEDWAY 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44042002 | General Industrial and Special Industrial Groups | 634 | B | Natural Gas | 3 | 1 | Air Conditioning | 2025-04-30 |  | 1 | FALSE | 51.3579 | 0.50025 | SPN-S000000008333 | 15087656000;7326964000;5444585000;5844558000;10594564000;10594555000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
592 | 48.4 | UNIT 1, TON BUSINESS PARK 2-8, MORLEY ROAD | TONBRIDGE | TN9 1RA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 4 | 9489.62 | 102145 | GIA | 713000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.68 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 44 | 15.08 | 237 | 23 | 840599 | SPN-S000000443812 | 500 | 250 | 40-60% | TONBRIDGE EAST 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062629009 | B8 Storage or Distribution | 201 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2018-02-12 |  | 1 | FALSE | 51.1923 | 0.28315 | SPN-S000000008503 | 11403063000;11434395000;11158876000;11158872000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
593 | 48.4 | 20, VALE RISE | TONBRIDGE | TN9 1TB | Tonbridge & Malling | TONBRIDGE HEAD POST OFFICE | Storage Depot And Premises | industrial | 1 | 8745.5 | 94136 | GIA | 610000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.75 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 48 | 13.9 | 219 | 23 | 848608 | SPN-S000000443043 | 800 | 720 | 80-100% | TONBRIDGE EAST 33/6.6KV | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1903 | 0.28924 | SPN-S000000008503 | 133929148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
594 | 48.4 | 3-7, MORLEY ROAD | TONBRIDGE | TN9 1RD | Tonbridge & Malling |  | Car Showroom And Premises; Warehouse And Premises | industrial | 2 | 5079.29 | 54673 | GIA | 519000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.67 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 82 | 8.07 | 457 | 23 | 888071 | SPN-S000000441514 | 300 | 90 | 20-40% | TONBRIDGE EAST 33/6.6KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062593914 | General Industrial and Special Industrial Groups | 3784 | A | Grid Supplied Electricity | 3 |  | Mixed-mode with Natural Ventilation | 2022-10-04 |  | 1 | FALSE | 51.1923 | 0.28358 | SPN-S000000008503 | 187688148;4966869000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
595 | 48.4 | 40, MORLEY ROAD | TONBRIDGE | TN9 1RA | Tonbridge & Malling |  | Factory And Premises | industrial | 2 | 3960.18 | 42627 | GIA | 296000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.68 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 6.29 | 238 | 23 | 900117 | SPN-S000000443812 | 500 | 250 | 40-60% | TONBRIDGE EAST 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962163 | B2 to B7 General Industrial and Special Industrial Groups | 1704 | D | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2013-10-01 |  | 0.5 | FALSE | 51.1923 | 0.28315 | SPN-S000000008503 | 129587148;1860086000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
596 | 48.4 | 400, VALE ROAD | TONBRIDGE | TN9 1SW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3680.31 | 39614 | GIA | 226000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.35 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 5.85 | 92 | 23 | 903130 | SPN-S000000443659 | 800 | 400 | 40-60% | TONBRIDGE EAST 33/6.6KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062594020 | Storage or Distribution | 4032 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2023-01-28 |  | 1 | FALSE | 51.1944 | 0.28726 | SPN-S000000008503 | 187804148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
597 | 48.4 | 2B 3A 3B & 4C-6A, MUNDAY WORKS, MORLEY ROAD | TONBRIDGE | TN9 1RA | Tonbridge & Malling |  | Factory And Premises | industrial | 1 | 3147.52 | 33880 | GIA | 202000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.68 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 5 | 189 | 23 | 908864 | SPN-S000000443812 | 500 | 250 | 40-60% | TONBRIDGE EAST 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013921803 | B2 to B7 General Industrial and Special Industrial Groups | 318 | F | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-11-07 |  | 1 | FALSE | 51.1923 | 0.28315 | SPN-S000000008503 | 8600208000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
598 | 48.4 | 17-19, SOVEREIGN WAY | TONBRIDGE | TN9 1RG | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 3064.24 | 32983 | GIA | 254500 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.81 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 4.87 | 77 | 23 | 909761 | SPN-S000000441164 | 500 | 250 | 40-60% | TONBRIDGE TOWN 33/6.6KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002917832 | Retail/Financial and Professional Services | 4591 | C | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2026-02-03 |  | 0.5 | FALSE | 51.1942 | 0.27579 | SPN-S000000008503 | 15087078000;10380446000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
599 | 48.4 | SANDERSON WAY | TONBRIDGE | TN9 1QG | Tonbridge & Malling | S & S SERVICES LTD | Warehouse And Premises | industrial | 1 | 2726.07 | 29343 | GIA | 225000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.26 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 4.33 | 68 | 23 | 913401 | SPN-S000000443407 | 500 | 350 | 60-80% | TONBRIDGE EAST 33/6.6KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062593835 | B8 Storage or Distribution | 180 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2014-03-26 |  | 1 | FALSE | 51.1946 | 0.29078 | SPN-S000000008503 | 333434148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
600 | 48.4 | COMMOTION HOUSE, MORLEY ROAD | TONBRIDGE | TN9 1RA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2191.96 | 23594 | GIA | 162000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.68 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 3.48 | 55 | 23 | 919150 | SPN-S000000443812 | 500 | 250 | 40-60% | TONBRIDGE EAST 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962163 | B2 to B7 General Industrial and Special Industrial Groups | 1704 | D | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2013-10-01 |  | 1 | FALSE | 51.1923 | 0.28315 | SPN-S000000008503 | 10803652000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
601 | 48.4 | POSTERN INDUSTRIAL ESTATE 420-422, VALE ROAD | TONBRIDGE | TN9 1SW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1982.03 | 21334 | GIA | 132000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.35 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 3.15 | 50 | 23 | 921410 | SPN-S000000443659 | 800 | 400 | 40-60% | TONBRIDGE EAST 33/6.6KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962083 | B8 Storage or Distribution | 723 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-03-13 |  | 0.67 | FALSE | 51.1944 | 0.28726 | SPN-S000000008503 | 2421332000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
602 | 48.3 | H S JACKSON & SON LTD, LYMBRIDGE GREEN | ASHFORD | TN25 6BJ | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 6236.38 | 67128 | GIA | 460000 | STANFORD 33/11KV | inside-area | 5.18 | Sellindge Grid | Sellindge | East Kent Zone | 6.2 | primary | 6.2 | Green | 15.1 | 8.8 | Thermal | 5 | 7 | 5 | 12 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.6 | 11.2 | Winter | 41.7808 | 6.1 | Green (Over 5% headroom) | 44207 | 66 | 9.91 | 281 | 4 | 83762 | SPN-S000000363354 | 100 | 30 | 20-40% | STANFORD 33/11KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1547 | 1.0391 | SPN-S000000008492 | 11044022000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
603 | 48.3 | MOTORWAY MAINTENANCE COMPOUND ADJ M20 INTERCHANGE | HYTHE | CT21 4EU | Folkestone & Hythe |  | Depot And Premises | industrial | 1 | 2064.87 | 22226 | GIA | 126000 | STANFORD 33/11KV | inside-area | 1.49 | Sellindge Grid | Sellindge | East Kent Zone | 6.2 | primary | 6.2 | Green | 15.1 | 8.8 | Thermal | 5 | 7 | 5 | 12 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.6 | 11.2 | Winter | 41.7808 | 6.1 | Green (Over 5% headroom) | 44207 | 100 | 3.28 | 52 | 4 | 128664 | SPN-R000000849208-000-001Z | 100 | 50 | 40-60% | STANFORD 33/11KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1088 | 1.0636 | SPN-S000000008492 | 926808000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
604 | 48.2 | PHINIA DELPHI UK LTD, COURTENEY ROAD | GILLINGHAM | ME8 0RY | Medway |  | Factory And Premises | industrial | 1 | 45489.26 | 489642 | GIA | 1310000 | RAINHAM MARK 33/11KV | inside-area | 0.33 | Chatham Grid | Kingsnorth | Mid Kent Zone | 19.3 | primary | 19.3 | Green | 48 | 20.6 | Thermal | 0 | 4.3 | 0 | 4.3 | 20.4 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | Green (Over 5% headroom) | 137611 | 28 | 72.29 | 2729 | 37 | 1898603 | SPN-S000000311994 | 750 | 675 | 80-100% | RAINHAM MARK 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3653 | 0.58125 | SPN-S000000008525 | 14873327000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
605 | 48 | UNIT 5 HORSMONDEN STORAGE, GOUDHURST ROAD | TONBRIDGE | TN12 8AY | Tunbridge Wells |  | Warehouse And Premises | industrial | 2 | 7768.4 | 83618 | GIA | 452500 | GOUDHURST 33/11KV | inside-area | 3.22 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 51 | 12.34 | 194 | 6 | 108382 | SPN-S000000441072 | 200 | 100 | 40-60% | GOUDHURST 33/11KV | 231 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1358 | 0.44081 | SPN-S000000008360 | 10912556000;10912551000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
606 | 48 | CHAROLAIS HOUSE, MAYNARDS FARM, LAMBERHURST QUARTER | TUNBRIDGE WELLS | TN3 8AL | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 3309.28 | 35621 | GIA | 70000 | GOUDHURST 33/11KV | inside-area | 5.87 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 100 | 5.26 | 83 | 6 | 156379 | SPN-R000000836013-000-020Z | 100 | 70 | 60-80% | GOUDHURST 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1157 | 0.38624 | SPN-S000000008360 | 8104415000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
607 | 47.9 | UNIT 1, WESTWOOD GATEWAY, MARGATE ROAD | BROADSTAIRS | CT10 2QU | Thanet |  | Retail Warehouse And Premises | bigbox | 1 | 6336.4 | 68204 | GIA | 700000 | THANET 33/11KV | inside-area | 0.69 | Thanet Grid | Richborough | East Kent Zone | 9.7 | primary | 9.7 | Green | 26 | 12.9 | Thermal | 1 | 2.1 | 0 | 3.1 | 8.7 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | Green (Over 5% headroom) | 69162 | 100 | 10.07 | 570 | 5 | 162076 | SPN-S000000343536 | 800 | 560 | 60-80% | THANET 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3621 | 1.3932 | SPN-S000000008349 | 10998597000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
608 | 47.9 | UNIT LB1 19, WESTWOOD CROSS, MARGATE ROAD | BROADSTAIRS | CT10 2BF | Thanet |  | Bowling Alley And Premises | bigbox | 1 | 2502.82 | 26940 | GIA | 206000 | THANET 33/11KV | inside-area | 0.95 | Thanet Grid | Richborough | East Kent Zone | 9.7 | primary | 9.7 | Green | 26 | 12.9 | Thermal | 1 | 2.1 | 0 | 3.1 | 8.7 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | Green (Over 5% headroom) | 69162 | 100 | 3.98 | 200 | 5 | 203340 | SPN-S000000343469 | 1000 | 700 | 60-80% | THANET 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10012958668 | A1/A2 Retail and Financial/Professional services | 399 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2021-11-15 |  | 1 | FALSE | 51.3596 | 1.3926 | SPN-S000000008349 | 14884935000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
609 | 47.9 | 3A, WESTWOOD CROSS, MARGATE ROAD | BROADSTAIRS | CT10 2BF | Thanet |  | Leisure Centre And Premises | bigbox | 1 | 2016.4 | 21704 | GIA | 96500 | THANET 33/11KV | inside-area | 0.95 | Thanet Grid | Richborough | East Kent Zone | 9.7 | primary | 9.7 | Green | 26 | 12.9 | Thermal | 1 | 2.1 | 0 | 3.1 | 8.7 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | Green (Over 5% headroom) | 69162 | 100 | 3.2 | 161 | 5 | 208576 | SPN-S000000343469 | 1000 | 700 | 60-80% | THANET 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3596 | 1.3926 | SPN-S000000008349 | 14538638000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
610 | 47.5 | DARTFORD FREIGHT TERMINAL, EDISON PARK, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QJ | Dartford | DAVIES TURNER | Warehouse And Premises | industrial | 1 | 23105.6 | 248706 | GIA | 1790000 | CROSSWAYS | inside-area | 0.94 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 38 | 36.72 | 578 | 35 | 5670595 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 227 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4584 | 0.25711 | SPN-S000000008626 | 398874147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
611 | 47.5 | BRIDGE PLACE, ANCHOR BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6SN | Dartford |  | Offices And Premises | office | 1 | 12563.24 | 135229 | NIA | 2280000 | CROSSWAYS | inside-area | 0.55 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 69 | 19.96 | 879 | 35 | 5784072 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 205 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002021664 | Offices and Workshop Businesses | 6670 | C | Natural Gas | 4 | 2 | Mixed-mode with Mechanical Ventilation | 2023-07-20 |  | 1 | FALSE | 51.4553 | 0.2543 | SPN-S000000008626 | 2847605000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
612 | 47.5 | GND-1ST FLR RADIUS HOUSE, ANCHOR BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QH | Dartford |  | Offices And Premises | office | 1 | 2380.8 | 25627 | NIA | 505000 | CROSSWAYS | inside-area | 0.37 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 3.78 | 167 | 35 | 5893674 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 124 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000544252 | B1 Offices and Workshop businesses | 5490 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2021-11-12 |  | 1 | FALSE | 51.4541 | 0.25254 | SPN-S000000008626 | 12987758000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
613 | 47.5 | UNIT CP25, VICTORY WAY, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6DT | Dartford |  | Offices And Premises | office | 1 | 2377.3 | 25589 | NIA | 472500 | CROSSWAYS | inside-area | 0.46 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 3.78 | 166 | 35 | 5893712 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10023438169 | B1 Offices and Workshop businesses | 2541 | B | Natural Gas | 4 | 2 | Air Conditioning | 2021-05-05 |  | 1 | FALSE | 51.4554 | 0.25074 | SPN-S000000008626 | 9653996000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
614 | 47.5 | CP45, VICTORY WAY, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6DT | Dartford |  | Warehouse And Premises | industrial | 1 | 1378.26 | 14835 | GIA | 220000 | CROSSWAYS | inside-area | 0.46 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 2.19 | 34 | 35 | 5904466 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10023438167 | Offices and Workshop Businesses | 1347 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2022-10-03 |  | 1 | FALSE | 51.4554 | 0.25074 | SPN-S000000008626 | 14009393000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
615 | 47.5 | UNIT 2A, GALLEON BOULEVARD, NEWTONS COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QL | Dartford |  | Warehouse And Premises | industrial | 1 | 1376.2 | 14813 | GIA | 205000 | CROSSWAYS | inside-area | 0.52 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 2.19 | 34 | 35 | 5904488 | SPN-S000000311176 | 1000 | 500 | 40-60% | CROSSWAYS | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4535 | 0.25646 | SPN-S000000008626 | 393349147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
616 | 47.5 | UNIT B, BRIDGE CLOSE, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Warehouse And Premises | industrial | 1 | 1265 | 13616 | GIA | 179000 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 2.01 | 32 | 35 | 5905685 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094156148 | B8 Storage or Distribution | 1263 | A | Natural Gas | 4 |  | Heating and Natural Ventilation | 2020-09-14 |  | 1 | FALSE | 51.4606 | 0.25638 | SPN-S000000008626 | 13461596000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
617 | 47.5 | UNIT F, BRIDGE CLOSE, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QP | Dartford |  | Warehouse And Premises | industrial | 1 | 1177.29 | 12672 | GIA | 155000 | CROSSWAYS | inside-area | 1.13 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 1.87 | 29 | 35 | 5906629 | SPN-S000000324374 | 800 | 560 | 60-80% | CROSSWAYS | 397 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094156152 | B8 Storage or Distribution | 1196 | A | Natural Gas | 4 |  | Heating and Natural Ventilation | 2020-09-14 |  | 1 | FALSE | 51.4606 | 0.25638 | SPN-S000000008626 | 13510893000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
618 | 47.5 | VOYAGER HOUSE, CAPSTAN COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QG | Dartford |  | Warehouse And Premises | industrial | 1 | 1065.61 | 11470 | GIA | 171000 | CROSSWAYS | inside-area | 0.26 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 1.69 | 27 | 35 | 5907831 | SPN-S000000316824 | 1000 | 100 | 0-20% | CROSSWAYS | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.453 | 0.2473 | SPN-S000000008626 | 2579728000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
619 | 47.5 | UNIT 16 AND 17, SCHOONER PARK, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6NW | Dartford |  | Warehouse And Premises | industrial | 1 | 1060.44 | 11414 | GIA | 185000 | CROSSWAYS | inside-area | 0.07 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 1.69 | 27 | 35 | 5907887 | SPN-S000000324354 | 1000 | 700 | 60-80% | CROSSWAYS | 59 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10023437835 | Offices and Workshop Businesses | 820 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2023-06-08 |  | 0.75 | FALSE | 51.4518 | 0.25033 | SPN-S000000008626 | 9128214000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
620 | 47.5 | C3, CHARLES PARK, CROSSWAYS BUSINESS PARK | DARTFORD | DA9 9BT | Dartford |  | Warehouse And Premises | industrial | 1 | 4504.66 | 48488 | GIA | 635000 | SWANSCOMBE 33/11KV | inside-area | 1.93 | Dartford Grid 33kV | Littlebrook | West Kent Zone | 5.6 | primary | 5.6 | Green | 13 | 6.4 | Thermal | 0 | 2.5 | 0 | 2.5 | 8.8 | Dartford Grid A 33kV | 64.9 | GREEN | 139 |  | RED | 2 | 21.5 | 0 | 13 | 9.9 | Winter | 50.7692 | 6.6 | Green (Over 5% headroom) | 39929 | 82 | 7.16 | 113 | 2 | 199069 | SPN-S000000311025 | 200 | 100 | 40-60% | SWANSCOMBE 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4525 | 0.27521 | SPN-S000000008522 | 3683896000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
621 | 47.5 | PT SWANSCOMBE WORKS, MANOR WAY | SWANSCOMBE | DA10 0LL | Dartford | BASIC ENGINEERING | Factory And Premises | industrial | 1 | 2459.2 | 26471 | GIA | 200000 | SWANSCOMBE 33/11KV | inside-area | 0.21 | Dartford Grid 33kV | Littlebrook | West Kent Zone | 5.6 | primary | 5.6 | Green | 13 | 6.4 | Thermal | 0 | 2.5 | 0 | 2.5 | 8.8 | Dartford Grid A 33kV | 64.9 | GREEN | 139 |  | RED | 2 | 21.5 | 0 | 13 | 9.9 | Winter | 50.7692 | 6.6 | Green (Over 5% headroom) | 39929 | 100 | 3.91 | 148 | 2 | 221086 | SPN-S000000313695 | 500 | 350 | 60-80% | SWANSCOMBE 33/11KV | 259 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4514 | 0.30061 | SPN-S000000008522 | 3799590000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
622 | 47.4 | 63, STATION ROAD | DARTFORD | DA3 7QA | Dartford | WAITROSE SUPERMARKET | Superstore And Premises | bigbox | 1 | 2581.6 | 27788 | GIA | 445000 | LONGFIELD 33/11KV | inside-area | 0.33 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 23 | 10 | Thermal | 0 | 0 | 0 | 0 | 13.3 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23 | 17.1 | Summer | 56.1404 | 9.6 | Green (Over 5% headroom) | 66310 | 100 | 4.1 | 232 | 1 | 58876 | SPN-S000000314222 | 800 | 400 | 40-60% | LONGFIELD 33/11KV | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000538080 | Retail/Financial and Professional Services | 2520 | C | Natural Gas | 5 | 2 | Air Conditioning | 2023-10-02 |  | 1 | FALSE | 51.3964 | 0.30073 | SPN-S000000008656 | 390100147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
623 | 47.4 | DISCOUNT BUILDERS MERCHANTS, LOWER ROAD | GRAVESEND | DA11 9BG | Gravesham |  | Builders Merchants And Premises | bigbox | 1 | 2484.37 | 26742 | GIA | 287500 | GRAVESEND WEST 33/11KV | inside-area | 0.33 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 3.95 | 224 | 19 | 450899 | SPN-S000000312297 | 500 | 150 | 20-40% | GRAVESEND WEST 33/11KV | 188 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012013811 | General Industrial and Special Industrial Groups | 5695 | A+ | Grid Supplied Electricity | 5 |  | Air Conditioning | 2026-02-05 |  | 0.5 | FALSE | 51.4535 | 0.32085 | SPN-S000000008511 | 9256091000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
624 | 47.4 | SWALE MOTORS (GRAVESEND) LTD EAGLE WAY, STONEBRIDGE ROAD | GRAVESEND | DA11 9BJ | Gravesham |  | Car Showroom And Premises | bigbox | 1 | 2272.1 | 24457 | GIA | 395000 | GRAVESEND WEST 33/11KV | inside-area | 0.19 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 3.61 | 204 | 19 | 453184 | SPN-S000000316830 | 500 | 150 | 20-40% | GRAVESEND WEST 33/11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4489 | 0.32136 | SPN-S000000008511 | 11721167000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
625 | 47.3 | UNITS 2-3 ABBEY WORKS, WHITEWAY ROAD | QUEENBOROUGH | ME11 5EJ | Swale |  | Workshop And Premises | industrial | 1 | 1846.31 | 19873 | GIA | 90000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.59 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 2.93 | 83 | 15 | 1120179 | SPN-S000000393585 | 315 | 220 | 60-80% | QUEENBOROUGH 33/6.6KV | 46 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4182 | 0.74263 | SPN-S000000008368 | 7776773000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
626 | 47.3 | BURO CONTRACTS, RUSHENDEN ROAD | QUEENBOROUGH | ME11 5HB | Swale |  | Warehouse And Premises | industrial | 1 | 1843.1 | 19839 | GIA | 79500 | QUEENBOROUGH 33/6.6KV | inside-area | 0.2 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 2.93 | 46 | 15 | 1120213 | SPN-S000000391561 | 300 | 90 | 20-40% | QUEENBOROUGH 33/6.6KV | 62 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4155 | 0.74772 | SPN-S000000008368 | 15142283000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
627 | 47.3 | TILE WORKS, BOROUGH ROAD | QUEENBOROUGH | ME11 5DN | Swale |  | Factory And Premises | industrial | 1 | 1597.24 | 17193 | GIA | 52000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.44 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 2.54 | 96 | 15 | 1122859 | SPN-S000000391560 | 500 | 150 | 20-40% | QUEENBOROUGH 33/6.6KV | 58 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062376904 | B1 Offices and Workshop businesses | 1740 | F | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-08-26 |  | 1 | FALSE | 51.4143 | 0.75368 | SPN-S000000008368 | 8620680000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
628 | 47.3 | 1, QUEENBOROUGH BUSINESS CENTRE, ARGENT ROAD | QUEENBOROUGH | ME11 5HZ | Swale |  | Workshop And Premises | industrial | 1 | 1512.46 | 16280 | GIA | 105000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.88 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 2.4 | 68 | 15 | 1123772 | SPN-S000000393967 | 500 | 350 | 60-80% | QUEENBOROUGH 33/6.6KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4059 | 0.74717 | SPN-S000000008368 | 336702147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
629 | 47.3 | 1-2 & 4, ELMLEY INDUSTRIAL ESTATE, ARGENT ROAD | QUEENBOROUGH | ME11 5GA | Swale |  | Workshop And Premises | industrial | 1 | 1270.5 | 13676 | GIA | 103000 | QUEENBOROUGH 33/6.6KV | inside-area | 1.05 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 2.02 | 57 | 15 | 1126376 | SPN-S000000393967 | 500 | 350 | 60-80% | QUEENBOROUGH 33/6.6KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4043 | 0.74882 | SPN-S000000008368 | 6021866000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
630 | 47.3 | UNIT 4 & 5, SHEET GLASS ROAD | QUEENBOROUGH | ME11 5JS | Swale |  | Warehouse And Premises | industrial | 1 | 1122.89 | 12087 | GIA | 90000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.77 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 100 | 1.78 | 28 | 15 | 1127965 | SPN-S000000393826 | 500 | 250 | 40-60% | QUEENBOROUGH 33/6.6KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023199095 | B2 to B7 General Industrial and Special Industrial Groups | 2621 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-03-31 |  | 0.75 | FALSE | 51.4071 | 0.75041 | SPN-S000000008368 | 13428093000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
631 | 47.1 | ALTON WIRE PRODUCTS LTD, PENNYPOT INDUSTRIAL ESTATE | HYTHE | CT21 6PE | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 1160.33 | 12490 | GIA | 54500 | HYTHE MAIN 33/11KV | inside-area | 2.11 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 1.84 | 70 | 7 | 194865 | SPN-S000000362229 | 500 | 350 | 60-80% | HYTHE MAIN 33/11KV | 46 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50013952 | B2 to B7 General Industrial and Special Industrial Groups | 1154 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-06-18 |  | 0.75 | FALSE | 51.0678 | 1.0639 | SPN-S000000008421 | 7329977000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
632 | 47.1 | STEEL COMPONENTS LTD, PENNYPOT INDUSTRIAL ESTATE, PENNYPOT ENTRANCE ROAD | HYTHE | CT21 6PE | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 1043 | 11227 | GIA | 34750 | HYTHE MAIN 33/11KV | inside-area | 2.11 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 1.66 | 63 | 7 | 196128 | SPN-S000000362229 | 500 | 350 | 60-80% | HYTHE MAIN 33/11KV | 46 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0678 | 1.0639 | SPN-S000000008421 | 9923883000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
633 | 47.1 | STANFORD MOTORWAY MAINTENANCE | HYTHE | CT21 4UX | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1000.74 | 10772 | GIA | 51000 | HYTHE MAIN 33/11KV | inside-area | 3.69 | Folkestone Total | Sellindge | East Kent Zone | 12.8 | primary | 12.8 | Green | 24 | 11.5 | Thermal | 0 | 10 | 7.7 | 10 | 9.6 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | Green (Over 5% headroom) | 91266 | 100 | 1.59 | 25 | 7 | 196583 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0938 | 1.0518 | SPN-S000000008421 | 1138222000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
634 | 47.1 | 26-28, TRIBUNE DRIVE | SITTINGBOURNE | ME10 2PG | Swale |  | Factory And Premises; Warehouse And Premises | industrial | 4 | 8239.25 | 88686 | GIA | 465000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 43 | 13.09 | 494 | 31 | 2878923 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3522 | 0.73795 | SPN-S000000008585 | 8853395000;9673388000;9851184000;14022316000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
635 | 47.1 | PHEASANTS AUTOPOINT, SHEPPEY WAY | SITTINGBOURNE | ME9 8QX | Swale | BOBBING CAR BREAKERS | Breakers Yard Vehicle Repair Workshop And Premises | industrial | 1 | 7950 | 85573 | OTH | 71000 | GROVEHURST LOCAL | inside-area | 1.9 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 44 | 12.63 | 358 | 31 | 2882036 | SPN-R000000858503-000-005Z | 200 | 180 | 80-100% | GROVEHURST LOCAL | 192 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3657 | 0.7264 | SPN-S000000008585 | 392598147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
636 | 47.1 | UNIT 140 TRINITY TRADING ESTATE MILL WAY | SITTINGBOURNE | ME10 2PD | Swale |  | Warehouse And Premises | industrial | 1 | 4756.32 | 51197 | GIA | 427500 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 74 | 7.56 | 119 | 31 | 2916412 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3515 | 0.73965 | SPN-S000000008585 | 14586021000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
637 | 47.1 | POWAKADDY INTERNATIONAL LTD, CASTLE ROAD | SITTINGBOURNE | ME10 3SQ | Swale |  | Warehouse And Premises | industrial | 1 | 4224.49 | 45472 | GIA | 355000 | GROVEHURST LOCAL | inside-area | 1.5 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 83 | 6.71 | 106 | 31 | 2922137 | SPN-S000000394748 | 1000 | 700 | 60-80% | GROVEHURST LOCAL | 148 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3536 | 0.76237 | SPN-S000000008585 | 6336056000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
638 | 47.1 | SITTINGBOURNE LOGISTICS PARK, SWALE WAY | SITTINGBOURNE | ME10 2FF | Swale |  | Road Haulage Depot And Premises | industrial | 1 | 4113.52 | 44278 | GIA | 480000 | GROVEHURST LOCAL | inside-area | 1.18 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 85 | 6.54 | 103 | 31 | 2923331 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.37 | 0.73795 | SPN-S000000008585 | 9520096000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
639 | 47.1 | RTC EUROPE LTD, CASTLE ROAD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3FP | Swale |  | Factory And Premises | industrial | 1 | 3769.16 | 40571 | GIA | 312500 | GROVEHURST LOCAL | inside-area | 1.77 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 93 | 5.99 | 226 | 31 | 2927038 | SPN-S000000394748 | 1000 | 700 | 60-80% | GROVEHURST LOCAL | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3509 | 0.76121 | SPN-S000000008585 | 6701437000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
640 | 47.1 | UNITS A B & C AT FLO PLAST LTD, HOWT GREEN, SHEPPEY WAY | SITTINGBOURNE | ME9 8QU | Swale |  | Factory And Premises | industrial | 1 | 3600.97 | 38760 | GIA | 161000 | GROVEHURST LOCAL | inside-area | 1.8 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 97 | 5.72 | 216 | 31 | 2928849 | SPN-S000000394545 | 800 | 560 | 60-80% | GROVEHURST LOCAL | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3734 | 0.73069 | SPN-S000000008585 | 14573685000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
641 | 47.1 | 40-43, CHURCH ROAD BUSINESS CENTRE, CHURCH ROAD | SITTINGBOURNE | ME10 3RS | Swale | WASH VAC SERVICES | Factory And Premises; Warehouse And Premises | industrial | 2 | 3596.92 | 38717 | GIA | 238000 | GROVEHURST LOCAL | inside-area | 1.99 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 98 | 5.72 | 216 | 31 | 2928892 | SPN-S000000394048 | 300 | 30 | 0-20% | SITTINGBOURNE TOWN 33/11KV | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3482 | 0.75583 | SPN-S000000008585 | 7118190000;333247147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
642 | 47.1 | UNIT 2 EUROLINK GATEWAY, CASTLE ROAD | SITTINGBOURNE | ME10 3AG | Swale |  | Warehouse And Premises | industrial | 3 | 3484.39 | 37506 | GIA | 311000 | GROVEHURST LOCAL | inside-area | 1.72 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 5.54 | 87 | 31 | 2930103 | SPN-S000000394605 | 500 | 350 | 60-80% | SITTINGBOURNE TOWN 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002457070 | B2 to B7 General Industrial and Special Industrial Groups | 1578 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-05-13 |  | 1 | FALSE | 51.3507 | 0.75744 | SPN-S000000008585 | 5358236000;5507279000;13858941000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
643 | 47.1 | UNITS 56 & 57 TRINITY TRADE CENTRE, MILL WAY | SITTINGBOURNE | ME10 2PD | Swale |  | Workshop And Premises | industrial | 1 | 3256.56 | 35053 | GIA | 405000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 5.17 | 147 | 31 | 2932556 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023200880 | B8 Storage or Distribution | 509 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-03-13 |  | 1 | FALSE | 51.3515 | 0.73965 | SPN-S000000008585 | 8936113000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
644 | 47.1 | NORTHERN END 3-4 WAREHOUSE, RIDHAM DOCK | SITTINGBOURNE | ME9 8SR | Swale |  | Warehouse And Premises | industrial | 1 | 2632 | 28331 | GIA | 87000 | GROVEHURST LOCAL | inside-area | 1.65 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 4.18 | 66 | 31 | 2939278 | SPN-S000000394887 | 315 | 32 | 0-20% | GROVEHURST LOCAL | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3805 | 0.75903 | SPN-S000000008585 | 335720147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
645 | 47.1 | UNIT 9 AT 5, TRINITY TRADING ESTATE, TRIBUNE DRIVE | SITTINGBOURNE | ME10 2PG | Swale |  | Workshop And Premises | industrial | 1 | 2471.37 | 26602 | GIA | 141000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 3.93 | 111 | 31 | 2941007 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023201494 | B8 Storage or Distribution | 2585 | D | Natural Gas | 4 | 1 | Heating and Natural Ventilation | 2021-05-24 |  | 1 | FALSE | 51.3522 | 0.73795 | SPN-S000000008585 | 9459727000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
646 | 47.1 | UNIT 10 KEMSLEY FIELDS BUSINESS PARK, BARGE WAY | SITTINGBOURNE | ME10 2FE | Swale |  | Warehouse And Premises | industrial | 1 | 2118.1 | 22799 | GIA | 191000 | GROVEHURST LOCAL | inside-area | 0.55 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 3.37 | 53 | 31 | 2944810 | SPN-S000000394797 | 800 | 560 | 60-80% | GROVEHURST LOCAL | 115 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023200132 | B1 Offices and Workshop businesses | 1673 | C | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2012-09-30 |  | 1 | FALSE | 51.3666 | 0.74595 | SPN-S000000008585 | 8495235000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
647 | 47.1 | UNIT 50C, MILL WAY | SITTINGBOURNE | ME10 2PD | Swale |  | Warehouse And Premises | industrial | 1 | 1889.5 | 20338 | GIA | 181000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 3 | 47 | 31 | 2947271 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3515 | 0.73965 | SPN-S000000008585 | 8076713000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
648 | 46.8 | NORTHDOWN BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 2DL | Maidstone | J PERKINS DISTRIBUTION LTD | Warehouse And Premises | industrial | 1 | 2113.92 | 22754 | GIA | 140000 | HARRIETSHAM 33/11KV | inside-area | 1.64 | Ashford Grid | Sellindge | Mid Kent Zone | 5.1 | primary | 5.1 | Green | 16 | 10.9 | Thermal | 13.5 | 0 | 5.4 | 13.5 | 3.5 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | Green (Over 5% headroom) | 36364 | 100 | 3.36 | 53 | 5 | 1100679 | SPN-R000000841410-000-002Z | 315 | 284 | 80-100% | HARRIETSHAM 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200003720466 | B1 Offices and Workshop businesses | 2498 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-12-30 |  | 1 | FALSE | 51.236 | 0.73059 | SPN-S000000008414 | 2283997000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
649 | 46.7 | MONSON HOUSE, MONSON WAY | TUNBRIDGE WELLS | TN1 1LQ | Tunbridge Wells |  | Offices And Premises | office | 1 | 1630.7 | 17553 | NIA | 233000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.76 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 2.59 | 114 | 13 | 396503 | SPN-S000000441369 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS TOWN 132/6.6kV | 24 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062542156 | B1 Offices and Workshop businesses | 1794 | D | Grid Supplied Electricity | 4 | 3 | Air Conditioning | 2020-12-24 |  | 1 | FALSE | 51.1331 | 0.26489 | SPN-S000000009251 | 190418148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
650 | 46.7 | CANTERBURY CHRIST CHURCH UNIVERSITY LUCY FILDES BUILDING 1, MEADOW ROAD | TUNBRIDGE WELLS | TN1 2YG | Tunbridge Wells |  | Offices And Premises | office | 1 | 1362.7 | 14668 | NIA | 307500 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.52 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 2.17 | 95 | 13 | 399388 | SPN-S000000441477 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS TOWN 132/6.6kV | 46 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.136 | 0.26427 | SPN-S000000009251 | 12086254000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
651 | 46.7 | PLUTO HOUSE, VALE AVENUE | TUNBRIDGE WELLS | TN1 1DJ | Tunbridge Wells |  | Offices And Premises | office | 1 | 1284 | 13821 | NIA | 305000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 1.21 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 2.04 | 90 | 13 | 400235 | SPN-S000000443039 | 800 | 560 | 60-80% | TUNBRIDGE WELLS TOWN 132/6.6kV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.13 | 0.26089 | SPN-S000000009251 | 14503799000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
652 | 46.7 | TUNBRIDGE WELLS BOROUGH COUNCIL TOWN HALL, MOUNT PLEASANT ROAD | TUNBRIDGE WELLS | TN1 1RS | Tunbridge Wells |  | Offices And Premises | office | 1 | 1096.8 | 11806 | NIA | 140000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 1.74 | 77 | 13 | 402250 | SPN-S000000441369 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS TOWN 132/6.6kV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008660629 | B1 Offices and Workshop businesses | 5321 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2020-06-16 |  | 1 | FALSE | 51.1326 | 0.26395 | SPN-S000000009251 | 15098140000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
653 | 46.7 | 88, GROSVENOR ROAD | TUNBRIDGE WELLS | TN1 2AX | Tunbridge Wells |  | Offices And Premises | office | 1 | 1006.7 | 10836 | NIA | 145000 | TUNBRIDGE WELLS TOWN 132/6.6kV | inside-area | 0.58 | Tunbridge Wells Total | Northfleet | West Kent Zone | 17 | primary | 17 | Green | 39 | 20.3 | Thermal | 0 | 0 | 0 | 0 | 15.7 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 35.5 | 27.3 | Winter | 47.8873 | 17 | Green (Over 5% headroom) | 121212 | 100 | 1.6 | 70 | 13 | 403220 | SPN-S000000442322 | 500 | 50 | 0-20% | TUNBRIDGE WELLS TOWN 132/6.6kV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008660862 | B1 Offices and Workshop businesses | 316 | F | Natural Gas | 3 |  | Air Conditioning | 2012-04-25 |  | 1 | FALSE | 51.1371 | 0.26216 | SPN-S000000009251 | 894254000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
654 | 46.5 | ASDA GILLINGHAM PIER SUPERSTORE, PIER ROAD | GILLINGHAM | ME7 1RZ | Medway |  | Superstore And Premises | bigbox | 1 | 6549.45 | 70498 | GIA | 1550000 | CHATHAM HILL 33/11KV | inside-area | 2.16 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 87 | 10.41 | 589 | 25 | 1045244 | SPN-S000000311873 | 500 | 250 | 40-60% | CHATHAM HILL 33/11KV | 57 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3954 | 0.55286 | SPN-S000000008645 | 9943026000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
655 | 46.5 | KINGSTANDING WAY | TUNBRIDGE WELLS | TN2 3UP | Tunbridge Wells | BOOKER BELMONT WHOLESALE; JEWSON LTD | Builders Merchants And Premises; Warehouse And Premises | bigbox | 2 | 6038.7 | 65000 | GIA | 627500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.49 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 94 | 9.6 | 543 | 50 | 1757916 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000064080 | B1 Offices and Workshop businesses | 247 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-11-07 |  | 1 | FALSE | 51.1597 | 0.29559 | SPN-S000000008504 | 192110148;185522148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
656 | 46.5 | J SAINSBURY PLC, ANGEL CENTRE, ANGEL LANE | TONBRIDGE | TN9 1SF | Tonbridge & Malling |  | Superstore And Premises | bigbox | 1 | 5763.35 | 62036 | GIA | 1350000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.6 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 99 | 9.16 | 519 | 50 | 1760880 | SPN-S000000442102 | 500 | 50 | 0-20% | TONBRIDGE TOWN 33/6.6KV | 208 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000963088 | General Assembly and Leisure, Night Clubs, and Theatres | 3958 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-09-29 |  | 1 | FALSE | 51.1922 | 0.27486 | SPN-S000000008504 | 8786192000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
657 | 46.5 | AUDI, DOWDING WAY | TUNBRIDGE WELLS | TN2 3UY | Tunbridge Wells |  | Car Showroom And Premises | bigbox | 1 | 5266.29 | 56686 | GIA | 820000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.81 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 8.37 | 474 | 50 | 1766230 | SPN-S000000451043 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000069863 | A1/A2 Retail and Financial/Professional services | 1365 | C | Natural Gas | 3 |  | Air Conditioning | 2016-07-19 |  | 0.5 | FALSE | 51.1546 | 0.28361 | SPN-S000000008504 | 9396744000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
658 | 46.5 | HENDY, KINGSTANDING BUSINESS PARK, KINGSTANDING WAY | TUNBRIDGE WELLS | TN2 3UP | Tunbridge Wells |  | Car Showroom And Premises | bigbox | 1 | 5124.86 | 55163 | GIA | 845000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.49 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 8.14 | 461 | 50 | 1767753 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000064076 | Retail/Financial and Professional Services | 5036 | A | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2024-12-17 |  | 1 | FALSE | 51.1597 | 0.29559 | SPN-S000000008504 | 14968975000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
659 | 46.5 | UNIT 4, THE FOUNTAINS RETAIL PARK, DOWDING WAY | TUNBRIDGE WELLS | TN2 3FB | Tunbridge Wells |  | Retail Warehouse And Premises | bigbox | 1 | 4645 | 49998 | GIA | 1300000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.73 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 7.38 | 418 | 50 | 1772918 | SPN-S000000451514 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 119 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000069955 | A1/A2 Retail and Financial/Professional services | 2089 | B | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2021-05-10 |  | 0.75 | FALSE | 51.1559 | 0.28798 | SPN-S000000008504 | 7511010000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
660 | 46.5 | ASDA, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EY | Tunbridge Wells |  | Superstore And Premises | bigbox | 1 | 4185.25 | 45050 | GIA | 1250000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 6.65 | 377 | 50 | 1777866 | SPN-S000000443773 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554171 | Retail/Financial and Professional Services | 1037 | E | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2024-02-23 |  | 1 | FALSE | 51.1549 | 0.28851 | SPN-S000000008504 | 9019410000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
661 | 46.5 | ARDEN TUNBRIDGE WELLS LTD, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3UE | Tunbridge Wells |  | Car Showroom And Premises | bigbox | 1 | 3816.63 | 41082 | GIA | 705000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.78 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 6.07 | 343 | 50 | 1781834 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 312 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554333 | A1/A2 Retail and Financial/Professional services | 269 | D | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2021-10-06 |  | 1 | FALSE | 51.1566 | 0.29451 | SPN-S000000008504 | 13524292000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
662 | 46.5 | 169, PIER ROAD | GILLINGHAM | ME7 1TZ | Medway |  | Car Showroom And Premises | bigbox | 1 | 3534.8 | 38048 | GIA | 472500 | CHATHAM HILL 33/11KV | inside-area | 2.41 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 5.62 | 318 | 25 | 1077694 | SPN-S000000311915 | 500 | 250 | 40-60% | CHATHAM HILL 33/11KV | 253 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3954 | 0.56014 | SPN-S000000008645 | 76452147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
663 | 46.5 | 5, KNIGHTS WAY | TUNBRIDGE WELLS | TN2 3UW | Tunbridge Wells |  | Bowling Alley And Premises | bigbox | 1 | 2733 | 29418 | GIA | 222000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.17 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.34 | 219 | 50 | 1793498 | SPN-S000000454051 | 800 | 560 | 60-80% | TUNBRIDGE WELLS TOWN 11KV | 38 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1535 | 0.29698 | SPN-S000000008504 | 624822000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
664 | 46.5 | UNIT A, GREAT LODGE RETAIL PARK, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EW | Tunbridge Wells |  | Retail Warehouse And Premises | bigbox | 1 | 2626.82 | 28275 | GIA | 595000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.63 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.17 | 236 | 50 | 1794641 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 214 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000064987 | Retail/Financial and Professional Services | 2608 | B | Grid Supplied Electricity | 4 | 138 | Air Conditioning | 2024-03-14 |  | 0.8 | FALSE | 51.1578 | 0.29287 | SPN-S000000008504 | 10258274000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
665 | 46.5 | LAMBERTS ROAD | TUNBRIDGE WELLS | TN2 3EH | Tunbridge Wells | CAFFYNS PLC | Car Showroom And Premises | bigbox | 1 | 2589.76 | 27876 | GIA | 327500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.08 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 4.12 | 233 | 50 | 1795040 | SPN-S000000442092 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 18 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008663414 | A1/A2 Retail and Financial/Professional services | 434 | C | Oil | 3 |  | Heating and Natural Ventilation | 2017-05-14 |  | 1 | FALSE | 51.1523 | 0.28416 | SPN-S000000008504 | 184357148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
666 | 46.5 | WATERFRONT LEISURE, PIER ROAD | GILLINGHAM | ME7 1RP | Medway |  | Leisure Centre And Premises | bigbox | 1 | 2489.67 | 26799 | GIA | 148000 | CHATHAM HILL 33/11KV | inside-area | 2.19 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.96 | 199 | 25 | 1088943 | SPN-S000000324324 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 108 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.395 | 0.55535 | SPN-S000000008645 | 2610377000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
667 | 46.5 | FURNITURE VILLAGE, KINGSTANDING WAY | TUNBRIDGE WELLS | TN2 3UP | Tunbridge Wells |  | Retail Warehouse And Premises | bigbox | 1 | 2433.56 | 26195 | GIA | 640000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.49 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.87 | 219 | 50 | 1796721 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1597 | 0.29559 | SPN-S000000008504 | 383643148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
668 | 46.5 | UNIT 1, LONGFIELD TRADE PARK, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3XQ | Tunbridge Wells |  | Retail Warehouse And Premises | bigbox | 1 | 2412.23 | 25965 | GIA | 477500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.83 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.83 | 217 | 50 | 1796951 | SPN-S000000441845 | 500 | 150 | 20-40% | TUNBRIDGE WELLS GRID 132/11 | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1553 | 0.28986 | SPN-S000000008504 | 10454622000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
669 | 46.5 | MOTORLINE VOLKSWAGEN, DOWDING WAY | TUNBRIDGE WELLS | TN2 3UY | Tunbridge Wells |  | Car Showroom And Premises | bigbox | 1 | 2225.28 | 23953 | GIA | 375000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.81 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.54 | 200 | 50 | 1798963 | SPN-S000000451043 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000063187 | A1/A2 Retail and Financial/Professional services | 2189 | C | Natural Gas | 3 |  | Air Conditioning | 2017-09-21 |  | 1 | FALSE | 51.1546 | 0.28361 | SPN-S000000008504 | 4773920000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
670 | 46.5 | DOWDING WAY | TUNBRIDGE WELLS | TN2 3DS | Tunbridge Wells | DRAKE & FLETCHER LTD | Car Showroom And Premises | bigbox | 1 | 2170.01 | 23358 | GIA | 405000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.72 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.45 | 195 | 50 | 1799558 | SPN-S000000451043 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1555 | 0.28404 | SPN-S000000008504 | 4186689000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
671 | 46.5 | UNIT 2, SWANMEAD WAY | TONBRIDGE | TN9 1GG | Tonbridge & Malling |  | Retail Warehouse And Premises | bigbox | 1 | 2121.7 | 22838 | GIA | 340000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.87 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.37 | 191 | 50 | 1800078 | SPN-S000000441286 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 108 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1978 | 0.28431 | SPN-S000000008504 | 11823516000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
672 | 46.4 | UNIT 45 DEAL BUSINESS PARK, SOUTHWALL ROAD | DEAL | CT14 9FH | Dover |  | Warehouse And Premises | industrial | 1 | 1299 | 13982 | GIA | 121000 | DEAL 33/11KV | inside-area | 0.17 | Betteshanger Grid | Sellindge | East Kent Zone | 12.3 | primary | 12.3 | Green | 24 | 11.7 | Thermal | 0 | 0 | 0 | 0 | 9.7 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.3 | 18.6 | Winter | 51.1211 | 11.4 | Green (Over 5% headroom) | 87701 | 100 | 2.06 | 32 | 4 | 112897 | SPN-S000000362945 | 500 | 350 | 60-80% | DEAL 33/11KV | 304 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2262 | 1.3922 | SPN-S000000008389 | 9794088000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
673 | 46.4 | DENNE & WOOLSTON, NORTHWALL ROAD | DEAL | CT14 6PN | Dover |  | Workshop And Premises | industrial | 1 | 1071.9 | 11538 | GIA | 45250 | DEAL 33/11KV | inside-area | 0.69 | Betteshanger Grid | Sellindge | East Kent Zone | 12.3 | primary | 12.3 | Green | 24 | 11.7 | Thermal | 0 | 0 | 0 | 0 | 9.7 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.3 | 18.6 | Winter | 51.1211 | 11.4 | Green (Over 5% headroom) | 87701 | 100 | 1.7 | 48 | 4 | 115341 | SPN-S000000371473 | 500 | 350 | 60-80% | DEAL 33/11KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2291 | 1.3985 | SPN-S000000008389 | 1635523000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
674 | 46.4 | UCL COACHBUILDERS, MINTERS YARD, SOUTHWALL ROAD | DEAL | CT14 9QB | Dover | UCL COACHBUILDERS | Workshop And Premises | industrial | 1 | 1061.2 | 11423 | GIA | 44750 | DEAL 33/11KV | inside-area | 0.31 | Betteshanger Grid | Sellindge | East Kent Zone | 12.3 | primary | 12.3 | Green | 24 | 11.7 | Thermal | 0 | 0 | 0 | 0 | 9.7 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.3 | 18.6 | Winter | 51.1211 | 11.4 | Green (Over 5% headroom) | 87701 | 100 | 1.69 | 48 | 4 | 115456 | SPN-R000000838908-000-004Z | 200 | 140 | 60-80% | DEAL 33/11KV | 14 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2291 | 1.3896 | SPN-S000000008389 | 130954145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
675 | 46.4 | CLAYGATE DISTRIBUTION LTD, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 12050.76 | 129713 | GIA | 995000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 26 | 19.15 | 301 | 24 | 789555 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 200003710041 | B1 Offices and Workshop businesses | 9410 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2013-07-25 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 6497316000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
676 | 46.4 | 3, PATRICIA WAY, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LF | Thanet |  | Factory And Premises; Warehouse And Premises; Warehouse, Office And Premises; Workshop And Premises | industrial | 4 | 9970.49 | 107321 | GIA | 723500 | ST PETERS 33/11KV | inside-area | 1.88 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 32 | 15.84 | 598 | 31 | 1386492 | SPN-S000000342743 | 1000 | 700 | 60-80% | ST PETERS 33/11KV | 129 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003079933 | Retail/Financial and Professional Services | 1146 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-05-05 |  | 1 | FALSE | 51.3556 | 1.4099 | SPN-S000000008478 | 1781188000;1781185000;9607760000;3700181000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
677 | 46.4 | 6 LYSANDER CLOSE 3-8 ANSON CLOSE AND 5-7 PATRICIA WAY, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LF | Thanet |  | Factory And Premises | industrial | 1 | 9929.1 | 106876 | GIA | 460000 | ST PETERS 33/11KV | inside-area | 1.88 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 32 | 15.78 | 596 | 31 | 1386937 | SPN-S000000342743 | 1000 | 700 | 60-80% | ST PETERS 33/11KV | 129 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003080012 | B1 Offices and Workshop businesses | 820 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-02-04 |  | 1 | FALSE | 51.3556 | 1.4099 | SPN-S000000008478 | 11497429000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
678 | 46.4 | UNIT 6 & 15 WHEELBARROW PARK, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 9462.97 | 101858 | GIA | 465000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 34 | 15.04 | 237 | 24 | 817410 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10014308274 | B2 to B7 General Industrial and Special Industrial Groups | 1208 | A | Natural Gas | 4 |  | Heating and Natural Ventilation | 2016-10-03 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 15010089000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
679 | 46.4 | UNITS 1-2, PATTENDEN LANE | TONBRIDGE | TN12 9QD | Maidstone |  | Factory And Premises | industrial | 1 | 7307.71 | 78659 | GIA | 312500 | MARDEN 33/11KV | inside-area | 0.23 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 44 | 11.61 | 438 | 24 | 840609 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.49097 | SPN-S000000008433 | 10294158000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
680 | 46.4 | SILENT GLISS LTD, PYRAMID BUSINESS PARK, POORHOLE LANE | BROADSTAIRS | CT10 2PT | Thanet |  | Factory And Premises | industrial | 1 | 6725.35 | 72391 | GIA | 710000 | ST PETERS 33/11KV | inside-area | 1.62 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 47 | 10.69 | 404 | 31 | 1421422 | SPN-S000000343300 | 1000 | 700 | 60-80% | THANET 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10012956843 | B2 to B7 General Industrial and Special Industrial Groups | 5902 | C | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2020-02-27 |  | 1 | FALSE | 51.3618 | 1.3999 | SPN-S000000008478 | 4725995000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
681 | 46.4 | 20, PATRICIA WAY, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LE | Thanet |  | Warehouse And Premises | industrial | 1 | 5185 | 55811 | GIA | 238000 | ST PETERS 33/11KV | inside-area | 1.88 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 61 | 8.24 | 130 | 31 | 1438002 | SPN-S000000342427 | 800 | 400 | 40-60% | RAMSGATE 33/11KV | 126 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003079926 | Retail/Financial and Professional Services | 4603 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-02-06 |  | 1 | FALSE | 51.3555 | 1.4097 | SPN-S000000008478 | 1781120000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
682 | 46.4 | UNIT 18, WHEELBARROW PARK, PATTENDEN LANE | TONBRIDGE | TN12 9QS | Maidstone |  | Warehouse And Premises | industrial | 2 | 5182.24 | 55781 | GIA | 397000 | MARDEN 33/11KV | inside-area | 0.24 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 61 | 8.24 | 130 | 24 | 863487 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.48946 | SPN-S000000008433 | 12510255000;12510252000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
683 | 46.4 | ENGLISH NATIONAL OPERA FRON BAYS 4-5, PATTENDEN LANE | TONBRIDGE | TN12 9QS | Maidstone | ENGLISH NATIONAL OPERA | Store And Premises | industrial | 1 | 5170 | 55649 | GIA | 252500 | MARDEN 33/11KV | inside-area | 0.24 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 62 | 8.22 | 129 | 24 | 863619 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.48946 | SPN-S000000008433 | 350469148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
684 | 46.4 | UNITS 8A-8, PATTENDEN LANE | TONBRIDGE | TN12 9QD | Maidstone |  | Factory And Premises | industrial | 1 | 4223.11 | 45457 | GIA | 297500 | MARDEN 33/11KV | inside-area | 0.23 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 75 | 6.71 | 253 | 24 | 873811 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.49097 | SPN-S000000008433 | 10294157000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
685 | 46.4 | STAPLEHURST TRANSIT LTD, STAPLEHURST ROAD | TONBRIDGE | TN12 9BW | Maidstone | STAPLEHURST TRANSIT LTD | Warehouse And Premises | industrial | 1 | 4126.55 | 44418 | GIA | 173000 | MARDEN 33/11KV | inside-area | 3.76 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 77 | 6.56 | 103 | 24 | 874850 | SPN-S000000392963 | 100 | 30 | 20-40% |  | 373 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.2012 | 0.526 | SPN-S000000008433 | 3707633000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
686 | 46.4 | BAY 3, WHEELBARROW PARK, PATTENDEN LANE | TONBRIDGE | TN12 9QS | Maidstone |  | Warehouse And Premises | industrial | 1 | 3940.7 | 42417 | GIA | 185000 | MARDEN 33/11KV | inside-area | 0.24 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 81 | 6.26 | 99 | 24 | 876851 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.48946 | SPN-S000000008433 | 2780279000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
687 | 46.4 | LUPOFRESH LTD, BENOVER ROAD | MAIDSTONE | ME18 6ET | Maidstone |  | Factory And Premises | industrial | 1 | 3673.81 | 39545 | GIA | 152000 | MARDEN 33/11KV | inside-area | 6.3 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 87 | 5.84 | 220 | 24 | 879723 | SPN-R000000843305-000-080Z | 200 | 140 | 60-80% | MARDEN 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.2182 | 0.43076 | SPN-S000000008433 | 15036388000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
688 | 46.4 | UNIT 4 FRUIT SHOW BUSINESS PARK, PATTENDEN LANE | TONBRIDGE | TN12 9GZ | Maidstone |  | Warehouse And Premises | industrial | 2 | 3366.8 | 36240 | GIA | 184500 | MARDEN 33/11KV | inside-area | 0.3 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 94 | 5.35 | 84 | 24 | 883028 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 117 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1784 | 0.49034 | SPN-S000000008433 | 15075457000;15075387000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
689 | 46.4 | UNITS 1-3 PIONEER BUSINESS PARK, PRINCES ROAD | RAMSGATE | CT11 7RX | Thanet |  | Warehouse And Premises | industrial | 1 | 2998.76 | 32278 | GIA | 90500 | ST PETERS 33/11KV | inside-area | 3.45 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.77 | 75 | 31 | 1461535 | SPN-S000000342157 | 500 | 250 | 40-60% | RAMSGATE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3413 | 1.4082 | SPN-S000000008478 | 8915163000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
690 | 46.4 | 9, ANSON CLOSE, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LG | Thanet |  | Warehouse And Premises | industrial | 1 | 2992.18 | 32208 | GIA | 161000 | ST PETERS 33/11KV | inside-area | 1.79 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.75 | 75 | 31 | 1461605 | SPN-S000000342068 | 500 | 250 | 40-60% | ST PETERS 33/11KV | 84 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3558 | 1.4181 | SPN-S000000008478 | 5313732000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
691 | 46.4 | LONDON ARRAY CONSTRUCTION MANAGEMENT AND OPERATIONS AND MAINTENANCE, MILITARY ROAD | RAMSGATE | CT11 9LG | Thanet |  | Workshop And Premises | industrial | 1 | 2868.21 | 30873 | NIA | 209000 | ST PETERS 33/11KV | inside-area | 4.7 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.56 | 129 | 31 | 1462940 | SPN-S000000342213 | 500 | 50 | 0-20% | RAMSGATE 33/11KV | 128 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013307477 | B8 Storage or Distribution | 2625 | B | Natural Gas | 4 | 2 | Air Conditioning | 2012-03-14 |  | 1 | FALSE | 51.3296 | 1.4164 | SPN-S000000008478 | 8361442000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
692 | 46.4 | BRIDGE HOUSE, PATTENDEN LANE | TONBRIDGE | TN12 9QS | Maidstone |  | Warehouse, Offices And Premises | industrial | 1 | 2780.4 | 29928 | GIA | 229000 | MARDEN 33/11KV | inside-area | 0.24 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 4.42 | 195 | 24 | 889340 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.48946 | SPN-S000000008433 | 14513867000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
693 | 46.4 | UNITS 5-7, NORTHDOWN ROAD INDUSTRIAL ESTATE, NORTHDOWN ROAD | BROADSTAIRS | CT10 3JP | Thanet |  | Warehouse, Office And Premises; Workshop, Warehouse And Premises | industrial | 2 | 2746.46 | 29563 | GIA | 179000 | ST PETERS 33/11KV | inside-area | 0.4 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.36 | 124 | 31 | 1464250 | SPN-S000000342441 | 500 | 250 | 40-60% | ST PETERS 33/11KV | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013307854 | B1 Offices and Workshop businesses | 555 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-09-20 |  | 1 | FALSE | 51.3694 | 1.421 | SPN-S000000008478 | 8959417000;13598660000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
694 | 46.4 | WAREHOUSE 1 G G TOMKINSON, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 2485.54 | 26754 | GIA | 179000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 3.95 | 62 | 24 | 892514 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10091196474 | B8 Storage or Distribution | 2014 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2018-04-12 |  | 0.8 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 6809058000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
695 | 46.4 | DANE PARK ROAD | RAMSGATE | CT11 7LT | Thanet | W W MARTIN LTD | Workshop And Premises | industrial | 1 | 2346.44 | 25257 | GIA | 56500 | ST PETERS 33/11KV | inside-area | 3.67 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.73 | 106 | 31 | 1468556 | SPN-S000000342190 | 800 | 400 | 40-60% | THANET 33/11KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062627905 | Offices and Workshop Businesses | 975 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2024-05-24 |  | 1 | FALSE | 51.3391 | 1.4241 | SPN-S000000008478 | 458604145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
696 | 46.4 | 5, LYSANDER CLOSE | BROADSTAIRS | CT10 2LA | Thanet |  | Factory And Premises; Workshop And Premises | industrial | 2 | 2186.3 | 23533 | GIA | 153000 | ST PETERS 33/11KV | inside-area | 1.7 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.47 | 131 | 31 | 1470280 | SPN-S000000343316 | 1000 | 700 | 60-80% | THANET 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3583 | 1.4058 | SPN-S000000008478 | 3667192000;1782924000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
697 | 46.4 | 12, LYSANDER CLOSE | BROADSTAIRS | CT10 2YJ | Thanet |  | Factory And Premises | industrial | 1 | 2111.6 | 22729 | GIA | 111000 | ST PETERS 33/11KV | inside-area | 2.08 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.36 | 127 | 31 | 1471084 | SPN-S000000342427 | 800 | 400 | 40-60% | RAMSGATE 33/11KV | 128 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003079937 | General Industrial and Special Industrial Groups | 2156 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-01-11 |  | 1 | FALSE | 51.354 | 1.4077 | SPN-S000000008478 | 1782932000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
698 | 46.4 | 12, WHEELBARROW INDUSTRIAL ESTATE, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 2050.79 | 22074 | GIA | 166000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 3.26 | 51 | 24 | 897194 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 200003669283 | B2 to B7 General Industrial and Special Industrial Groups | 2213 | C | Oil | 3 |  | Heating and Natural Ventilation | 2018-12-18 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 6084860000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
699 | 46.4 | TEA WAREHOUSE 9, PATTENDEN LANE | MAIDSTONE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1955.23 | 21046 | GIA | 152000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 3.11 | 49 | 24 | 898222 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10091196474 | B8 Storage or Distribution | 2014 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2018-04-12 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 13346324000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
700 | 46.4 | UNITS 7 & 10, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1893.4 | 20380 | GIA | 144000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 3.01 | 47 | 24 | 898888 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1774 | 0.48987 | SPN-S000000008433 | 7445790000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
701 | 46.3 | PROSPECT PLACE, WESTGATE ROAD | DARTFORD | DA1 1DY | Dartford | B & Q PLC; MATALAN | Retail Warehouse And Premises | bigbox | 2 | 13969.22 | 150363 | GIA | 1635000 | DARTFORD GRID B 11KV | inside-area | 0.38 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 69 | 22.2 | 1257 | 54 | 2622386 | LPN-S000000073869 | 1000 | 500 | 40-60% | DARTFORD GRID B 11KV | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4473 | 0.21623 | LPN-S000000000716 | 3697774000;3102594000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
702 | 46.3 | HAYS ROAD | SNODLAND | ME6 5TQ | Tonbridge & Malling | TESCO STORES LTD | Warehouse And Premises | industrial | 1 | 23484.67 | 252787 | GIA | 2330000 | HALLING 33/11KV | inside-area | 4.34 | Medway Grid | Kingsnorth | Mid Kent Zone | 12.2 | primary | 12.2 | Green | 24 | 8.5 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 23 | 17.3 | Winter | 64.3478 | 14.8 | Green (Over 5% headroom) | 86988 | 34 | 37.32 | 587 | 3 | 218463 | SPN-R000000851909-000-083Z | 50 | 25 | 40-60% | HALLING 33/11KV | 280 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10002907830 | B8 Storage or Distribution | 22765 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-02-28 |  | 1 | FALSE | 51.3223 | 0.43039 | SPN-S000000008615 | 410268148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
703 | 46.3 | MEKADSHEI SHEVEI CHARITABLE TRUST BLDG 500 DISCOVERY PARK, RAMSGATE ROAD | SANDWICH | CT13 9FE | Dover |  | Offices And Premises | office | 1 | 13395.61 | 144189 | NIA | 2200000 | RICHBOROUGH 33/11KV | inside-area | 0.71 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 60 | 21.29 | 938 | 29 | 1198829 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.2869 | 1.3415 | SPN-S000000008342 | 15050412000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
704 | 46.3 | UNITS 6 & 7 (WAREHOUSES F & G BLDG 819) HUGIN LANE DISCOVERY PARK, RAMSGATE ROAD | SANDWICH | CT13 9FG | Dover |  | Offices And Premises | office | 1 | 2012.14 | 21658 | NIA | 287500 | RICHBOROUGH 33/11KV | inside-area | 0.78 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.2 | 141 | 29 | 1321360 | SPN-S000000341051 | 800 | 720 | 80-100% | RICHBOROUGH 33/11KV | 252 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034887523 | Offices and Workshop Businesses | 1481 | C | Natural Gas | 3 | 57 | Air Conditioning | 2024-02-14 |  | 0.5 | FALSE | 51.2855 | 1.3447 | SPN-S000000008342 | 14014773000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
705 | 46.3 | 3RD FLR CENTRE POD BLDG 530, EAST SITE DISCOVERY PARK, RAMSGATE ROAD | SANDWICH | CT13 9NJ | Dover |  | Offices And Premises | office | 1 | 1924.74 | 20718 | NIA | 380000 | RICHBOROUGH 33/11KV | inside-area | 2.08 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.06 | 135 | 29 | 1322300 | SPN-S000000341057 | 1000 | 700 | 60-80% | RICHBOROUGH 33/11KV | 160 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.274 | 1.3408 | SPN-S000000008342 | 8577630000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
706 | 46.3 | OFFS 1-3 & 8-9 SOUTH POD & LAB 24 & OFF 25 CENTRAL POD 2ND FLR BLDG 530, EAST SITE DISCOVERY PARK, RAMSGATE ROAD | SANDWICH | CT13 9NJ | Dover |  | Offices And Premises | office | 1 | 1907.6 | 20533 | NIA | 380000 | RICHBOROUGH 33/11KV | inside-area | 2.08 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 3.03 | 134 | 29 | 1322485 | SPN-S000000341057 | 1000 | 700 | 60-80% | RICHBOROUGH 33/11KV | 160 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.274 | 1.3408 | SPN-S000000008342 | 14925937000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
707 | 46.3 | MKR RECOVERY SERVICES, AMBROSETTI SITE, RAMSGATE ROAD | SANDWICH | CT13 9QN | Dover |  | Workshop And Premises | industrial | 1 | 1684.07 | 18127 | GIA | 125000 | RICHBOROUGH 33/11KV | inside-area | 1.88 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 2.68 | 76 | 29 | 1324891 | SPN-S000000343069 | 200 | 140 | 60-80% | RICHBOROUGH 33/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3091 | 1.3502 | SPN-S000000008342 | 14682780000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
708 | 46.3 | DPH 1C 022 023 024 & 029 1ST FLR DISCOVERY PARK HOUSE BLDG 530, RAMSGATE ROAD, DISCOVERY PARK | SANDWICH | CT13 9ND | Dover |  | Laboratory And Premises | industrial | 1 | 1372.33 | 14772 | NIA | 257500 | RICHBOROUGH 33/11KV | inside-area | 0.93 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 2.18 | 137 | 29 | 1328246 | SPN-S000000341051 | 800 | 720 | 80-100% | RICHBOROUGH 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034887858 | General Industrial and Special Industrial Groups | 4597 | A | District Heating | 4 | 3 | Heating and Natural Ventilation | 2022-10-05 |  | 0.5 | FALSE | 51.284 | 1.3457 | SPN-S000000008342 | 15113125000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
709 | 46.3 | GEOFF FISHER TRANSPORT LTD, MINTERS YARD, RAMSGATE ROAD | SANDWICH | CT13 9LY | Dover |  | Warehouse Workshop And Premises | industrial | 1 | 1308.64 | 14086 | GIA | 105000 | RICHBOROUGH 33/11KV | inside-area | 1.5 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 2.08 | 59 | 29 | 1328932 | SPN-S000000342599 | 800 | 560 | 60-80% | RICHBOROUGH 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034882227 | Storage or Distribution | 1453 | E | Oil | 3 |  | Heating and Natural Ventilation | 2026-05-21 |  | 0.67 | FALSE | 51.279 | 1.3505 | SPN-S000000008342 | 12622009000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
710 | 46.3 | EAST KENT DISTRIBUTION DEPOT LITTLE CLIFFSEND FARM, CHALK HILL | RAMSGATE | CT12 5HP | Thanet |  | Warehouse And Premises | industrial | 1 | 1231.73 | 13258 | GIA | 74000 | RICHBOROUGH 33/11KV | inside-area | 4.86 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 1.96 | 31 | 29 | 1329760 | SPN-R000000846305-000-015Z | 200 | 140 | 60-80% | RAMSGATE 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3303 | 1.3813 | SPN-S000000008342 | 11899067000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
711 | 46.3 | DPH GC 001 011 012 024 025 GND FLR BLDG 530, RAMSGATE ROAD, DISCOVERY PARK | SANDWICH | CT13 9ND | Dover |  | Laboratory And Premises | industrial | 1 | 1216.15 | 13091 | NIA | 229000 | RICHBOROUGH 33/11KV | inside-area | 0.93 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 1.93 | 122 | 29 | 1329927 | SPN-S000000341051 | 800 | 720 | 80-100% | RICHBOROUGH 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034887858 | General Industrial and Special Industrial Groups | 4597 | A | District Heating | 4 | 3 | Heating and Natural Ventilation | 2022-10-05 |  | 0.5 | FALSE | 51.284 | 1.3457 | SPN-S000000008342 | 15112619000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
712 | 46.3 | DPH GC 001 011 012 024 025 GND FLR, DISCOVERY PARK HOUSE BLDG 530, RAMSGATE ROAD | SANDWICH | CT13 9ND | Dover |  | Laboratory And Premises | industrial | 1 | 1216.15 | 13091 | NIA | 229000 | RICHBOROUGH 33/11KV | inside-area | 0.93 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 1.93 | 122 | 29 | 1329927 | SPN-S000000341051 | 800 | 720 | 80-100% | RICHBOROUGH 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10034887858 | General Industrial and Special Industrial Groups | 4597 | A | District Heating | 4 | 3 | Heating and Natural Ventilation | 2022-10-05 |  | 0.5 | FALSE | 51.284 | 1.3457 | SPN-S000000008342 | 15141373000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
713 | 46.3 | 1, CHANNEL VIEW ROAD | RAMSGATE | CT12 4EX | Thanet |  | Warehouse And Premises | industrial | 1 | 1155.1 | 12433 | GIA | 81000 | RICHBOROUGH 33/11KV | inside-area | 5.54 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 1.84 | 29 | 29 | 1330585 | SPN-S000000342155 | 315 | 94 | 20-40% | RICHBOROUGH 33/11KV | 189 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062283961 | B8 Storage or Distribution | 977 | A | Other | 4 |  | Unconditioned | 2020-04-28 |  | 1 | FALSE | 51.34 | 1.324 | SPN-S000000008342 | 13606860000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
714 | 46.3 | BUILDING 4, SANDWICH INDUSTRIAL ESTATE, RAMSGATE ROAD | SANDWICH | CT13 9LU | Dover | SDF FABRICATIONS LTD | Factory And Premises | industrial | 1 | 1055.99 | 11367 | GIA | 22000 | RICHBOROUGH 33/11KV | inside-area | 1.59 | Richborough Grid | Richborough | East Kent Zone | 12.2 | primary | 12.2 | Green | 23.8 | 9.9 | Thermal | 0 | 0 | 1.9 | 0 | 9.6 | Richborough Grid 33kV | 72.9 | GREEN | 144.9 | 49.9 | GREEN | 7 | 286.7 | 3 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | Green (Over 5% headroom) | 86988 | 100 | 1.68 | 63 | 29 | 1331651 | SPN-S000000341054 | 1000 | 900 | 80-100% | RICHBOROUGH 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.2781 | 1.3493 | SPN-S000000008342 | 1552772000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
715 | 46.3 | BIDDENDEN ROAD | ASHFORD | TN27 9HT | Maidstone | DANIELS GROUP | Factory And Premises | industrial | 1 | 5163.88 | 55583 | GIA | 375000 | HEADCORN 33/6.6KV | inside-area | 1.52 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 60 | 8.21 | 310 | 6 | 112126 | [9 empty] | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1629 | 0.63307 | SPN-S000000008365 | 9166218000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
716 | 46.3 | MARLEY FARM, HEADCORN ROAD | ASHFORD | TN27 8PJ | Ashford | PREMIER COATINGS LTD | Factory And Premises; Warehouse And Premises | industrial | 2 | 3533.77 | 38037 | GIA | 167000 | HEADCORN 33/6.6KV | inside-area | 3.54 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 88 | 5.62 | 212 | 6 | 129672 | SPN-R000000836509-000-274Z | 50 | 15 | 20-40% | HEADCORN 33/6.6KV | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10012861638 | B8 Storage or Distribution | 244 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-02-02 |  | 1 | FALSE | 51.1608 | 0.66272 | SPN-S000000008365 | 331582148;9026847000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
717 | 46.1 | FOWLER WELCH, LONDON ROAD | SITTINGBOURNE | ME9 9PR | Swale |  | Chill Store And Premises | industrial | 1 | 12938.54 | 139269 | GIA | 890000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 2.72 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 24 | 20.56 | 323 | 58 | 2384756 | SPN-S000000394342 | 200 | 60 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 43 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3307 | 0.78811 | SPN-S000000008344 | 10545595000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
718 | 46.1 | UNIT K, CASTLE ROAD | SITTINGBOURNE | ME10 3AP | Swale |  | Warehouse And Premises | industrial | 1 | 12446.58 | 133974 | GIA | 1000000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.46 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 24 | 19.78 | 311 | 58 | 2390051 | SPN-S000000394042 | 300 | 150 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 109 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3383 | 0.74937 | SPN-S000000008344 | 513796000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
719 | 46.1 | GALLERY DIRECT, CASTLE ROAD | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 12306.14 | 132462 | GIA | 620000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 25 | 19.56 | 308 | 58 | 2391563 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023196833 | General Industrial and Special Industrial Groups | 12368 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-10-08 |  | 1 | FALSE | 51.3462 | 0.75036 | SPN-S000000008344 | 15095318000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
720 | 46.1 | UNITS 3-4, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale | WIRE BELT COMPANY LTD | Factory And Premises; Warehouse And Premises | industrial | 4 | 10756.86 | 115786 | GIA | 791000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 28 | 17.09 | 645 | 58 | 2408239 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 4408235000;333399147;333391147;333736147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
721 | 46.1 | BENNETT OPIE LTD, WENTWORTH COURT, CASTLE ROAD | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 8757.8 | 94268 | GIA | 530000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 35 | 13.92 | 219 | 58 | 2429757 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 13402611000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
722 | 46.1 | LENHAM STORAGE LTD 22, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 8252.02 | 88824 | GIA | 670000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 37 | 13.11 | 206 | 58 | 2435201 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 11250717000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
723 | 46.1 | 7A-7G, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Factory And Premises | industrial | 1 | 7647.01 | 82312 | GIA | 435000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 40 | 12.15 | 459 | 58 | 2441713 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 337520147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
724 | 46.1 | DOLPHIN WORKS, CROWN QUAY LANE | SITTINGBOURNE | ME10 3JN | Swale | SUPREME CONCRETE | Factory And Premises | industrial | 1 | 7399.32 | 79646 | GIA | 477500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.73 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 41 | 11.76 | 444 | 58 | 2444379 | SPN-S000000391212 | 800 | 720 | 80-100% | SITTINGBOURNE TOWN 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3412 | 0.74263 | SPN-S000000008344 | 7491886000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
725 | 46.1 | PLOTS 4A 4B & 4C, BINGHAM ROAD | SITTINGBOURNE | ME10 3SU | Swale |  | Warehouse And Premises | industrial | 1 | 7261.32 | 78160 | GIA | 525000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.78 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 42 | 11.54 | 182 | 58 | 2445865 | SPN-S000000393241 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.346 | 0.76215 | SPN-S000000008344 | 11329705000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
726 | 46.1 | UNITS 1 & 2 TRILOGY, EUROLINK V, SWALE WAY | SITTINGBOURNE | ME10 3NH | Swale |  | Warehouse And Premises | industrial | 1 | 6809.67 | 73299 | GIA | 580000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 1.2 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 45 | 10.82 | 170 | 58 | 2450726 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10094600697 | B2 to B7 General Industrial and Special Industrial Groups | 3937 | A | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2021-04-25 |  | 1 | FALSE | 51.3448 | 0.76965 | SPN-S000000008344 | 13790643000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
727 | 46.1 | DOCUMENT WAREHOUSE UK, CASTLE ROAD | SITTINGBOURNE | ME10 3JP | Swale |  | Warehouse And Premises | industrial | 1 | 6525 | 70234 | GIA | 575000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.45 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 47 | 10.37 | 163 | 58 | 2453791 | SPN-S000000393486 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 145 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3457 | 0.75216 | SPN-S000000008344 | 9439577000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
728 | 46.1 | UNIT 10, STYLES CLOSE | SITTINGBOURNE | ME10 3BF | Swale |  | Warehouse And Premises | industrial | 5 | 5437.92 | 58533 | GIA | 501000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.8 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 56 | 8.64 | 136 | 58 | 2465492 | SPN-S000000393241 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 264 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10093085238 | B2 to B7 General Industrial and Special Industrial Groups | 2251 | A | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-11-29 |  | 0.5 | FALSE | 51.347 | 0.76103 | SPN-S000000008344 | 8175672000;9110926000;7436940000;6638461000;14947499000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
729 | 46.1 | CONSTANTIA SITTINGBOURNE EUROLINK COMMERCIAL PARK, BONHAM DRIVE | SITTINGBOURNE | ME10 3RY | Swale |  | Factory And Premises | industrial | 1 | 5278.1 | 56813 | GIA | 345000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.64 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 58 | 8.39 | 317 | 58 | 2467212 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 46 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3468 | 0.7487 | SPN-S000000008344 | 13309413000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
730 | 46.1 | SALVATORI BUILDING EUROLINK V, SWALE WAY | SITTINGBOURNE | ME10 3TF | Swale |  | Warehouse And Premises | industrial | 1 | 5135.13 | 55274 | GIA | 457500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.83 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 59 | 8.16 | 128 | 58 | 2468751 | SPN-S000000393241 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 370 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3436 | 0.76477 | SPN-S000000008344 | 11329647000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
731 | 46.1 | W J ODDS LTD, CROWN QUAY LANE | SITTINGBOURNE | ME10 3JN | Swale |  | Factory And Premises | industrial | 1 | 4520.55 | 48659 | GIA | 101000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.73 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 67 | 7.18 | 271 | 58 | 2475366 | SPN-S000000391212 | 800 | 720 | 80-100% | SITTINGBOURNE TOWN 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3412 | 0.74263 | SPN-S000000008344 | 10358997000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
732 | 46.1 | MACO DOOR AND HARDWARE (UK)LTD, CASTLE ROAD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3LY | Swale |  | Warehouse And Premises | industrial | 1 | 4290.1 | 46178 | GIA | 280000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.31 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 71 | 6.82 | 107 | 58 | 2477847 | SPN-S000000394503 | 500 | 250 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 79 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3428 | 0.74908 | SPN-S000000008344 | 1334367000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
733 | 46.1 | UNIT 2 DOLPHIN PARK, CREMERS ROAD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3HB | Swale |  | Warehouse And Premises | industrial | 1 | 4052.64 | 43622 | GIA | 307500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.28 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 75 | 6.44 | 101 | 58 | 2480403 | SPN-S000000393486 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10035063979 | B8 Storage or Distribution | 3273 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2022-06-07 |  | 0.75 | FALSE | 51.3439 | 0.75127 | SPN-S000000008344 | 3951250000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
734 | 46.1 | RADFIELD, LONDON ROAD | SITTINGBOURNE | ME9 9PS | Swale |  | Factory And Premises | industrial | 1 | 4008 | 43142 | GIA | 222000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 2.63 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 76 | 6.37 | 240 | 58 | 2480883 | SPN-S000000394342 | 200 | 60 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10096400309 | General Industrial and Special Industrial Groups | 269 | B | Other | 3 |  | Unconditioned | 2023-06-16 |  | 1 | FALSE | 51.3311 | 0.78693 | SPN-S000000008344 | 1302141000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
735 | 46.1 | LAND FOR PARKING, BONHAM DRIVE | SITTINGBOURNE | ME10 3RR | Swale |  | Storage Depot And Premises | industrial | 1 | 3695.3 | 39776 | GIA | 36750 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.78 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 82 | 5.87 | 92 | 58 | 2484249 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 236 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3485 | 0.75024 | SPN-S000000008344 | 10722365000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
736 | 46.1 | DOKA UK FORMWORK TECHNOLOGIES LTD, EUROLINK V INDUSTRIAL PARK, SWALE WAY | SITTINGBOURNE | ME10 3NH | Swale |  | Warehouse And Premises | industrial | 1 | 3452.88 | 37166 | GIA | 432500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 1.2 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 88 | 5.49 | 86 | 58 | 2486859 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10094599193 | B1 Offices and Workshop businesses | 4286 | A | Natural Gas | 4 |  | Heating and Natural Ventilation | 2020-02-11 |  | 1 | FALSE | 51.3448 | 0.76965 | SPN-S000000008344 | 13034953000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
737 | 46.1 | 9A-9C, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Factory And Premises | industrial | 1 | 3373.19 | 36309 | GIA | 260000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 90 | 5.36 | 202 | 58 | 2487716 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 396980147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
738 | 46.1 | 12A-12D, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Factory And Premises | industrial | 1 | 3313.6 | 35667 | GIA | 240000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 92 | 5.27 | 199 | 58 | 2488358 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 337519147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
739 | 46.1 | UNIT 2, MANTLE CLOSE | SITTINGBOURNE | ME10 3BW | Swale |  | Warehouse And Premises | industrial | 2 | 3263.48 | 35128 | GIA | 282000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 1.02 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 93 | 5.19 | 82 | 58 | 2488897 | SPN-S000000391348 | 200 | 100 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 380 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10013742170 | B8 Storage or Distribution | 1348 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-11-16 |  | 1 | FALSE | 51.3468 | 0.76535 | SPN-S000000008344 | 7580103000;6591247000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
740 | 46.1 | UNIT 4, CROWN QUAY TRADE CENTRE 1, EUROLINK WAY | SITTINGBOURNE | ME10 3DY | Swale |  | Warehouse And Premises | industrial | 1 | 3195.14 | 34392 | GIA | 154000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.71 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 95 | 5.08 | 80 | 58 | 2489633 | SPN-S000000391212 | 800 | 720 | 80-100% | SITTINGBOURNE TOWN 33/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023197809 | B1 Offices and Workshop businesses | 441 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-05-26 |  | 1 | FALSE | 51.342 | 0.74291 | SPN-S000000008344 | 6978707000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
741 | 46.1 | 1-3, HEARD WAY INDUSTRIAL ESTATE, HEARD WAY | SITTINGBOURNE | ME10 3SA | Swale |  | Warehouse And Premises | industrial | 1 | 3081.15 | 33165 | GIA | 201000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.54 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 99 | 4.9 | 77 | 58 | 2490860 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 59 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.346 | 0.74949 | SPN-S000000008344 | 8796811000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
742 | 46.1 | 10-10B, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Factory And Premises | industrial | 1 | 3076.51 | 33115 | GIA | 295000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 99 | 4.89 | 185 | 58 | 2490910 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 333392147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
743 | 46.1 | 13, DOLPHIN PARK, UPPER FIELD ROAD | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 3031.96 | 32636 | GIA | 220000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.82 | 76 | 58 | 2491389 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 11881364000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
744 | 46.1 | GATEWAY CENTRE, CASTLE ROAD | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 3022.9 | 32538 | GIA | 234000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.8 | 76 | 58 | 2491487 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 3328459000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
745 | 46.1 | UNIT 5, CREMERS ROAD, DOLPHIN PARK, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3HB | Swale |  | Warehouse And Premises | industrial | 1 | 2968 | 31947 | GIA | 327500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.28 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.72 | 74 | 58 | 2492078 | SPN-S000000393486 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3439 | 0.75127 | SPN-S000000008344 | 14997070000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
746 | 46.1 | UNITS 15B & 15C, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 2915.44 | 31382 | GIA | 215000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.63 | 73 | 58 | 2492643 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 8335816000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
747 | 46.1 | CROWN QUAY LANE | SITTINGBOURNE | ME10 3HU | Swale | SWALE MOTORS LIMITED | Vehicle Repair Workshop And Premises | industrial | 1 | 2880.3 | 31003 | GIA | 169000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.9 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.58 | 130 | 58 | 2493022 | SPN-S000000391670 | 500 | 350 | 60-80% | SITTINGBOURNE TOWN 33/11KV | 25 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062626708 | B2 to B7 General Industrial and Special Industrial Groups | 865 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-02-18 |  | 1 | FALSE | 51.3405 | 0.74037 | SPN-S000000008344 | 294256147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
748 | 46.1 | MAINSTREAM HOUSE, BONHAM DRIVE, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Factory And Premises | industrial | 1 | 2815.57 | 30307 | GIA | 188000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.47 | 169 | 58 | 2493718 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 4830889000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
749 | 46.1 | COOKS CLASSICS, EUROLINK V INDUSTRIAL PARK, SWALE WAY | SITTINGBOURNE | ME10 3NH | Swale |  | Warehouse And Premises | industrial | 1 | 2775.4 | 29874 | GIA | 290000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 1.2 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.41 | 69 | 58 | 2494151 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023202835 | Storage or Distribution | 5129 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2022-09-29 |  | 0.75 | FALSE | 51.3448 | 0.76965 | SPN-S000000008344 | 13034549000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
750 | 46.1 | JEWSON LTD, CROWN QUAY LANE | SITTINGBOURNE | ME10 3JN | Swale |  | Warehouse And Premises | industrial | 1 | 2719.6 | 29274 | GIA | 136000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.73 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.32 | 68 | 58 | 2494751 | SPN-S000000391212 | 800 | 720 | 80-100% | SITTINGBOURNE TOWN 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3412 | 0.74263 | SPN-S000000008344 | 14291432000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
751 | 46.1 | 14B & 14C, DOLPHIN PARK, UPPER FIELD ROAD | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 2582.3 | 27796 | GIA | 191000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 4.1 | 65 | 58 | 2496229 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 8609534000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
752 | 46.1 | PLOT N2A, CASTLE ROAD | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 2470.87 | 26596 | GIA | 214000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.93 | 62 | 58 | 2497429 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 6426182000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
753 | 46.1 | TRANCHE 3 AT 22, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Factory And Premises | industrial | 1 | 2462.86 | 26510 | GIA | 195000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.91 | 148 | 58 | 2497515 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 11250733000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
754 | 46.1 | UNIT 1A, BONHAM DRIVE, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 2404.16 | 25878 | GIA | 183000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.82 | 60 | 58 | 2498147 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 5284785000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
755 | 46.1 | 4E, STYLES CLOSE | SITTINGBOURNE | ME10 3BF | Swale |  | Factory And Premises | industrial | 1 | 2210.34 | 23792 | GIA | 237000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.8 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.51 | 133 | 58 | 2500233 | SPN-S000000393241 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 264 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10093085238 | B2 to B7 General Industrial and Special Industrial Groups | 2251 | A | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-11-29 |  | 0.5 | FALSE | 51.347 | 0.76103 | SPN-S000000008344 | 10769380000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
756 | 46.1 | PLOT 4F, PHASE IV, EUROLINK BUSINESS PARK | SITTINGBOURNE | ME10 3TF | Swale |  | Warehouse And Premises | industrial | 1 | 2136 | 22992 | GIA | 192000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.83 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.39 | 53 | 58 | 2501033 | SPN-S000000393241 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 370 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3436 | 0.76477 | SPN-S000000008344 | 6076264000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
757 | 46.1 | D5, BONHAM DRIVE | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 2032 | 21872 | GIA | 160000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.23 | 51 | 58 | 2502153 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 385409147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
758 | 46.1 | UNIT D3, BONHAM DRIVE, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RY | Swale |  | Factory And Premises | industrial | 1 | 1967.43 | 21177 | GIA | 154000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.64 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 3.13 | 118 | 58 | 2502848 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 46 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3468 | 0.7487 | SPN-S000000008344 | 335678147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
759 | 45.9 | TESCO STORES LTD, CRESCENT ROAD | FAVERSHAM | ME13 7AS | Swale |  | Superstore And Premises | bigbox | 2 | 9182.82 | 98843 | GIA | 2380000 | FAVERSHAM 33/11KV | inside-area | 1.35 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 59 | 14.59 | 826 | 21 | 995192 | SPN-S000000391941 | 500 | 350 | 60-80% | FAVERSHAM 33/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3171 | 0.89354 | SPN-S000000008405 | 13291168000;13291168000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
760 | 45.9 | MORRISONS SUPERMARKET PLC, MILL WAY | SITTINGBOURNE | ME10 3ET | Swale |  | Superstore And Premises | bigbox | 1 | 6738.6 | 72534 | GIA | 1560000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.22 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 81 | 10.71 | 606 | 25 | 1142843 | SPN-S000000393511 | 315 | 158 | 40-60% | SITTINGBOURNE WEST 33/11KV | 194 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3439 | 0.73225 | SPN-S000000008444 | 14787514000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
761 | 45.9 | BUNNINGS, SITTINGBOURNE RETAIL PARK, MILL WAY | SITTINGBOURNE | ME10 3ET | Swale |  | Retail Warehouse And Premises | bigbox | 1 | 6317.12 | 67997 | GIA | 342500 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.22 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 86 | 10.04 | 569 | 25 | 1147380 | SPN-S000000393511 | 315 | 158 | 40-60% | SITTINGBOURNE WEST 33/11KV | 194 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3439 | 0.73225 | SPN-S000000008444 | 11193194000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
762 | 45.9 | SAINSBURYS SUPERSTORE, ROMAN SQUARE | SITTINGBOURNE | ME10 4BJ | Swale |  | Superstore And Premises | bigbox | 1 | 5696.27 | 61314 | GIA | 1430000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.51 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 95 | 9.05 | 513 | 25 | 1154063 | SPN-S000000393350 | 500 | 250 | 40-60% | SITTINGBOURNE WEST 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3395 | 0.73678 | SPN-S000000008444 | 11385424000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
763 | 45.9 | SAINSBURYS, BYSING WOOD ROAD | FAVERSHAM | ME13 7UD | Swale |  | Superstore And Premises | bigbox | 1 | 4373.14 | 47072 | GIA | 1010000 | FAVERSHAM 33/11KV | inside-area | 3.05 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 6.95 | 394 | 21 | 1046963 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3227 | 0.87076 | SPN-S000000008405 | 11698113000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
764 | 45.9 | WICKES BUILDING SUPPLIES LTD, CRYALLS LANE | SITTINGBOURNE | ME10 1NU | Swale |  | Retail Warehouse And Premises | bigbox | 1 | 3226.6 | 34731 | GIA | 330000 | SITTINGBOURNE WEST 33/11KV | inside-area | 0.19 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 5.13 | 290 | 25 | 1180646 | SPN-S000000391913 | 500 | 350 | 60-80% | SITTINGBOURNE WEST 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062693197 | Retail/Financial and Professional Services | 2766 | B | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2022-06-28 |  | 1 | FALSE | 51.3426 | 0.71706 | SPN-S000000008444 | 9199953000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
765 | 45.9 | HOME BARGAINS, NORTH LANE | FAVERSHAM | ME13 7DY | Swale |  | Retail Warehouse And Premises | bigbox | 1 | 2180.11 | 23466 | GIA | 267500 | FAVERSHAM 33/11KV | inside-area | 1.73 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 3.46 | 196 | 21 | 1070569 | SPN-S000000394288 | 800 | 560 | 60-80% | FAVERSHAM 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062626173 | Retail/Financial and Professional Services | 2227 | A | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2025-02-14 |  | 1 | FALSE | 51.317 | 0.8877 | SPN-S000000008405 | 14949704000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
766 | 45.9 | UNITS H1-H4, EAST MILL, IMPERIAL BUSINESS ESTATE | GRAVESEND | DA11 0DP | Gravesham |  | Warehouse And Premises | industrial | 1 | 4554.2 | 49021 | GIA | 505000 | ROSHERVILLE 33/6.6KV | inside-area | 0.4 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 64 | 7.24 | 114 | 14 | 1941835 | SPN-S000000311495 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200002471190 | B8 Storage or Distribution | 911 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2017-04-18 |  | 1 | FALSE | 51.4449 | 0.35813 | SPN-S000000008470 | 12465746000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
767 | 45.9 | WALBROOK WEST, QUEENBOROUGH ROAD | SHEERNESS | ME12 3XT | Swale |  | Warehouse And Premises | industrial | 1 | 3980.29 | 42843 | GIA | 372500 | MINSTER 33/6.6KV | inside-area | 0.64 | Sheerness Grid | Kemsley | Mid Kent Zone | 4.4 | primary | 4.4 | Green | 13.8 | 9 | Thermal | 0 | 2.3 | 0 | 2.3 | 4.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 13.2 | 10.5 | Winter | 34.8485 | 4.6 | Green (Over 5% headroom) | 31373 | 73 | 6.32 | 100 | 1 | 21860 | SPN-S000000400117 | 200 | 100 | 40-60% | MINSTER 33/6.6KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10094602751 | Storage or Distribution | 3826 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2023-10-02 |  | 1 | FALSE | 51.4124 | 0.80188 | SPN-S000000008436 | 14460036000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
768 | 45.9 | UNITS J1-J2, EAST MILL, IMPERIAL BUSINESS ESTATE | GRAVESEND | DA11 0DP | Gravesham |  | Warehouse And Premises | industrial | 1 | 2687.43 | 28927 | GIA | 315000 | ROSHERVILLE 33/6.6KV | inside-area | 0.4 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 4.27 | 67 | 14 | 1961929 | SPN-S000000311495 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012011458 | B1 Offices and Workshop businesses | 889 | C | Natural Gas | 3 |  | Air Conditioning | 2017-04-21 |  | 1 | FALSE | 51.4449 | 0.35813 | SPN-S000000008470 | 12465722000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
769 | 45.9 | UNIT G1 & G2, WEST MILL, IMPERIAL BUSINESS ESTATE | GRAVESEND | DA11 0DL | Gravesham |  | Factory And Premises | industrial | 1 | 2254.44 | 24267 | GIA | 270000 | ROSHERVILLE 33/6.6KV | inside-area | 0.22 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 3.58 | 135 | 14 | 1966589 | SPN-S000000316858 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 |  | D2 General Assembly and Leisure plus Night Clubs and Theatres | 1293 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-21 |  | 0.75 | FALSE | 51.4435 | 0.35667 | SPN-S000000008470 | 389815147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
770 | 45.9 | FIVE ASH ROAD | GRAVESEND | DA11 0RE | Gravesham | CAUSEWAY STEEL PRODUCTS LTD | Factory And Premises | industrial | 1 | 2207.97 | 23766 | GIA | 121000 | ROSHERVILLE 33/6.6KV | inside-area | 0.55 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 3.51 | 132 | 14 | 1967090 | SPN-S000000311132 | 750 | 75 | 0-20% | ROSHERVILLE 33/6.6KV | 79 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4373 | 0.35192 | SPN-S000000008470 | 97783147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
771 | 45.9 | 1-2, TRANSIT WORKS, POWER STATION ROAD | SHEERNESS | ME12 3AD | Swale |  | Warehouse And Premises | industrial | 1 | 2030.83 | 21860 | GIA | 76500 | MINSTER 33/6.6KV | inside-area | 2.02 | Sheerness Grid | Kemsley | Mid Kent Zone | 4.4 | primary | 4.4 | Green | 13.8 | 9 | Thermal | 0 | 2.3 | 0 | 2.3 | 4.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 13.2 | 10.5 | Winter | 34.8485 | 4.6 | Green (Over 5% headroom) | 31373 | 100 | 3.23 | 51 | 1 | 42843 | SPN-S000000391543 | 500 | 250 | 40-60% | MINSTER 33/6.6KV | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062693971 | B1 Offices and Workshop businesses | 2567 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2015-02-13 |  | 0.8 | FALSE | 51.4275 | 0.77718 | SPN-S000000008436 | 11728633000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
772 | 45.9 | BRITISH TELECOMMUNICATIONS PLC, BROADWATER LANE | TUNBRIDGE WELLS | TN2 5RE | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1907.69 | 20534 | GIA | 147000 | TUNBRIDGE WELLS TOWN 11KV | inside-area | 2.36 | Tunbridge Wells Total | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 7.4 | 2.8 | Thermal | 0 | 5.6 | 0 | 5.6 | 4.1 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 7.2 | 6.5 | Winter | 62.5 | 4.5 | Green (Over 5% headroom) | 31373 | 100 | 3.03 | 48 | 2 | 157520 | SPN-S000000442324 | 500 | 250 | 40-60% | TUNBRIDGE WELLS TOWN 11KV | 168 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1214 | 0.25388 | SPN-S000000007371 | 8386715000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
773 | 45.7 | UNIT 1 & UNIT 2, NORFOLK ROAD | GRAVESEND | DA12 2PS | Gravesham |  | Factory And Premises | industrial | 1 | 6375 | 68620 | GIA | 307500 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.38 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 45 | 10.13 | 382 | 10 | 349306 | SPN-S000000312283 | 300 | 90 | 20-40% | GRAVESEND TOWN 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200002883428 | General Industrial and Special Industrial Groups | 990 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-08-02 |  | 1 | FALSE | 51.4414 | 0.38944 | SPN-S000000008409 | 7473661000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
774 | 45.7 | ALBION PARADE | GRAVESEND | DA12 2RN | Gravesham | AVENUE TRANSPORT; FEABREX LTD; GRAVESEND STEEL | Factory And Premises; Warehouse And Premises | industrial | 4 | 5607.82 | 60362 | GIA | 376000 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.18 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 51 | 8.91 | 336 | 10 | 357564 | SPN-S000000311733 | 800 | 560 | 60-80% | GRAVESEND TOWN 33/6.6KV | 27 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4431 | 0.38425 | SPN-S000000008409 | 7235926000;404860147;7235926000;2246258000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
775 | 45.7 | UNIT P & PT UNIT Q, FIRCROFT WAY | EDENBRIDGE | TN8 6EL | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 4901.97 | 52764 | GIA | 229000 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 58 | 7.79 | 123 | 9 | 199522 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002017298 | B8 Storage or Distribution | 1842 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-10-11 |  | 0.5 | FALSE | 51.2066 | 0.063969 | SPN-S000000008408 | 413727148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
776 | 45.7 | UNIT 2 AT 7, FIRCROFT WAY | EDENBRIDGE | TN8 6ER | Sevenoaks |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 3609.67 | 38854 | GIA | 280000 | FOUR ELMS 33/11KV | inside-area | 3.82 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 79 | 5.74 | 162 | 9 | 213432 | SPN-S000000441613 | 500 | 250 | 40-60% | FOUR ELMS 33/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2071 | 0.064837 | SPN-S000000008408 | 6935869000;7201685000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
777 | 45.7 | JUNIPER PLACE, FIRCROFT WAY | EDENBRIDGE | TN8 6EL | Sevenoaks |  | Warehouse And Premises | industrial | 2 | 3262.66 | 35119 | GIA | 228500 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 87 | 5.18 | 82 | 9 | 217167 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2066 | 0.063969 | SPN-S000000008408 | 6295776000;14113465000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
778 | 45.7 | UNIT D, FIRCROFT WAY | EDENBRIDGE | TN8 6EL | Sevenoaks |  | Factory And Premises | industrial | 1 | 2924.4 | 31478 | GIA | 162000 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 97 | 4.65 | 175 | 9 | 220808 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2066 | 0.063969 | SPN-S000000008408 | 2890415000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
779 | 45.7 | HYE OAK LTD, MARK LANE | GRAVESEND | DA12 2QB | Gravesham |  | Warehouse And Premises | industrial | 1 | 2292.78 | 24679 | GIA | 187000 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.84 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 3.64 | 57 | 10 | 393247 | SPN-S000000311311 | 500 | 350 | 60-80% | GRAVESEND TOWN 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4428 | 0.39588 | SPN-S000000008409 | 3731874000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
780 | 45.7 | UNIT 5B 6-8 AND 11-12, FIRCROFT BUSINESS CENTRE, FIRCROFT WAY | EDENBRIDGE | TN8 6EN | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1895.61 | 20404 | GIA | 139000 | FOUR ELMS 33/11KV | inside-area | 3.86 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 100 | 3.01 | 85 | 9 | 231882 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035185012 | B1 Offices and Workshop businesses | 535 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-06-12 |  | 1 | FALSE | 51.2064 | 0.064806 | SPN-S000000008408 | 14191654000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
781 | 45.3 | AFFINITY HOUSE, BEAUFORT COURT, SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4FD | Medway |  | Offices And Premises | office | 1 | 1714.6 | 18456 | NIA | 136000 | STROOD 132/11KV | inside-area | 1.77 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 2.72 | 120 | 62 | 3323002 | SPN-S000000312295 | 1000 | 500 | 40-60% | STROOD 132/11KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44027594 | Offices and Workshop Businesses | 1487 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-08-25 |  | 0.75 | FALSE | 51.39 | 0.51952 | SPN-S000000009948 | 10379080000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
782 | 45.3 | 3 & 4A & 6-8 & 12 &16, BEAUFORT COURT, CHRISTCHURCH HOUSE, SIR THOMAS LONGLEY ROAD | ROCHESTER | ME2 4DP | Medway |  | Offices And Premises | office | 1 | 1199.59 | 12912 | NIA | 85500 | STROOD 132/11KV | inside-area | 1.77 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.91 | 84 | 62 | 3328546 | SPN-S000000312295 | 1000 | 500 | 40-60% | STROOD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.39 | 0.51954 | SPN-S000000009948 | 14941902000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
783 | 45.3 | 165, HIGH STREET | ROCHESTER | ME1 1EH | Medway |  | Post Office And Premises | office | 1 | 1121.33 | 12070 | NIA | 75500 | STROOD 132/11KV | inside-area | 1.63 | STROOD 132/11KV | Kingsnorth | Mid Kent Zone | 16 | primary | 16 | Green | 60 | 43.9 | Thermal | 3 | 5.4 | 3.8 | 8.4 | 8.3 |  |  |  | 0 |  | RED | 3 | 60.6 | 0 | 57 | 57 | Winter | 26.8421 | 15.3 | Green (Over 5% headroom) | 114082 | 100 | 1.78 | 78 | 62 | 3329388 | SPN-S000000311620 | 750 | 375 | 40-60% | STROOD 132/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3862 | 0.50731 | SPN-S000000009948 | 166190147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
784 | 45.2 | LIBERTY HOUSE, THAMESPORT, GRAIN ROAD | ROCHESTER | ME3 0EP | Medway |  | Warehouse And Premises | industrial | 1 | 4190.53 | 45106 | GIA | 320000 | GRAIN 33/11KV | inside-area | 0.59 | Northfleet East | Northfleet | Mid Kent Zone | 3.9 | primary | 3.9 | Green | 7.3 | 3.4 | Voltage | 0 | 0 | 55 | 0 | 2.1 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 6.8 | 6.8 | Winter | 52.9412 | 3.6 | Green (Over 5% headroom) | 27807 | 62 | 6.66 | 105 | 2 | 436858 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 44016065 | B2 to B7 General Industrial and Special Industrial Groups | 3790 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-08-19 |  | 0.67 | FALSE | 51.4412 | 0.68581 | SPN-S000000008425 | 14043624000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
785 | 45.2 | SHED 2, THAMESPORT, GRAIN ROAD | ROCHESTER | ME3 0EP | Medway |  | Warehouse And Premises | industrial | 1 | 3780 | 40688 | GIA | 285000 | GRAIN 33/11KV | inside-area | 0.59 | Northfleet East | Northfleet | Mid Kent Zone | 3.9 | primary | 3.9 | Green | 7.3 | 3.4 | Voltage | 0 | 0 | 55 | 0 | 2.1 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 6.8 | 6.8 | Winter | 52.9412 | 3.6 | Green (Over 5% headroom) | 27807 | 68 | 6.01 | 94 | 2 | 441276 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 44041180 | B2 to B7 General Industrial and Special Industrial Groups | 3872 | C | Other | 3 |  | Unconditioned | 2019-08-13 |  | 1 | FALSE | 51.4412 | 0.68581 | SPN-S000000008425 | 9816405000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
786 | 44.7 | BRUNSWICK ROAD | ASHFORD | TN23 1EH | Ashford | METIISTO DESIGN LIMITED | Warehouse And Premises | industrial | 1 | 1660.55 | 17874 | GIA | 88000 | SINGLETON 33/6.6KV | inside-area | 0.73 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 2.64 | 42 | 24 | 730240 | SPN-S000000362211 | 500 | 350 | 60-80% | SINGLETON 33/6.6KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012870167 | B8 Storage or Distribution | 1573 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-04-11 |  | 1 | FALSE | 51.1494 | 0.85636 | SPN-S000000008610 | 10471973000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
787 | 44.7 | BRUNSWICK ROAD | ASHFORD | TN23 1EL | Ashford | DONALDSON TIMBER ENGINEERING (SE) | Factory And Premises | industrial | 1 | 1647.77 | 17736 | GIA | 127000 | SINGLETON 33/6.6KV | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 2.62 | 99 | 24 | 730378 | SPN-S000000361812 | 1000 | 500 | 40-60% | SINGLETON 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200001522670 | B2 to B7 General Industrial and Special Industrial Groups | 1898 | C | Oil | 3 |  | Heating and Natural Ventilation | 2021-03-06 |  | 1 | FALSE | 51.1493 | 0.85381 | SPN-S000000008610 | 1659139000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
788 | 44.7 | UNIT 4 BROOKFIELD INDUSTRIAL ESTATE, LEACON ROAD | ASHFORD | TN23 4TU | Ashford |  | Warehouse And Premises | industrial | 1 | 1374.72 | 14797 | GIA | 132000 | SINGLETON 33/6.6KV | inside-area | 0.63 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 2.18 | 34 | 24 | 733317 | SPN-S000000363944 | 1000 | 700 | 60-80% | SINGLETON 33/6.6KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | B8 Storage or Distribution | 3848 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-11-03 |  | 1 | FALSE | 51.1467 | 0.85614 | SPN-S000000008610 | 15114066000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
789 | 44.7 | UNITS 5 & 6, BRUNSWICK INDUSTRIAL CENTRE, BRUNSWICK ROAD | ASHFORD | TN23 1ED | Ashford |  | Warehouse And Premises | industrial | 1 | 1281.6 | 13795 | GIA | 92000 | SINGLETON 33/6.6KV | inside-area | 0.78 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 2.04 | 32 | 24 | 734319 | SPN-S000000363754 | 300 | 150 | 40-60% | SINGLETON 33/6.6KV | 25 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012862116 | B8 Storage or Distribution | 1339 | D | Grid Supplied Electricity | 5 |  | Heating and Mechanical Ventilation | 2020-10-23 |  | 1 | FALSE | 51.1491 | 0.8575 | SPN-S000000008610 | 14705239000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
790 | 44.7 | UNITS 4 & 5, FAIRWOOD INDUSTRIAL PARK, LEACON ROAD | ASHFORD | TN23 4FB | Ashford |  | Warehouse And Premises | industrial | 1 | 1259.39 | 13556 | GIA | 104000 | SINGLETON 33/6.6KV | inside-area | 0.88 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 2 | 31 | 24 | 734558 | SPN-S000000371066 | 1000 | 900 | 80-100% | SINGLETON 33/6.6KV | 34 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062559305 | B8 Storage or Distribution | 2498 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-05-31 |  | 0.5 | FALSE | 51.147 | 0.8597 | SPN-S000000008610 | 13778849000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
791 | 44.7 | UNIT 6, ST GEORGES BUSINESS CENTRE, BRUNSWICK ROAD | ASHFORD | TN23 1EL | Ashford |  | Warehouse And Premises | industrial | 1 | 1181.5 | 12718 | GIA | 77000 | SINGLETON 33/6.6KV | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 1.88 | 30 | 24 | 735396 | SPN-S000000361812 | 1000 | 500 | 40-60% | SINGLETON 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1493 | 0.85381 | SPN-S000000008610 | 330650148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
792 | 44.7 | CHART HOUSE, DENCORA WAY | ASHFORD | TN23 4FH | Ashford |  | Workshop And Premises | industrial | 1 | 1081 | 11636 | GIA | 98500 | SINGLETON 33/6.6KV | inside-area | 0.86 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 1.72 | 49 | 24 | 736478 | SPN-S000000364587 | 800 | 560 | 60-80% | SINGLETON 33/6.6KV | 41 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012843527 | B2 to B7 General Industrial and Special Industrial Groups | 1198 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2021-07-06 |  | 1 | FALSE | 51.1463 | 0.85945 | SPN-S000000008610 | 4067589000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
793 | 44.7 | 1, VICTORIA ROAD | ASHFORD | TN23 7HE | Ashford |  | Warehouse And Premises | industrial | 1 | 1073.2 | 11552 | GIA | 109000 | SINGLETON 33/6.6KV | inside-area | 1.53 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 1.71 | 27 | 24 | 736562 | SPN-S000000363367 | 315 | 94 | 20-40% | SINGLETON 33/6.6KV | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004392088 | B8 Storage or Distribution | 1134 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-10-22 |  | 1 | FALSE | 51.1448 | 0.86896 | SPN-S000000008610 | 9334978000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
794 | 44.7 | ASHFORD RECOVERY LTD, CARLTON ROAD | ASHFORD | TN23 1DP | Ashford |  | Workshop And Premises | industrial | 1 | 1034.7 | 11137 | GIA | 72000 | SINGLETON 33/6.6KV | inside-area | 0.91 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 1.64 | 47 | 24 | 736977 | SPN-S000000371615 | 1000 | 700 | 60-80% | SINGLETON 33/6.6KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.15 | 0.8588 | SPN-S000000008610 | 988386000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
795 | 44.6 | TESCO, BRIDGE ROAD | SHEERNESS | ME12 1RH | Swale |  | Superstore And Premises | bigbox | 1 | 6682.08 | 71925 | GIA | 1590000 | SHEERNESS 33/6.6KV | inside-area | 0.74 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 71 | 10.62 | 601 | 19 | 757219 | SPN-S000000391501 | 800 | 400 | 40-60% | SHEERNESS 33/6.6KV | 145 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062377174 | A1/A2 Retail and Financial/Professional services | 7131 | C | Natural Gas | 3 |  | Air Conditioning | 2019-03-29 |  | 1 | FALSE | 51.4413 | 0.7574 | SPN-S000000008483 | 10911711000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
796 | 44.5 | DAVID LLOYD LEISURE 21, KINGS HILL AVENUE | WEST MALLING | ME19 4UA | Tonbridge & Malling |  | Leisure Centre And Premises | bigbox | 1 | 8403.7 | 90457 | GIA | 510000 | MEREWORTH 33/11KV | inside-area | 2.87 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 56 | 13.35 | 672 | 30 | 913889 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002912733 | General Assembly and Leisure, Night Clubs, and Theatres | 22786 | C | Natural Gas | 3 |  | Air Conditioning | 2023-12-07 |  | 1 | FALSE | 51.2765 | 0.39436 | SPN-S000000008643 | 8601583000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
797 | 44.5 | 1, ALEXANDER GROVE, KINGS HILL | WEST MALLING | ME19 4SZ | Tonbridge & Malling |  | Superstore And Premises | bigbox | 1 | 6174.43 | 66461 | GIA | 1620000 | MEREWORTH 33/11KV | inside-area | 2.91 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 76 | 9.81 | 556 | 30 | 937885 | SPN-S000000394727 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 43 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000966571 | Retail/Financial and Professional Services | 6213 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-05-23 |  | 1 | FALSE | 51.2725 | 0.40226 | SPN-S000000008643 | 9012232000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
798 | 44.5 | SEVEN MILE LANE | TONBRIDGE | TN12 5JG | Tonbridge & Malling | BROOKSIDE NURSERIES | Garden Centre And Premises | bigbox | 1 | 3941.1 | 42422 | GIA | 67000 | MEREWORTH 33/11KV | inside-area | 4 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 6.26 | 355 | 30 | 961924 | SPN-R000000864308-000-041Z | 100 | -10 | -20-0% | MEREWORTH 33/11KV | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062545163 | B1 Offices and Workshop businesses | 61 | A+ | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-07-24 |  | 1 | FALSE | 51.2219 | 0.39245 | SPN-S000000008643 | 136888148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
799 | 44.3 | LUNSFORD DISTRICT CENTRE | AYLESFORD | ME20 6SR | Tonbridge & Malling | TESCO | Superstore And Premises | bigbox | 1 | 8417.13 | 90601 | GIA | 2220000 | AYLESFORD 33/6.6KV | inside-area | 2.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 55 | 13.38 | 758 | 85 | 4975093 | SPN-S000000393817 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3108 | 0.44058 | SPN-S000000008312 | 13269740000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
800 | 44.3 | SAINSBURYS, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Superstore And Premises | bigbox | 1 | 6879.5 | 74050 | GIA | 2030000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 67 | 10.93 | 619 | 85 | 4991644 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2915 | 0.47299 | SPN-S000000008312 | 15045763000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
801 | 44.3 | UNIT 1, SOUTH AYLESFORD RETAIL PARK, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7TP | Tonbridge & Malling |  | Retail Warehouse And Premises | bigbox | 2 | 6686.11 | 71969 | GIA | 1215000 | AYLESFORD 33/6.6KV | inside-area | 0.77 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 69 | 10.62 | 602 | 85 | 4993725 | SPN-S000000394150 | 800 | 560 | 60-80% | AYLESFORD 33/6.6KV | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002916171 | A1/A2 Retail and Financial/Professional services | 4650 | B | Natural Gas | 4 |  | Heating and Natural Ventilation | 2020-11-11 |  | 1 | FALSE | 51.294 | 0.46985 | SPN-S000000008312 | 8271450000;8271458000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
802 | 44.3 | LONDON ROAD | AYLESFORD | ME20 6HJ | Tonbridge & Malling | B & Q RETAIL LTD | Retail Warehouse And Premises | bigbox | 1 | 3539.2 | 38096 | GIA | 395000 | AYLESFORD 33/6.6KV | inside-area | 1.93 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 5.62 | 319 | 85 | 5027598 | SPN-S000000394400 | 315 | 220 | 60-80% | AYLESFORD 33/6.6KV | 157 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000960312 | C1 Hotels | 2566 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2012-09-09 |  | 1 | FALSE | 51.2987 | 0.43969 | SPN-S000000008312 | 71419148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
803 | 44.3 | PERFORMANCE HOUSE, FORSTAL ROAD | AYLESFORD | ME20 7XA | Maidstone |  | Car Showroom And Premises | bigbox | 1 | 3138.75 | 33785 | GIA | 455000 | AYLESFORD 33/6.6KV | inside-area | 2.04 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 4.99 | 282 | 85 | 5031909 | SPN-S000000392466 | 800 | 560 | 60-80% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10014306465 | A1/A2 Retail and Financial/Professional services | 3166 | C | Natural Gas | 3 | 2 | Air Conditioning | 2017-04-03 |  | 1 | FALSE | 51.3007 | 0.49664 | SPN-S000000008312 | 7593454000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
804 | 44.3 | TRAVIS PERKINS, FORSTAL ROAD | AYLESFORD | ME20 7AG | Maidstone |  | Builders Merchants And Premises | bigbox | 1 | 2256.89 | 24293 | GIA | 452500 | AYLESFORD 33/6.6KV | inside-area | 2.16 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 3.59 | 203 | 85 | 5041401 | SPN-S000000392466 | 800 | 560 | 60-80% | AYLESFORD 33/6.6KV | 134 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003662521 | B8 Storage or Distribution | 2143 | B | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2012-12-14 |  | 1 | FALSE | 51.2994 | 0.49835 | SPN-S000000008312 | 11217697000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
805 | 44.2 | 83-91, MAIN ROAD | DARTFORD | DA4 9HQ | Dartford |  | Showroom And Premises | bigbox | 1 | 2828 | 30440 | NIA | 131000 | FARNINGHAM 33/11KV | inside-area | 3.24 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 4.49 | 255 | 7 | 241568 | SPN-S000000316031 | 500 | 250 | 40-60% | FARNINGHAM 33/11KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000543296 | B1 Offices and Workshop businesses | 1713 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-05-12 |  | 0.67 | FALSE | 51.4089 | 0.23737 | SPN-S000000008403 | 23898147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
806 | 44.1 | LIDL FOOD STORE, HAVEN DRIVE | FOLKESTONE | CT18 7RH | Folkestone & Hythe |  | Superstore And Premises | bigbox | 1 | 2627.16 | 28278 | GIA | 590000 | FOLKESTONE EAST 33/11KV | inside-area | 3.35 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 100 | 4.17 | 236 | 7 | 322932 | SPN-S000000371457 | 1000 | 900 | 80-100% | FOLKESTONE EAST 33/11KV | 268 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50107213 | A1/A2 Retail and Financial/Professional services | 2833 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2017-08-10 |  | 0.5 | FALSE | 51.1124 | 1.1601 | SPN-S000000008660 | 11137699000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
807 | 44.1 | PT GND FLR & PT 1ST FLR RHS AT FRASER HOUSE, HENWOOD INDUSTRIAL ESTATE | ASHFORD | TN24 8DR | Ashford |  | Workshop And Premises | industrial | 1 | 5046.72 | 54322 | GIA | 241000 | ASHFORD EAST 33/11KV | inside-area | 1.07 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 41 | 8.02 | 227 | 27 | 1910765 | SPN-S000000371274 | 500 | 150 | 20-40% | ASHFORD EAST 33/11KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848129 | B1 Offices and Workshop businesses | 4979 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2017-03-27 |  | 0.67 | FALSE | 51.1526 | 0.88315 | SPN-S000000008402 | 12331784000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
808 | 44.1 | UNIT 6 AT, VANGUARD INDUSTRIAL ESTATE, HENWOOD | ASHFORD | TN24 8DH | Ashford |  | Warehouse And Premises | industrial | 2 | 4444.39 | 47839 | GIA | 335000 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 46 | 7.06 | 111 | 27 | 1917248 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848698 | B1 Offices and Workshop businesses | 570 | C | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2018-08-17 |  | 1 | FALSE | 51.1507 | 0.88453 | SPN-S000000008402 | 12805221000;12805220000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
809 | 44.1 | LOW BAY WAREHOUSE UNIT 15, HENWOOD INDUSTRIAL ESTATE | ASHFORD | TN24 8DH | Ashford |  | Warehouse And Premises | industrial | 1 | 3246.04 | 34940 | GIA | 195000 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 63 | 5.16 | 81 | 27 | 1930147 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848698 | B1 Offices and Workshop businesses | 570 | C | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2018-08-17 |  | 1 | FALSE | 51.1507 | 0.88453 | SPN-S000000008402 | 15050929000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
810 | 44.1 | UNIT 3, VANGUARD INDUSTRIAL ESTATE, HENWOOD | ASHFORD | TN24 8DH | Ashford |  | Factory And Premises; Warehouse And Premises | industrial | 2 | 3045.6 | 32783 | GIA | 222500 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 67 | 4.84 | 183 | 27 | 1932304 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848698 | B1 Offices and Workshop businesses | 570 | C | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2018-08-17 |  | 1 | FALSE | 51.1507 | 0.88453 | SPN-S000000008402 | 7957970000;7757005000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
811 | 44.1 | UNIT 7, WYVERN WAY, HENWOOD INDUSTRIAL ESTATE | ASHFORD | TN24 8DW | Ashford |  | Warehouse And Premises | industrial | 1 | 2531 | 27243 | GIA | 179000 | ASHFORD EAST 33/11KV | inside-area | 0.94 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 81 | 4.02 | 63 | 27 | 1937844 | SPN-S000000364093 | 315 | 158 | 40-60% | ASHFORD EAST 33/11KV | 10 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Offices and Workshop Businesses | 2279 | D | LPG | 3 | 2 | Heating and Natural Ventilation | 2026-06-12 |  | 1 | FALSE | 51.1505 | 0.88707 | SPN-S000000008402 | 8151743000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
812 | 44.1 | UNITS 1A & A1-A6, BILTING BUSINESS CENTRE, CANTERBURY ROAD | ASHFORD | TN25 4HF | Ashford |  | Warehouse And Premises | industrial | 1 | 2310.2 | 24867 | GIA | 76500 | ASHFORD EAST 33/11KV | inside-area | 6.6 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 89 | 3.67 | 58 | 27 | 1940220 | SPN-R000000856010-000-049Z | 200 | 140 | 60-80% | CHARTHAM 33/11KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.208 | 0.94246 | SPN-S000000008402 | 9346389000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
813 | 44.1 | ASHFORD HIGHWAYS DEPOT 4, JAVELIN WAY | ASHFORD | TN24 8AD | Ashford |  | Storage Depot And Premises | industrial | 1 | 2078.4 | 22372 | GIA | 166000 | ASHFORD EAST 33/11KV | inside-area | 0.87 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 99 | 3.3 | 52 | 27 | 1942715 | SPN-S000000364093 | 315 | 158 | 40-60% | ASHFORD EAST 33/11KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1507 | 0.88813 | SPN-S000000008402 | 15116013000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
814 | 44.1 | UNIT 18, HENWOOD INDUSTRIAL ESTATE | ASHFORD | TN24 8DH | Ashford |  | Warehouse And Premises | industrial | 1 | 1926.65 | 20738 | GIA | 153000 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 3.06 | 48 | 27 | 1944349 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012881406 | B2 to B7 General Industrial and Special Industrial Groups | 1471 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2016-02-12 |  | 1 | FALSE | 51.1507 | 0.88453 | SPN-S000000008402 | 2330839000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
815 | 44 | UNIT 10, HAWKHURST STATION BUSINESS PARK, GILLS GREEN | CRANBROOK | TN18 5BD | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 2634.81 | 28361 | GIA | 200000 | HAWKHURST 33/11KV | inside-area | 1.34 | Hartley Grid | Ninfield | East Sussex Zone | 3 | primary | 3 | Green | 15 | 10 | Thermal | 0 | 0 | 0 | 0 | 3.8 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 14.1 | 10.6 | Summer | 31.1321 | 3.3 | Green (Over 5% headroom) | 21390 | 75 | 4.19 | 66 | 3 | 86190 | SPN-S000000451541 | 800 | 400 | 40-60% | HAWKHURST 33/11KV | 43 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10000071833 | B2 to B7 General Industrial and Special Industrial Groups | 2350 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2021-04-20 |  | 1 | FALSE | 51.0638 | 0.50589 | SPN-S000000008363 | 10670301000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
816 | 44 | CRANBROOK ROAD | CRANBROOK | TN18 5HB | Tunbridge Wells | AUSCOT HOLDINGS LTD | Cold Stores & Premises | industrial | 1 | 2385.66 | 25679 | GIA | 207000 | HAWKHURST 33/11KV | inside-area | 1.31 | Hartley Grid | Ninfield | East Sussex Zone | 3 | primary | 3 | Green | 15 | 10 | Thermal | 0 | 0 | 0 | 0 | 3.8 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 14.1 | 10.6 | Summer | 31.1321 | 3.3 | Green (Over 5% headroom) | 21390 | 83 | 3.79 | 286 | 3 | 88872 | SPN-S000000451541 | 800 | 400 | 40-60% | HAWKHURST 33/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.0636 | 0.50619 | SPN-S000000008363 | 540490000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
817 | 44 | PART WAREHOUSE OLD RIDES FARM, LOWER ROAD | SHEERNESS | ME12 4BD | Swale |  | Warehouse And Premises | industrial | 1 | 1923.9 | 20709 | GIA | 84000 | EASTCHURCH PRISON 33/6.6KV | inside-area | 1.81 | Sheerness Grid | Kemsley | Mid Kent Zone | 3 | primary | 3 | Green | 10 | 5.7 | Thermal | 0 | 0 | 12 | 0 | 2.2 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 9.3 | 7 | Winter | 43.0108 | 4 | Green (Over 5% headroom) | 21390 | 100 | 3.06 | 48 | 1 | 43057 | SPN-S000000400411 | 500 | 450 | 80-100% | EASTCHURCH PRISON 33/6.6KV | 259 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3998 | 0.87825 | SPN-S000000008587 | 12580653000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
818 | 43.9 | TESCO STORES LTD, AISHER WAY | SEVENOAKS | TN13 2QS | Sevenoaks |  | Superstore And Premises | bigbox | 1 | 8016.41 | 86288 | GIA | 2090000 | SUNDRIDGE 33/11KV | inside-area | 2.41 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 55 | 12.74 | 721 | 9 | 218147 | SPN-S000000444631 | 500 | 150 | 20-40% |  | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062547936 | A1/A2 Retail and Financial/Professional services | 8064 | C | Natural Gas | 4 |  | Air Conditioning | 2021-06-23 |  | 0.67 | FALSE | 51.2898 | 0.16478 | SPN-S000000008496 | 10168230000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
819 | 43.9 | 58, HIGH STREET | SEVENOAKS | TN13 1JR | Sevenoaks |  | Superstore And Premises | bigbox | 1 | 4262.76 | 45884 | GIA | 1020000 | SUNDRIDGE 33/11KV | inside-area | 4.3 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 6.77 | 384 | 9 | 258551 | SPN-S000000446618 | 1000 | 500 | 40-60% |  | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062547086 | A1/A2 Retail and Financial/Professional services | 3194 | C | Natural Gas | 4 | 2 | Air Conditioning | 2022-02-01 |  | 1 | FALSE | 51.2697 | 0.19337 | SPN-S000000008496 | 7898347000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
820 | 43.8 | WYEVALE GARDEN CENTRE, MAIDSTONE ROAD | TONBRIDGE | TN12 6QJ | Tunbridge Wells |  | Garden Centre And Premises | bigbox | 1 | 7513.3 | 80872 | GIA | 87500 | PADDOCK WOOD 33/11KV | inside-area | 1.58 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 58 | 11.94 | 676 | 38 | 1850244 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1916 | 0.3931 | SPN-S000000008454 | 12555375000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
821 | 43.8 | WAITROSE, CHURCH ROAD | TONBRIDGE | TN12 6EX | Tunbridge Wells |  | Superstore And Premises | bigbox | 1 | 3019.81 | 32505 | GIA | 600000 | PADDOCK WOOD 33/11KV | inside-area | 0.27 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 4.8 | 272 | 38 | 1898611 | SPN-S000000441553 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062545581 | A1/A2 Retail and Financial/Professional services | 3018 | C | Natural Gas | 3 | 2 | Heating and Mechanical Ventilation | 2020-05-16 |  | 1 | FALSE | 51.1799 | 0.39326 | SPN-S000000008454 | 9268285000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
822 | 43.7 | DEPARTMENT OF WORK AND PENSIONS, MILL LANE HOUSE, MILL LANE | MARGATE | CT9 1LB | Thanet |  | Offices And Premises | office | 1 | 1123.86 | 12097 | NIA | 81500 | MARGATE 33/11KV | inside-area | 0.6 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 1.79 | 79 | 24 | 552514 | SPN-S000000341988 | 1000 | 500 | 40-60% | MARGATE 33/11KV | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062306099 | B1 Offices and Workshop businesses | 4626 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-11-23 |  | 1 | FALSE | 51.3858 | 1.3827 | SPN-S000000008655 | 7189964000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
823 | 43.7 | HAECKELS, ZION PLACE | MARGATE | CT9 1RP | Thanet |  | Offices And Premises | office | 1 | 1075.85 | 11580 | NIA | 124000 | MARGATE 33/11KV | inside-area | 1.33 | Thanet Grid | Richborough | East Kent Zone | 14.8 | primary | 14.8 | Green | 37.1 | 18.8 | Thermal | 0 | 0 | 0 | 0 | 15.8 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 36.4 | 27.6 | Winter | 49.4505 | 18 | Green (Over 5% headroom) | 105526 | 100 | 1.71 | 75 | 24 | 553031 | SPN-S000000341961 | 500 | 50 | 0-20% | THANET 33/11KV | 103 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3913 | 1.3888 | SPN-S000000008655 | 14295562000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
824 | 43.5 | ASDA 387, MAIDSTONE ROAD | CHATHAM | ME5 9SE | Medway |  | Superstore And Premises | bigbox | 1 | 10571.69 | 113793 | GIA | 1950000 | MEDWAY 33/11KV | inside-area | 3.38 | Medway Grid | Kingsnorth | Mid Kent Zone | 6.4 | primary | 6.4 | Green | 22.8 | 16.5 | Thermal | 0 | 0 | 0 | 0 | -2.4 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 21.9 | 16.6 | Winter | 27.8539 | 6.1 | Green (Over 5% headroom) | 45633 | 40 | 16.8 | 951 | 4 | 192367 | SPN-S000000312162 | 300 | 210 | 60-80% | MEDWAY 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062393395 | A1/A2 Retail and Financial/Professional services | 8718 | C | Natural Gas | 3 |  | Heating and Mechanical Ventilation | 2016-03-11 |  | 1 | FALSE | 51.3472 | 0.50836 | SPN-S000000008333 | 13014639000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
825 | 43.5 | UNIT D, HORSTED RETAIL PARK, MAIDSTONE ROAD | CHATHAM | ME5 9SQ | Medway |  | Retail Warehouse And Premises | bigbox | 1 | 4225.13 | 45479 | GIA | 570000 | MEDWAY 33/11KV | inside-area | 3.24 | Medway Grid | Kingsnorth | Mid Kent Zone | 6.4 | primary | 6.4 | Green | 22.8 | 16.5 | Thermal | 0 | 0 | 0 | 0 | -2.4 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 21.9 | 16.6 | Winter | 27.8539 | 6.1 | Green (Over 5% headroom) | 45633 | 100 | 6.71 | 380 | 4 | 260681 | SPN-S000000324605 | 1000 | 500 | 40-60% | MEDWAY 33/11KV | 165 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062393296 | Retail/Financial and Professional Services | 4202 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-07-10 |  | 1 | FALSE | 51.3522 | 0.50712 | SPN-S000000008333 | 165135147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
826 | 43.5 | UNIT A, HORSTED RETAIL PARK, MAIDSTONE ROAD | CHATHAM | ME5 9SQ | Medway |  | Retail Warehouse And Premises | bigbox | 1 | 3599.36 | 38743 | GIA | 595000 | MEDWAY 33/11KV | inside-area | 3.24 | Medway Grid | Kingsnorth | Mid Kent Zone | 6.4 | primary | 6.4 | Green | 22.8 | 16.5 | Thermal | 0 | 0 | 0 | 0 | -2.4 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 21.9 | 16.6 | Winter | 27.8539 | 6.1 | Green (Over 5% headroom) | 45633 | 100 | 5.72 | 324 | 4 | 267417 | SPN-S000000324605 | 1000 | 500 | 40-60% | MEDWAY 33/11KV | 165 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062393384 | A1/A2 Retail and Financial/Professional services | 4725 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2018-03-09 |  | 0.75 | FALSE | 51.3522 | 0.50712 | SPN-S000000008333 | 165133147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
827 | 43.5 | 448, MAIDSTONE ROAD | CHATHAM | ME5 9QL | Tonbridge & Malling |  | Car Supermarket And Premises | bigbox | 1 | 2351.75 | 25314 | GIA | 625000 | MEDWAY 33/11KV | inside-area | 3.65 | Medway Grid | Kingsnorth | Mid Kent Zone | 6.4 | primary | 6.4 | Green | 22.8 | 16.5 | Thermal | 0 | 0 | 0 | 0 | -2.4 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 21.9 | 16.6 | Winter | 27.8539 | 6.1 | Green (Over 5% headroom) | 45633 | 100 | 3.74 | 212 | 4 | 280846 | SPN-S000000311639 | 500 | 250 | 40-60% | MEDWAY 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3354 | 0.50539 | SPN-S000000008333 | 11556071000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
828 | 43.5 | WOTTON ROAD | ASHFORD | TN23 6LL | Ashford | LOK N STORE LTD | Factory And Premises; Warehouse And Premises | industrial | 3 | 10162.9 | 109392 | GIA | 580000 | ASHFORD CENTRAL | inside-area | 1.48 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 17 | 16.15 | 610 | 36 | 858846 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062618353 | B1 Offices and Workshop businesses | 195 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-04-05 |  | 1 | FALSE | 51.1321 | 0.86713 | SPN-S000000008302 | 2768419000;5910912000;2768419000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
829 | 43.5 | KENT SPACE AT UNIT 1, KINGSNORTH INDUSTRIAL ESTATE, WOTTON ROAD | ASHFORD | TN23 6LN | Ashford |  | Warehouse, Meeting Rooms And Premises | industrial | 1 | 6211.13 | 66856 | GIA | 290000 | ASHFORD CENTRAL | inside-area | 1.45 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 28 | 9.87 | 155 | 36 | 901382 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062559492 | B1 Offices and Workshop businesses | 7087 | C | Grid Supplied Electricity | 4 |  | Air Conditioning | 2018-03-27 |  | 0.6 | FALSE | 51.1323 | 0.86737 | SPN-S000000008302 | 9895331000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
830 | 43.5 | 3-8, MACE LANE | ASHFORD | TN24 8EP | Ashford |  | Factory And Premises; Warehouse And Premises; Workshop And Premises | industrial | 3 | 5497.68 | 59176 | GIA | 433000 | ASHFORD CENTRAL | inside-area | 0.96 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 31 | 8.74 | 330 | 36 | 909062 | SPN-S000000361013 | 500 | 350 | 60-80% | ASHFORD CENTRAL | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Storage or Distribution | 528 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-07 |  | 1 | FALSE | 51.1514 | 0.87791 | SPN-S000000008302 | 5029371000;380821148;329122148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
831 | 43.5 | 25-35, ELLINGHAM WAY | ASHFORD | TN23 6NF | Ashford |  | Factory And Premises | industrial | 1 | 3101.7 | 33386 | GIA | 220000 | ASHFORD CENTRAL | inside-area | 1.99 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 56 | 4.93 | 186 | 36 | 934852 | SPN-S000000364140 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.128 | 0.86147 | SPN-S000000008302 | 328056148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
832 | 43.5 | C-SCOPE INTERNATIONAL LTD PRECISION HOUSE, WOTTON ROAD | ASHFORD | TN23 6LN | Ashford |  | Factory And Premises | industrial | 1 | 2913.4 | 31360 | GIA | 157000 | ASHFORD CENTRAL | inside-area | 1.45 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 59 | 4.63 | 175 | 36 | 936878 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1323 | 0.86737 | SPN-S000000008302 | 13576062000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
833 | 43.5 | UNIT 22A, WOTTON ROAD | ASHFORD | TN23 6LW | Ashford |  | Warehouse And Premises | industrial | 2 | 2870.6 | 30899 | GIA | 231000 | ASHFORD CENTRAL | inside-area | 1.4 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 60 | 4.56 | 72 | 36 | 937339 | SPN-S000000362128 | 500 | 250 | 40-60% | SINGLETON 33/6.6KV | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012872774 | B1 Offices and Workshop businesses | 1167 | C | Grid Supplied Electricity | 3 | 3 | Air Conditioning | 2014-06-01 |  | 0.5 | FALSE | 51.1327 | 0.86671 | SPN-S000000008302 | 85974000;85974000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
834 | 43.5 | UNIT 3C, OLD RAILWAY WORKS, NEWTOWN ROAD | ASHFORD | TN24 0PN | Ashford |  | Store And Premises | industrial | 1 | 2731.7 | 29404 | GIA | 33500 | ASHFORD CENTRAL | inside-area | 1.01 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 63 | 4.34 | 68 | 36 | 938834 | SPN-S000000371059 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 134 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1398 | 0.87963 | SPN-S000000008302 | 538625145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
835 | 43.5 | UNITS 10 12 & 14-15, WOTTON TRADING ESTATE, WOTTON ROAD | ASHFORD | TN23 6JS | Ashford |  | Warehouse And Premises | industrial | 2 | 2342 | 25209 | GIA | 158000 | ASHFORD CENTRAL | inside-area | 1.49 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 74 | 3.72 | 59 | 36 | 943029 | SPN-S000000362128 | 500 | 250 | 40-60% | SINGLETON 33/6.6KV | 130 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.132 | 0.86562 | SPN-S000000008302 | 15164698000;15160176000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
836 | 43.5 | BERGEN LIMITED, WOTTON ROAD | ASHFORD | TN23 6LL | Ashford |  | Warehouse And Premises | industrial | 1 | 2315.3 | 24922 | GIA | 150000 | ASHFORD CENTRAL | inside-area | 1.48 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 74 | 3.68 | 58 | 36 | 943316 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1321 | 0.86713 | SPN-S000000008302 | 14555975000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
837 | 43.5 | ASHFORD SORTING CENTRE, TANNERY LANE | ASHFORD | TN23 1PL | Ashford | POST OFFICE | Sorting Office And Premises | industrial | 1 | 2269.8 | 24432 | GIA | 158000 | ASHFORD CENTRAL | inside-area | 0.61 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 76 | 3.61 | 159 | 36 | 943806 | SPN-S000000361974 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1467 | 0.87655 | SPN-S000000008302 | 212231148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
838 | 43.5 | INCA HOUSE, WOTTON ROAD | ASHFORD | TN23 6LL | Ashford |  | Workshop And Premises | industrial | 1 | 2114.57 | 22761 | GIA | 156000 | ASHFORD CENTRAL | inside-area | 1.48 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 81 | 3.36 | 95 | 36 | 945477 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012842131 | Storage or Distribution | 2095 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-02-02 |  | 1 | FALSE | 51.1321 | 0.86713 | SPN-S000000008302 | 2971187000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
839 | 43.4 | LANCASTER LAND ROVER, WOODGATE WAY | TONBRIDGE | TN11 0FU | Tonbridge & Malling |  | Car Showroom And Premises | bigbox | 1 | 4260.21 | 45856 | GIA | 835000 | TONBRIDGE EAST 33/6.6KV | inside-area | 2.34 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 98 | 6.77 | 383 | 23 | 896888 | SPN-S000000451612 | 500 | 350 | 60-80% | TONBRIDGE EAST 33/6.6KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002910421 | A1/A2 Retail and Financial/Professional services | 4185 | A | Natural Gas | 5 | 2 | Heating and Natural Ventilation | 2018-11-14 |  | 1 | FALSE | 51.1849 | 0.28953 | SPN-S000000008503 | 11768973000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
840 | 43.4 | WAITROSE, SOVEREIGN WAY | TONBRIDGE | TN9 1RG | Tonbridge & Malling |  | Superstore And Premises | bigbox | 1 | 4173.3 | 44921 | GIA | 915000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.81 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 6.63 | 376 | 23 | 897823 | SPN-S000000441164 | 500 | 250 | 40-60% | TONBRIDGE TOWN 33/6.6KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002917832 | Retail/Financial and Professional Services | 4591 | C | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2026-02-03 |  | 1 | FALSE | 51.1942 | 0.27579 | SPN-S000000008503 | 2720168000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
841 | 43.4 | PORSCHE CENTRE TONBRIDGE, BROOK FARM, FIVE OAK GREEN ROAD | TONBRIDGE | TN11 0QN | Tunbridge Wells |  | Car Showroom And Premises | bigbox | 1 | 3498.98 | 37663 | GIA | 505000 | TONBRIDGE EAST 33/6.6KV | inside-area | 2.17 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 5.56 | 315 | 23 | 905081 | SPN-R000000850303-000-001Z | 315 | 94 | 20-40% | TONBRIDGE EAST 33/6.6KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065647 | Retail/Financial and Professional Services | 2057 | D | Natural Gas | 4 |  | Air Conditioning | 2023-06-16 |  | 0.57 | FALSE | 51.1863 | 0.29284 | SPN-S000000008503 | 3754213000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
842 | 43.4 | 19, VALE RISE | TONBRIDGE | TN9 1SW | Tonbridge & Malling |  | Car Showroom And Premises | bigbox | 1 | 2834.9 | 30515 | GIA | 515000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.35 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 4.5 | 255 | 23 | 912229 | SPN-S000000443659 | 800 | 400 | 40-60% | TONBRIDGE EAST 33/6.6KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962079 | General Industrial and Special Industrial Groups | 881 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-06-05 |  | 0.5 | FALSE | 51.1944 | 0.28726 | SPN-S000000008503 | 4281490000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
843 | 43.4 | VOLVO CARS TONBRIDGE, VALE RISE | TONBRIDGE | TN9 1TB | Tonbridge & Malling |  | Car Showroom And Premises | bigbox | 1 | 2132.92 | 22959 | GIA | 442500 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.75 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 3.39 | 192 | 23 | 919785 | SPN-S000000443043 | 800 | 720 | 80-100% | TONBRIDGE EAST 33/6.6KV | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062594127 | B1 Offices and Workshop businesses | 958 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2016-06-06 |  | 0.67 | FALSE | 51.1903 | 0.28924 | SPN-S000000008503 | 12670852000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
844 | 43.3 | HOME ORCHARD | DARTFORD | DA1 1BA | Dartford | BRITISH TELECOM | Offices And Premises | office | 1 | 1486.9 | 16005 | NIA | 180000 | DARTFORD GRID B 11KV | inside-area | 0.65 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.36 | 104 | 54 | 2756744 | LPN-S000000073819 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4449 | 0.21751 | LPN-S000000000716 | 168167147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
845 | 43.3 | GND FLR WORKSHOP & 1ST FLR REAR, HAWLEY MILL, HAWLEY ROAD | DARTFORD | DA2 7SY | Dartford |  | Offices And Premises | office | 1 | 1464.06 | 15759 | NIA | 151000 | DARTFORD GRID B 11KV | inside-area | 3.21 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.33 | 102 | 54 | 2756990 | SPN-S000000316039 | 315 | 158 | 40-60% | DARTFORD 132/11KV | 129 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4238 | 0.23281 | LPN-S000000000716 | 12445636000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
846 | 43.3 | GND FLR REAR, HAWLEY MILL, HAWLEY ROAD | DARTFORD | DA2 7SY | Dartford |  | Offices And Premises | office | 1 | 1360.96 | 14649 | NIA | 175000 | DARTFORD GRID B 11KV | inside-area | 3.21 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 2.16 | 95 | 54 | 2758100 | SPN-S000000316039 | 315 | 158 | 40-60% | DARTFORD 132/11KV | 129 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | [12 empty] | 51.4238 | 0.23281 | LPN-S000000000716 | 15107270000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
847 | 43.3 | PT GND WING A & 1ST FLR WING A-B 191, HAWLEY ROAD, QUESTOR | DARTFORD | DA1 1PU | Dartford |  | Offices And Premises | office | 1 | 1015.27 | 10928 | NIA | 145000 | DARTFORD GRID B 11KV | inside-area | 2.43 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 100 | 1.61 | 71 | 54 | 2761821 | SPN-S000000314094 | 300 | 150 | 40-60% | DARTFORD 132/11KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 |  | Offices and Workshop Businesses | 178 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-12-05 |  | 1 | FALSE | 51.4291 | 0.2234 | LPN-S000000000716 | 12651640000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
848 | 43.3 | N H S SUPPLIES, ST BARNABAS CLOSE, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LW | Maidstone |  | Warehouse And Premises | industrial | 1 | 13510.12 | 145422 | GIA | 1160000 | WATERSIDE 33/11KV | inside-area | 2.04 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 12 | 21.47 | 338 | 44 | 1581204 | SPN-S000000394102 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014308420 | Storage or Distribution | 13882 | C | Natural Gas | 3 |  | Air Conditioning | 2025-01-28 |  | 1 | FALSE | 51.2913 | 0.50057 | SPN-S000000008529 | 406173148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
849 | 43.3 | AMPHENOL LIMITED, THANET WAY | WHITSTABLE | CT5 3JF | Canterbury |  | Factory And Premises | industrial | 1 | 12632.49 | 135975 | GIA | 525000 | WHITSTABLE 33/11KV | inside-area | 1.85 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 13 | 20.07 | 758 | 11 | 494176 | SPN-S000000343037 | 1000 | 100 | 0-20% | WHITSTABLE 33/11KV | 151 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062301098 | B2 to B7 General Industrial and Special Industrial Groups | 1801 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-04-29 |  | 1 | FALSE | 51.3578 | 1.0577 | SPN-S000000008516 | 14460010000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
850 | 43.3 | THE SALVATORI GROUP UNIT 4, COVERT ROAD, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EQ | Dover |  | Warehouse, Offices And Premises | industrial | 1 | 10394.99 | 111891 | GIA | 410000 | WINGHAM 33/11KV | inside-area | 3.7 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 16 | 16.52 | 728 | 18 | 722982 | SPN-S000000362770 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2213 | 1.1926 | SPN-S000000008517 | 10267373000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
851 | 43.3 | TYLER WAY | WHITSTABLE | CT5 2RS | Canterbury | JOHN HELLYAR & COMPANY LTD; MARIE ANTOINETTE COMPANY LTD; WOODFIELD SYSTEMS LTD | Factory And Premises; Factory, Warehouse And Premises | industrial | 3 | 10385.9 | 111793 | GIA | 533000 | HERNE BAY 33/11KV | inside-area | 1.59 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 16 | 16.5 | 623 | 16 | 666034 | SPN-S000000341433 | 500 | 250 | 40-60% | HERNE BAY 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033164595 | B2 to B7 General Industrial and Special Industrial Groups | 488 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-03-23 |  | 1 | FALSE | 51.3623 | 1.0766 | SPN-S000000008417 | 285147145;516754145;289652145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
852 | 43.3 | COVERT ROAD, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EP | Dover | SHARP INTERPACK | Factory And Premises | industrial | 1 | 9252 | 99588 | GIA | 550000 | WINGHAM 33/11KV | inside-area | 3.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 18 | 14.7 | 555 | 18 | 735285 | SPN-S000000371222 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10034873854 | B8 Storage or Distribution | 4658 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-05-25 |  | 0.5 | FALSE | 51.2226 | 1.1926 | SPN-S000000008517 | 11049000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
853 | 43.3 | 1, COOTING ROAD, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EP | Dover | CERMATCO; SEAFIELD LOGISTICS LTD | Factory And Premises; Warehouse And Premises | industrial | 3 | 8946.44 | 96299 | GIA | 507750 | WINGHAM 33/11KV | inside-area | 3.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 19 | 14.22 | 537 | 18 | 738574 | SPN-S000000371222 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2226 | 1.1926 | SPN-S000000008517 | 8407299000;6097786000;6021761000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
854 | 43.3 | 11-13, ST LAURENCE AVENUE, SPECTRUM WEST, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LL | Maidstone |  | Factory And Premises; Warehouse And Premises | industrial | 3 | 8788.6 | 94600 | GIA | 899000 | WATERSIDE 33/11KV | inside-area | 1.96 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 19 | 13.97 | 527 | 44 | 1632026 | SPN-S000000394224 | 1000 | 100 | 0-20% | WATERSIDE 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2916 | 0.50332 | SPN-S000000008529 | 388213148;1113527000;6290743000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
855 | 43.3 | UNIT 18A WARES PACK HOUSE, WARES FARM, REDWALL LANE | MAIDSTONE | ME17 4BA | Maidstone |  | Storage Depot And Premises | industrial | 1 | 8256.44 | 88871 | GIA | 345000 | SHEPWAY 33/11KV | inside-area | 5.78 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 20 | 13.12 | 206 | 47 | 1410398 | SPN-S000000394421 | 500 | 150 | 20-40% | SHEPWAY 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095448750 | General Industrial and Special Industrial Groups | 7372 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2024-12-23 |  | 1 | FALSE | 51.2122 | 0.49646 | SPN-S000000008644 | 12922359000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
856 | 43.3 | RIVER FARM, CHART HILL ROAD | TONBRIDGE | TN12 0RW | Maidstone |  | Warehouse And Premises | industrial | 1 | 7988.31 | 85985 | GIA | 405000 | SHEPWAY 33/11KV | inside-area | 6.62 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 21 | 12.69 | 200 | 47 | 1413284 | SPN-R000000864407-000-087Z | 100 | 70 | 60-80% | SHEPWAY 33/11KV | 375 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003655584 | Storage or Distribution | 8204 | A | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-08-06 |  | 1 | FALSE | 51.1925 | 0.55385 | SPN-S000000008644 | 11447866000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
857 | 43.3 | SORTING OFFICE, MILITARY ROAD | CANTERBURY | CT1 1AA | Canterbury |  | Sorting Office And Premises | industrial | 1 | 7506.86 | 80803 | GIA | 432500 | CANTERBURY TOWN 33/11KV | inside-area | 0.64 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 22 | 11.93 | 525 | 27 | 977973 | SPN-S000000342547 | 500 | 150 | 20-40% | CANTERBURY TOWN 33/11KV | 130 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2844 | 1.0945 | SPN-S000000008410 | 288641145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
858 | 43.3 | STORAGE KING CANTERBURY TRADE PARK, STURRY ROAD | CANTERBURY | CT2 0AA | Canterbury |  | Warehouse And Premises | industrial | 1 | 6798.6 | 73179 | GIA | 265000 | CANTERBURY TOWN 33/11KV | inside-area | 2.26 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 24 | 10.8 | 170 | 27 | 985597 | SPN-R000000841011-000-057Z | 50 | 25 | 40-60% | CANTERBURY TOWN 33/11KV | 12 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10096028208 | B8 Storage or Distribution | 6741 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2023-10-27 |  | 1 | FALSE | 51.296 | 1.1127 | SPN-S000000008410 | 14868667000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
859 | 43.3 | BIG BOX CO, BIRCHOLT ROAD | MAIDSTONE | ME15 9NE | Maidstone |  | Warehouse And Premises | industrial | 1 | 6671.27 | 71809 | GIA | 272500 | SHEPWAY 33/11KV | inside-area | 1.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 25 | 10.6 | 167 | 47 | 1427460 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2421 | 0.56002 | SPN-S000000008644 | 3250716000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
860 | 43.3 | 1ST FLR POWERHUB BUSINESS CENTRE, ST PETERS STREET | MAIDSTONE | ME16 0ST | Maidstone |  | Workshop And Premises | industrial | 3 | 6496.64 | 69929 | GIA | 407000 | WATERSIDE 33/11KV | inside-area | 0.2 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 25 | 10.32 | 292 | 44 | 1656697 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 112 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.277 | 0.51619 | SPN-S000000008529 | 14440525000;13850524000;14523671000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
861 | 43.3 | HERMITAGE MILLS, HERMITAGE LANE | MAIDSTONE | ME16 9NR | Maidstone | J DEMPSON & COMPANY LTD | Factory And Premises | industrial | 1 | 5929.54 | 63825 | GIA | 367500 | BARMING 33/11KV | inside-area | 0.74 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 4.1 | Green | 22.8 | 18.7 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 21 | 15.9 | Winter | 18.0952 | 3.8 | Green (Over 5% headroom) | 17825 | 28 | 9.42 | 356 | 3 | 108626 | SPN-S000000392440 | 500 | 350 | 60-80% | BARMING 33/11KV | 62 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2708 | 0.48239 | SPN-S000000008527 | 36072148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
862 | 43.3 | 4-6, JOSEPH WILSON INDUSTRIAL ESTATE, MILLSTROOD ROAD | WHITSTABLE | CT5 3PS | Canterbury |  | Builders Merchants; Vehicle Repair Workshop And Premises; Workshop And Premises | industrial | 4 | 5677.95 | 61117 | GIA | 500000 | WHITSTABLE 33/11KV | inside-area | 0.95 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 29 | 9.02 | 256 | 11 | 569034 | SPN-S000000342959 | 800 | 240 | 20-40% | WHITSTABLE 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3457 | 1.0443 | SPN-S000000008516 | 800831000;4450775000;14986989000;11863936000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
863 | 43.3 | PARKWOOD INDUSTRIAL ESTATE, SUTTON ROAD | MAIDSTONE | ME15 9NE | Maidstone | DRACARD LTD; SANGERS LTD | Factory And Premises; Warehouse And Premises | industrial | 2 | 5541.7 | 59650 | GIA | 332000 | SHEPWAY 33/11KV | inside-area | 1.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 30 | 8.81 | 333 | 47 | 1439619 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2421 | 0.56002 | SPN-S000000008644 | 182745148;182746148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
864 | 43.3 | THEOBALD HOUSE, BIRCHOLT ROAD | MAIDSTONE | ME15 9YF | Maidstone |  | Warehouse And Premises | industrial | 1 | 5506.67 | 59273 | GIA | 315000 | SHEPWAY 33/11KV | inside-area | 1.6 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 30 | 8.75 | 138 | 47 | 1439996 | SPN-S000000392174 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 84 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022897285 | B8 Storage or Distribution | 2748 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2021-04-20 |  | 0.5 | FALSE | 51.2396 | 0.56192 | SPN-S000000008644 | 13569121000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
865 | 43.3 | UNITS 9 10 10A 11 & 12 JOSPEH WILSON INDUSTRIAL ESTATE, MILLSTROOD ROAD | WHITSTABLE | CT5 3PS | Canterbury |  | Factory And Premises | industrial | 1 | 5397.99 | 58103 | GIA | 228000 | WHITSTABLE 33/11KV | inside-area | 0.95 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 31 | 8.58 | 324 | 11 | 572048 | SPN-S000000342959 | 800 | 240 | 20-40% | WHITSTABLE 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3457 | 1.0443 | SPN-S000000008516 | 8606301000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
866 | 43.3 | UNIT B4 LOC 8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 5381.81 | 57929 | GIA | 570000 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 31 | 8.55 | 135 | 19 | 750855 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451875 | General Industrial and Special Industrial Groups | 2852 | A+ | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-09-24 |  | 0.75 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14683835000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
867 | 43.3 | UNITS 1-7, MARSHWOOD BUSINESS PARK, MARSHWOOD CLOSE | CANTERBURY | CT1 1DX | Canterbury |  | Warehouse And Premises | industrial | 1 | 5227.11 | 56264 | GIA | 209000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.85 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 32 | 8.31 | 131 | 28 | 1175861 | SPN-S000000343062 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062279026 | Retail/Financial and Professional Services | 2291 | C | Grid Supplied Electricity | 4 |  | Air Conditioning | 2022-06-28 |  | 1 | FALSE | 51.2913 | 1.0996 | SPN-S000000008597 | 14503212000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
868 | 43.3 | TECHNOLOGY HOUSE & UNIT 1, HERNE BAY WEST TRADING ESTATE, SEA STREET | HERNE BAY | CT6 8JZ | Canterbury |  | Workshop And Premises | industrial | 1 | 4520.1 | 48654 | GIA | 236000 | HERNE BAY 33/11KV | inside-area | 1.2 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 37 | 7.18 | 203 | 16 | 729173 | SPN-S000000341390 | 500 | 250 | 40-60% | HERNE BAY 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10090316232 | B8 Storage or Distribution | 2120 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-07-27 |  | 1 | FALSE | 51.364 | 1.1018 | SPN-S000000008417 | 12228463000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
869 | 43.3 | EASISTORE, HART STREET | MAIDSTONE | ME16 8RA | Maidstone |  | Warehouse And Premises | industrial | 1 | 4461.84 | 48027 | GIA | 195000 | WATERSIDE 33/11KV | inside-area | 0.72 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 37 | 7.09 | 112 | 44 | 1678599 | SPN-S000000392170 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2706 | 0.51719 | SPN-S000000008529 | 9354763000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
870 | 43.3 | B3, LOC8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 4323.76 | 46541 | GIA | 472500 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 38 | 6.87 | 108 | 19 | 762243 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451878 | B8 Storage or Distribution | 4274 | A+ | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-04-28 |  | 1 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14523004000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
871 | 43.3 | MAIDSTONE BARRACKS GOODS YARD, BUCKLAND HILL | MAIDSTONE | ME16 0SQ | Maidstone |  | Store And Premises | industrial | 1 | 4322.46 | 46527 | GIA | 205000 | WATERSIDE 33/11KV | inside-area | 0.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 38 | 6.87 | 108 | 44 | 1680099 | SPN-S000000393220 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022892571 | Retail/Financial and Professional Services | 4388 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-08-23 |  | 0.67 | FALSE | 51.2772 | 0.51477 | SPN-S000000008529 | 411415148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
872 | 43.3 | UNIT B1 LOC 8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 4206 | 45273 | GIA | 462500 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 39 | 6.68 | 105 | 19 | 763511 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451875 | General Industrial and Special Industrial Groups | 2852 | A+ | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-09-24 |  | 0.75 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14373730000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
873 | 43.3 | DHL WAREHOUSE 125-127, HERMITAGE LANE | AYLESFORD | ME20 7PX | Tonbridge & Malling |  | Storage Depot And Premises | industrial | 1 | 4025.71 | 43332 | GIA | 247000 | BARMING 33/11KV | inside-area | 2.42 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 4.1 | Green | 22.8 | 18.7 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 21 | 15.9 | Winter | 18.0952 | 3.8 | Green (Over 5% headroom) | 17825 | 41 | 6.4 | 101 | 3 | 129119 | SPN-S000000392141 | 500 | 350 | 60-80% | BARMING 33/11KV | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2857 | 0.47677 | SPN-S000000008527 | 15104718000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
874 | 43.3 | UNITS 8-13, WINGHAM ENGINEERING SITE, GOODNESTONE ROAD | CANTERBURY | CT3 1AR | Dover |  | Warehouse And Premises; Workshop And Premises | industrial | 2 | 3931.9 | 42323 | GIA | 161500 | WINGHAM 33/11KV | inside-area | 1.81 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 42 | 6.25 | 177 | 18 | 792550 | SPN-S000000343759 | 100 | -10 | -20-0% | WINGHAM 33/11KV | 278 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062298304 | B2 to B7 General Industrial and Special Industrial Groups | 1231 | F | Oil | 3 |  | Heating and Natural Ventilation | 2016-07-20 |  | 0.5 | FALSE | 51.2677 | 1.2196 | SPN-S000000008517 | 7622434000;5480784000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
875 | 43.3 | OLD MILL FARM | MAIDSTONE | ME17 1XD | Maidstone |  | Warehouse And Premises | industrial | 2 | 3769.12 | 40570 | GIA | 179500 | MAIDSTONE GRID SOUTH | inside-area | 5.42 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 44 | 5.99 | 94 | 19 | 768214 | SPN-R000000953212-000-030Z | 100 | 70 | 60-80% | MAIDSTONE GRID SOUTH | 219 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2567 | 0.6056 | SPN-S000000009533 | 15129273000;12990584000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
876 | 43.3 | UNIT B2 LOC 8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 3743 | 40289 | GIA | 412500 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 44 | 5.95 | 94 | 19 | 768495 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451875 | General Industrial and Special Industrial Groups | 2852 | A+ | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-09-24 |  | 0.75 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14373732000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
877 | 43.3 | K E F ELECTRONICS, ECCLESTON ROAD | MAIDSTONE | ME15 6QN | Maidstone |  | Factory And Premises | industrial | 1 | 3636.91 | 39147 | GIA | 152000 | WATERSIDE 33/11KV | inside-area | 1.34 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 46 | 5.78 | 218 | 44 | 1687479 | SPN-S000000394902 | 800 | 560 | 60-80% | FAIRMEADOW 11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2653 | 0.51466 | SPN-S000000008529 | 893184000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
878 | 43.3 | HENRY BLAIR BUILDING, LIPHOOK WAY, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LQ | Maidstone |  | Warehouse And Premises | industrial | 1 | 3577 | 38502 | GIA | 332500 | WATERSIDE 33/11KV | inside-area | 2.39 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 46 | 5.68 | 89 | 44 | 1688124 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 183 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003734175 | Offices and Workshop Businesses | 1654 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-07-05 |  | 0.5 | FALSE | 51.2942 | 0.49854 | SPN-S000000008529 | 813222000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
879 | 43.3 | ST LEONARDS ROAD, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LS | Maidstone | FILEDER FILTER SYSTEMS LTD | Warehouse And Premises | industrial | 1 | 3523.65 | 37928 | GIA | 272500 | WATERSIDE 33/11KV | inside-area | 2.29 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 47 | 5.6 | 88 | 44 | 1688698 | SPN-S000000394082 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10091196285 | Offices and Workshop Businesses | 590 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2023-02-02 |  | 1 | FALSE | 51.2918 | 0.49617 | SPN-S000000008529 | 2196100000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
880 | 43.3 | UNIT F3 AND UNIT G, BIRCHOLT ROAD | MAIDSTONE | ME15 9YY | Maidstone |  | Warehouse And Premises | industrial | 1 | 3488.65 | 37551 | GIA | 209000 | SHEPWAY 33/11KV | inside-area | 2.04 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 47 | 5.54 | 87 | 47 | 1461718 | SPN-S000000394968 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 117 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.235 | 0.56123 | SPN-S000000008644 | 14711703000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
881 | 43.3 | KEMET INTERNATIONAL, PARKWOOD INDUSTRIAL ESTATE, SUTTON ROAD | MAIDSTONE | ME15 9NE | Maidstone |  | Factory And Premises | industrial | 1 | 3455.84 | 37198 | GIA | 179000 | SHEPWAY 33/11KV | inside-area | 1.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 48 | 5.49 | 207 | 47 | 1462071 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2421 | 0.56002 | SPN-S000000008644 | 5013857000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
882 | 43.3 | BIRCHOLT ROAD | MAIDSTONE | ME15 9XT | Maidstone | MARLEY PROPERTIES LTD | Factory And Premises | industrial | 1 | 3400.9 | 36607 | GIA | 245000 | SHEPWAY 33/11KV | inside-area | 1.88 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 49 | 5.4 | 204 | 47 | 1462662 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003672796 | B1 Offices and Workshop businesses | 513 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2017-02-03 |  | 1 | FALSE | 51.2359 | 0.5586 | SPN-S000000008644 | 394675148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
883 | 43.3 | UNIT 116, JOSEPH WILSON INDUSTRIAL ESTATE, MILLSTROOD ROAD | WHITSTABLE | CT5 3SN | Canterbury |  | Warehouse And Premises | industrial | 1 | 3393.48 | 36527 | GIA | 272500 | WHITSTABLE 33/11KV | inside-area | 1.08 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 49 | 5.39 | 85 | 11 | 593624 | SPN-S000000342959 | 800 | 240 | 20-40% | WHITSTABLE 33/11KV | 115 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10096026487 | Retail/Financial and Professional Services | 3399 | A | Grid Supplied Electricity | 4 |  | Mixed-mode with Mechanical Ventilation | 2023-08-09 |  | 0.75 | FALSE | 51.3441 | 1.0445 | SPN-S000000008516 | 15053472000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
884 | 43.3 | BROAD OAK ROAD | CANTERBURY | CT2 7PY | Canterbury | BOOKER CASH & CARRY | Warehouse And Premises | industrial | 1 | 3366.9 | 36241 | GIA | 250000 | CANTERBURY TOWN 33/11KV | inside-area | 1.76 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 49 | 5.35 | 84 | 27 | 1022535 | SPN-S000000343794 | 800 | 720 | 80-100% | CANTERBURY TOWN 33/11KV | 389 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2963 | 1.0676 | SPN-S000000008410 | 113663000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
885 | 43.3 | UNIT F1 INTEGRA, BIRCHOLT ROAD | MAIDSTONE | ME15 9YY | Maidstone |  | Warehouse And Premises | industrial | 1 | 3339.91 | 35950 | GIA | 265000 | SHEPWAY 33/11KV | inside-area | 2.04 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 50 | 5.31 | 83 | 47 | 1463319 | SPN-S000000394968 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 117 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 |  | Storage or Distribution | 2233 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-03-20 |  | 0.67 | FALSE | 51.235 | 0.56123 | SPN-S000000008644 | 15038434000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
886 | 43.3 | HOWFIELD LANE | CANTERBURY | CT4 7HG | Canterbury | TIVOLI ENTERPRISES COMPANY LTD | Workshop And Premises | industrial | 1 | 3109.2 | 33467 | GIA | 189000 | CHARTHAM 33/11KV | inside-area | 1.05 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 5.2 | Green | 15 | 9.4 | Thermal | 0 | 5.7 | 0 | 5.7 | 5.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 14.4 | 10.6 | Winter | 37.5 | 5.4 | Green (Over 5% headroom) | 17825 | 53 | 4.94 | 140 | 4 | 114012 | SPN-R000000856006-000-229Z | 200 | 20 | 0-20% | CHARTHAM 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000674716 | B2 to B7 General Industrial and Special Industrial Groups | 1783 | E | Oil | 3 |  | Heating and Natural Ventilation | 2012-12-18 |  | 1 | FALSE | 51.2646 | 1.0311 | SPN-S000000008560 | 167878145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
887 | 43.3 | SIMMONDS ROAD | CANTERBURY | CT1 3RA | Canterbury | RICEMANS WAREHOUSE | Warehouse And Premises | industrial | 1 | 2884.2 | 31045 | GIA | 133000 | CANTERBURY TOWN 33/11KV | inside-area | 1.64 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 57 | 4.58 | 72 | 27 | 1027731 | SPN-S000000342883 | 500 | 250 | 40-60% | CANTERBURY TOWN 33/11KV | 115 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000682284 | B1 Offices and Workshop businesses | 211 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2013-01-11 |  | 1 | FALSE | 51.2735 | 1.0704 | SPN-S000000008410 | 159237145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
888 | 43.3 | UNIT A13, LOC8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 2840.93 | 30579 | GIA | 350000 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 58 | 4.51 | 71 | 19 | 778205 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451876 | B8 Storage or Distribution | 4100 | A+ | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-04-20 |  | 0.67 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14963333000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
889 | 43.3 | L & G FOREST PRODUCTS, DETLING AERODROME | MAIDSTONE | ME14 3HU | Maidstone |  | Warehouse And Premises | industrial | 1 | 2840.4 | 30574 | GIA | 214000 | MAIDSTONE GRID SOUTH | inside-area | 6.21 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 58 | 4.51 | 71 | 19 | 778210 | SPN-R000000953213-000-105Z | 315 | 220 | 60-80% | MAIDSTONE NORTH 132/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022900232 | B8 Storage or Distribution | 2556 | D | Oil | 3 | 1 | Heating and Natural Ventilation | 2018-11-19 |  | 0.67 | FALSE | 51.3105 | 0.60109 | SPN-S000000009533 | 6739272000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
890 | 43.3 | UNITS 8-9, HASLEMERE INDUSTRIAL ESTATE, SUTTON ROAD | MAIDSTONE | ME15 9NZ | Maidstone |  | Warehouse And Premises | industrial | 2 | 2602.74 | 28016 | GIA | 252000 | SHEPWAY 33/11KV | inside-area | 1.63 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 64 | 4.14 | 65 | 47 | 1471253 | SPN-S000000392441 | 500 | 350 | 60-80% | SHEPWAY 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2385 | 0.55923 | SPN-S000000008644 | 11098856000;10564038000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
891 | 43.3 | SPINNEY HOUSE, WILCOX CLOSE, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EP | Dover |  | Warehouse And Premises | industrial | 1 | 2590.4 | 27883 | GIA | 111000 | WINGHAM 33/11KV | inside-area | 3.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 64 | 4.12 | 65 | 18 | 806990 | SPN-S000000371222 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10034873887 | B8 Storage or Distribution | 2990 | C | LPG | 3 |  | Heating and Natural Ventilation | 2012-06-27 |  | 1 | FALSE | 51.2226 | 1.1926 | SPN-S000000008517 | 126634145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
892 | 43.3 | UNITS 37-40, LAKESVIEW BUSINESS PARK, THOMAS WAY, ISLAND ROAD | CANTERBURY | CT3 4JZ | Canterbury |  | Workshop And Premises | industrial | 1 | 2574.51 | 27712 | GIA | 290000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.58 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 64 | 4.09 | 116 | 28 | 1204413 | SPN-S000000343485 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.316 | 1.1732 | SPN-S000000008597 | 4511210000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
893 | 43.3 | UNIT 11, LAKESVIEW BUSINESS PARK, ISLAND ROAD | CANTERBURY | CT3 4JG | Canterbury |  | Factory And Premises | industrial | 1 | 2532.91 | 27264 | GIA | 206000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.65 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 65 | 4.03 | 152 | 28 | 1204861 | SPN-S000000343378 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.316 | 1.1743 | SPN-S000000008597 | 8153333000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
894 | 43.3 | UNIT 3J, DETLING AERODROME | MAIDSTONE | ME14 3HU | Maidstone |  | Warehouse And Premises | industrial | 1 | 2526.2 | 27192 | GIA | 166000 | MAIDSTONE GRID SOUTH | inside-area | 6.21 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 66 | 4.01 | 63 | 19 | 781592 | SPN-R000000953213-000-105Z | 315 | 220 | 60-80% | MAIDSTONE NORTH 132/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022900232 | B8 Storage or Distribution | 2556 | D | Oil | 3 | 1 | Heating and Natural Ventilation | 2018-11-19 |  | 0.67 | FALSE | 51.3105 | 0.60109 | SPN-S000000009533 | 15072876000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
895 | 43.3 | GND FLR CENTRAL STORE AT INTEX HOUSE, COOTING ROAD, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EP | Dover |  | Warehouse And Premises | industrial | 2 | 2485.24 | 26751 | GIA | 67000 | WINGHAM 33/11KV | inside-area | 3.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 67 | 3.95 | 62 | 18 | 808122 | SPN-S000000371222 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2226 | 1.1926 | SPN-S000000008517 | 15066499000;15066501000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
896 | 43.3 | 4, ST AUGUSTINES BUSINESS PARK | WHITSTABLE | CT5 2QJ | Canterbury |  | Warehouse And Premises | industrial | 1 | 2457.7 | 26454 | GIA | 136000 | HERNE BAY 33/11KV | inside-area | 1.43 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 67 | 3.91 | 61 | 16 | 751373 | SPN-S000000343236 | 1000 | 700 | 60-80% | WHITSTABLE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3621 | 1.0792 | SPN-S000000008417 | 6586923000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
897 | 43.3 | 3-3A, CANTERBURY INDUSTRIAL PARK, ISLAND ROAD | CANTERBURY | CT3 4HQ | Canterbury |  | Warehouse And Premises | industrial | 1 | 2416.4 | 26010 | GIA | 139000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 69 | 3.84 | 60 | 28 | 1206115 | SPN-S000000342849 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3138 | 1.1709 | SPN-S000000008597 | 291306145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
898 | 43.3 | KINGSWOOD CHRISTMAS TREES, GRAVELLY BOTTOM ROAD | MAIDSTONE | ME17 3NU | Maidstone |  | Warehouse And Premises (Part Exempt) | industrial | 1 | 2346.81 | 25261 | GIA | 44000 | SHEPWAY 33/11KV | inside-area | 5.58 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 71 | 3.73 | 59 | 47 | 1474008 | SPN-R000000864405-000-057Z | 100 | 50 | 40-60% | SHEPWAY 33/11KV | 118 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2267 | 0.61927 | SPN-S000000008644 | 13679585000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
899 | 43.3 | 6-7, COTTON ROAD | CANTERBURY | CT1 3RB | Canterbury |  | Warehouse And Premises | industrial | 2 | 2345.44 | 25246 | GIA | 178000 | CANTERBURY TOWN 33/11KV | inside-area | 1.74 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 71 | 3.73 | 59 | 27 | 1033530 | SPN-S000000342189 | 1000 | 500 | 40-60% | CANTERBURY TOWN 33/11KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062280578 | B8 Storage or Distribution | 593 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-05-22 |  | 0.5 | FALSE | 51.2743 | 1.067 | SPN-S000000008410 | 4833035000;3122637000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
900 | 43.3 | BOLEYN HOUSE, ST AUGUSTINES BUSINESS PARK, ESTUARY CLOSE | WHITSTABLE | CT5 2QJ | Canterbury | CATHEDRAL CONTRACTS | Workshop And Premises | industrial | 1 | 2344.43 | 25235 | GIA | 127000 | HERNE BAY 33/11KV | inside-area | 1.43 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 71 | 3.73 | 105 | 16 | 752592 | SPN-S000000343236 | 1000 | 700 | 60-80% | WHITSTABLE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3621 | 1.0792 | SPN-S000000008417 | 4770468000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
901 | 43.3 | UNIT A12, LOC8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 2318 | 24951 | GIA | 277500 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 71 | 3.68 | 58 | 19 | 783833 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451874 | General Industrial and Special Industrial Groups | 2290 | A+ | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-09-04 |  | 1 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14963330000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
902 | 43.3 | BRITELITE HOUSE, BIRCHOLT ROAD | MAIDSTONE | ME15 9XT | Maidstone |  | Warehouse And Premises | industrial | 1 | 2278.89 | 24530 | GIA | 170000 | SHEPWAY 33/11KV | inside-area | 1.88 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 73 | 3.62 | 57 | 47 | 1474739 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2359 | 0.5586 | SPN-S000000008644 | 9344742000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
903 | 43.3 | BRAY & SON LTD BRAY HOUSE UNIT 15, HERONDEN ROAD | MAIDSTONE | ME15 9YR | Maidstone |  | Warehouse And Premises | industrial | 1 | 2263 | 24359 | GIA | 161000 | SHEPWAY 33/11KV | inside-area | 1.79 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 73 | 3.6 | 57 | 47 | 1474910 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2371 | 0.5599 | SPN-S000000008644 | 14173893000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
904 | 43.3 | 182, JOHN WILSON BUSINESS PARK, THANET WAY | WHITSTABLE | CT5 3RB | Canterbury |  | Factory And Premises | industrial | 1 | 2242.9 | 24142 | GIA | 164000 | WHITSTABLE 33/11KV | inside-area | 1.75 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 74 | 3.56 | 135 | 11 | 606009 | SPN-S000000343037 | 1000 | 100 | 0-20% | WHITSTABLE 33/11KV | 118 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000682975 | Offices and Workshop Businesses | 2251 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-10-05 |  | 0.75 | FALSE | 51.3577 | 1.0562 | SPN-S000000008516 | 518797145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
905 | 43.3 | UNITS A AND B, HIGHLAND COURT FARM | CANTERBURY | CT4 5HW | Canterbury |  | Warehouse And Premises | industrial | 1 | 2198.37 | 23663 | GIA | 154000 | WINGHAM 33/11KV | inside-area | 4.82 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 75 | 3.49 | 55 | 18 | 811210 | SPN-S000000343459 | 315 | 158 | 40-60% | WINGHAM 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2394 | 1.1478 | SPN-S000000008517 | 14979523000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
906 | 43.3 | ALBION WORKS, CHURCH LANE | CANTERBURY | CT4 6QS | Canterbury | JALI LTD | Workshop And Premises | industrial | 1 | 2197.04 | 23649 | GIA | 125000 | WINGHAM 33/11KV | inside-area | 6.29 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 75 | 3.49 | 99 | 18 | 811224 | SPN-S000000364981 | 315 | 158 | 40-60% | LIGHTWEIGHT AGGREGATES | 217 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2036 | 1.1667 | SPN-S000000008517 | 1736093000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
907 | 43.3 | DENNE JOINERY LTD | CANTERBURY | CT3 1NB | Canterbury |  | Workshop And Premises | industrial | 1 | 2158 | 23228 | NIA | 114000 | WINGHAM 33/11KV | inside-area | 2.38 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 77 | 3.43 | 97 | 18 | 811645 | SPN-R000000851705-000-209Z | 315 | 220 | 60-80% | WINGHAM 33/11KV | 24 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.267 | 1.19 | SPN-S000000008517 | 6891517000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
908 | 43.3 | CLAYTON GLASS LTD, MARSHWOOD INDUSTRIAL ESTATE, MARSHWOOD CLOSE | CANTERBURY | CT1 1DX | Canterbury |  | Factory And Premises | industrial | 1 | 2147.8 | 23119 | GIA | 156000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.85 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 77 | 3.41 | 129 | 28 | 1209006 | SPN-S000000343062 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10093444120 | B2 to B7 General Industrial and Special Industrial Groups | 2107 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-05-23 |  | 0.67 | FALSE | 51.2913 | 1.0996 | SPN-S000000008597 | 15125366000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
909 | 43.3 | MARSHWOOD INDUSTRIAL ESTATE, MARSHWOOD CLOSE | CANTERBURY | CT1 1DX | Canterbury | SOLAGLAS LTD | Factory And Premises | industrial | 1 | 2147.8 | 23119 | GIA | 156000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.85 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 77 | 3.41 | 129 | 28 | 1209006 | SPN-S000000343062 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10093444121 | B2 to B7 General Industrial and Special Industrial Groups | 340 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2013-03-13 |  | 1 | FALSE | 51.2913 | 1.0996 | SPN-S000000008597 | 295732145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
910 | 43.3 | RATLING ROAD | CANTERBURY | CT3 3AY | Dover | GUS TRANSPORT LTD | Warehouse And Premises | industrial | 1 | 2093.8 | 22537 | GIA | 120000 | WINGHAM 33/11KV | inside-area | 2.37 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 79 | 3.33 | 52 | 18 | 812336 | SPN-S000000362834 | 500 | 150 | 20-40% | WINGHAM 33/11KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2308 | 1.2079 | SPN-S000000008517 | 36018145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
911 | 43.3 | UNIT 2 C A BUSINESS PARK, TYLER WAY | WHITSTABLE | CT5 2RP | Canterbury |  | Workshop And Premises | industrial | 1 | 2084.66 | 22439 | GIA | 135000 | HERNE BAY 33/11KV | inside-area | 1.7 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 79 | 3.31 | 94 | 16 | 755388 | SPN-S000000341433 | 500 | 250 | 40-60% | HERNE BAY 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3635 | 1.0762 | SPN-S000000008417 | 13692802000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
912 | 43.3 | UNITS G13 G14 & G15 POWERHUB BUSINESS CENTRE, ST PETERS STREET | MAIDSTONE | ME16 0ST | Maidstone |  | Warehouse And Premises | industrial | 1 | 2048.33 | 22048 | GIA | 90500 | WATERSIDE 33/11KV | inside-area | 0.2 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 81 | 3.25 | 51 | 44 | 1704578 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 112 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10094444284 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 2152 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2021-06-22 |  | 1 | FALSE | 51.277 | 0.51619 | SPN-S000000008529 | 12232887000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
913 | 43.3 | JACOBI JAYNE, WEALDEN FOREST PARK, HERNE COMMON | HERNE BAY | CT6 7LQ | Canterbury |  | Warehouse, Offices And Premises | industrial | 1 | 2040.36 | 21962 | GIA | 97500 | CANTERBURY LOCAL 33/11KV | inside-area | 4.98 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 81 | 3.24 | 143 | 28 | 1210163 | SPN-S000000343460 | 100 | 10 | 0-20% | CANTERBURY LOCAL 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3312 | 1.119 | SPN-S000000008597 | 10260456000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
914 | 43.3 | UNIT 10 APPLEDOWN HOUSE, BARTON BUSINESS PARK | CANTERBURY | CT1 3AA | Canterbury |  | Warehouse And Premises | industrial | 1 | 2016.54 | 21706 | GIA | 93000 | CANTERBURY TOWN 33/11KV | inside-area | 2.22 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 82 | 3.2 | 50 | 27 | 1037070 | [9 empty] | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.27 | 1.1065 | SPN-S000000008410 | 513438145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
915 | 43.3 | UNIT 12 THOMAS WAY, LAKESVIEW BUSINESS PARK, ISLAND ROAD | CANTERBURY | CT3 4JZ | Canterbury |  | Warehouse And Premises | industrial | 1 | 2015.3 | 21692 | GIA | 182000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.58 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 82 | 3.2 | 50 | 28 | 1210433 | SPN-S000000343485 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033163466 | General Industrial and Special Industrial Groups | 2043 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-03-10 |  | 0.75 | FALSE | 51.316 | 1.1732 | SPN-S000000008597 | 4015139000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
916 | 43.3 | ROYAL MAIL MAIDSTONE DELIVERY OFFICE, BIRCHOLT ROAD | MAIDSTONE | ME15 9EE | Maidstone |  | Warehouse And Premises | industrial | 1 | 1981.88 | 21333 | GIA | 214000 | SHEPWAY 33/11KV | inside-area | 1.85 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 84 | 3.15 | 50 | 47 | 1477936 | SPN-S000000393712 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 159 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014314696 | B1 Offices and Workshop businesses | 1760 | B | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2012-10-26 |  | 0.67 | FALSE | 51.2377 | 0.56369 | SPN-S000000008644 | 8723090000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
917 | 43.3 | UNIT 11C, CLAREMONT WAY, LAKESVIEW BUSINESS PARK | CANTERBURY | CT3 4JG | Canterbury |  | Warehouse And Premises | industrial | 1 | 1978.8 | 21300 | GIA | 109000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.65 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 84 | 3.14 | 49 | 28 | 1210825 | SPN-S000000343378 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.316 | 1.1743 | SPN-S000000008597 | 8042404000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
918 | 43.3 | UNIT 7, BARTON BUSINESS PARK | CANTERBURY | CT1 3AA | Canterbury |  | Warehouse And Premises | industrial | 1 | 1971 | 21216 | GIA | 104000 | CANTERBURY TOWN 33/11KV | inside-area | 2.22 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 84 | 3.13 | 49 | 27 | 1037560 | [9 empty] | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200001487921 | Storage or Distribution | 1776 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-04-04 |  | 1 | FALSE | 51.27 | 1.1065 | SPN-S000000008410 | 506916145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
919 | 43.3 | GROUP 4 SECURICOR CASH SERVICES LTD, LIPHOOK WAY, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LQ | Maidstone |  | Warehouse, Office And Premises | industrial | 1 | 1950 | 20990 | GIA | 234000 | WATERSIDE 33/11KV | inside-area | 2.39 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 85 | 3.1 | 136 | 44 | 1705636 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 183 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003734175 | Offices and Workshop Businesses | 1654 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-07-05 |  | 0.5 | FALSE | 51.2942 | 0.49854 | SPN-S000000008529 | 5122436000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
920 | 43.3 | CROWN WORKS, HERONDEN ROAD | MAIDSTONE | ME15 9YR | Maidstone | POPE & HAYWARDS LTD | Factory And Premises | industrial | 1 | 1944.7 | 20933 | GIA | 131000 | SHEPWAY 33/11KV | inside-area | 1.79 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 85 | 3.09 | 117 | 47 | 1478336 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2371 | 0.5599 | SPN-S000000008644 | 182891148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
921 | 43.3 | BLACKSOLE HOUSE, ALTIRA BUSINESS PARK, THE BOULEVARD, THANET WAY | HERNE BAY | CT6 6GZ | Canterbury |  | Warehouse, Offices And Premises | industrial | 1 | 1935.7 | 20836 | GIA | 155000 | HERNE BAY 33/11KV | inside-area | 3.9 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 86 | 3.08 | 135 | 16 | 756991 | SPN-S000000343379 | 315 | 220 | 60-80% | HERNE BAY 33/11KV | 312 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3619 | 1.15 | SPN-S000000008417 | 6942166000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
922 | 43.3 | ADVANCED TOOLING SYSTEMS UK LTD, COLDRED ROAD | MAIDSTONE | ME15 9XX | Maidstone |  | Factory And Premises | industrial | 1 | 1928.4 | 20757 | GIA | 136000 | SHEPWAY 33/11KV | inside-area | 1.9 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 86 | 3.06 | 116 | 47 | 1478512 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2359 | 0.55939 | SPN-S000000008644 | 4859570000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
923 | 43.3 | BARRETTS JAGUAR LAND ROVER AFTER SALES CENTRE, GEOFFREY BARRETT WAY | CANTERBURY | CT2 7WX | Canterbury |  | Workshop And Premises | industrial | 1 | 1906.88 | 20525 | GIA | 191000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.24 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 87 | 3.03 | 86 | 28 | 1211600 | SPN-S000000341794 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.291 | 1.0909 | SPN-S000000008597 | 11495469000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
924 | 43.3 | 1-5, FAIRFAX BUSINESS CENTRE, BIRCHOLT ROAD | MAIDSTONE | ME15 9SF | Maidstone |  | Factory And Premises | industrial | 1 | 1868.57 | 20113 | GIA | 148000 | SHEPWAY 33/11KV | inside-area | 1.98 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 89 | 2.97 | 112 | 47 | 1479156 | SPN-S000000394968 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2356 | 0.56119 | SPN-S000000008644 | 7223402000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
925 | 43.2 | BROOKLYN FARM, CHAPEL LANE | CRANBROOK | TN17 3NU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 2100 | 22604 | GIA | 25250 | CRANBROOK 33/11KV | inside-area | 2.51 | Hartley Grid | Ninfield | East Sussex Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.2 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 35.4839 | 2.2 | Green (Over 5% headroom) | 17112 | 76 | 3.34 | 52 | 3 | 47251 | SPN-R000000838109-000-043Z | 200 | 100 | 40-60% | CRANBROOK 33/11KV | 108 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1015 | 0.56774 | SPN-S000000008381 | 10713796000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
926 | 43 | POLHILL GARDEN CENTRE, POLHILL GARDEN CENTRE, POLHILL | SEVENOAKS | TN14 7AD | Sevenoaks |  | Garden Centre And Premises | bigbox | 1 | 13820.65 | 148764 | GIA | 610000 | SOUTH ORPINGTON 33/11KV | inside-area | 5.34 | Chelsfield Grid | Northfleet | West Kent Zone | 6 | primary | 6 | Green | 22.8 | 16.9 | Thermal | 0 | 0 | 0 | 0 | 0.6 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.8 | Winter | 26.1062 | 5.9 | Green (Over 5% headroom) | 42781 | 29 | 21.96 | 1244 | 1 | 97166 | SPN-R000000848912-000-043Z | 50 | 25 | 40-60% | SOUTH ORPINGTON 33/11KV | 270 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3317 | 0.14957 | SPN-S000000008489 | 10450745000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
927 | 43 | COOLINGS NURSERIES, RUSHMORE HILL | SEVENOAKS | TN14 7NN | Sevenoaks |  | Garden Centre And Premises | bigbox | 1 | 9027.03 | 97166 | NIA | 147000 | SOUTH ORPINGTON 33/11KV | inside-area | 3.93 | Chelsfield Grid | Northfleet | West Kent Zone | 6 | primary | 6 | Green | 22.8 | 16.9 | Thermal | 0 | 0 | 0 | 0 | 0.6 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.8 | Winter | 26.1062 | 5.9 | Green (Over 5% headroom) | 42781 | 44 | 14.34 | 812 | 1 | 148764 | SPN-S000000447207 | 500 | 250 | 40-60% | SOUTH ORPINGTON 33/11KV | 210 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062548981 | A1/A2 Retail and Financial/Professional services | 240 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-02-18 |  | 1 | FALSE | 51.3293 | 0.11987 | SPN-S000000008489 | 386024148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
928 | 42.9 | EDEN HOUSE, ENTERPRISE WAY | EDENBRIDGE | TN8 6HF | Sevenoaks | PAUL CORBETT LTD (EASISTORE) | Warehouse And Premises | industrial | 1 | 8512 | 91622 | GIA | 287500 | EDENBRIDGE 33/11KV | inside-area | 1.08 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 17 | 13.53 | 213 | 11 | 350351 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062592971 | B1 Offices and Workshop businesses | 687 | A | Natural Gas | 3 |  | Air Conditioning | 2012-07-27 |  | 1 | FALSE | 51.2065 | 0.059998 | SPN-S000000008614 | 1261156000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
929 | 42.9 | ALEXIR PACKAGING EAST & WEST, ENTERPRISE WAY | EDENBRIDGE | TN8 6HF | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 7324.79 | 78843 | GIA | 407500 | EDENBRIDGE 33/11KV | inside-area | 1.08 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 20 | 11.64 | 183 | 11 | 363130 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035181112 | B2 to B7 General Industrial and Special Industrial Groups | 3830 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2015-11-26 |  | 0.6 | FALSE | 51.2065 | 0.059998 | SPN-S000000008614 | 12182198000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
930 | 42.9 | AMBE HOUSE, COMMERCE WAY | EDENBRIDGE | TN8 6ED | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 5319.44 | 57258 | GIA | 272500 | EDENBRIDGE 33/11KV | inside-area | 1.29 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 27 | 8.45 | 133 | 11 | 384715 | SPN-S000000442659 | 500 | 250 | 40-60% | EDENBRIDGE 33/11KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002018664 | B1 Offices and Workshop businesses | 5234 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2017-04-05 |  | 0.5 | FALSE | 51.2054 | 0.06327 | SPN-S000000008614 | 7900062000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
931 | 42.9 | KCL HOUSE, STATION ROAD | EDENBRIDGE | TN8 6HL | Sevenoaks |  | Factory And Premises | industrial | 1 | 3151.15 | 33919 | GIA | 189000 | EDENBRIDGE 33/11KV | inside-area | 1.1 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 46 | 5.01 | 189 | 11 | 408054 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062592980 | General Industrial and Special Industrial Groups | 3002 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2024-06-24 |  | 1 | FALSE | 51.2066 | 0.06102 | SPN-S000000008614 | 7618483000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
932 | 42.9 | BUILDING AT WALNUT TREE FARM, CHURCH ROAD | ASHFORD | TN25 6SA | Ashford |  | Warehouse And Premises | industrial | 1 | 2769.52 | 29811 | GIA | 121000 | SMEETH 33/11KV | inside-area | 1.66 | Sellindge Grid | Sellindge | East Kent Zone | 2.2 | primary | 2.2 | Green | 3.8 | 0.9 | Thermal | 0 | 0 | 0 | 0 | 2.9 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.7 | Winter | 76.3158 | 2.9 | Green (Over 5% headroom) | 15686 | 53 | 4.4 | 69 | 1 | 11967 | SPN-S000000361236 | 200 | 100 | 40-60% | STANFORD 33/11KV | 79 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1195 | 0.96108 | SPN-S000000008485 | 12045307000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
933 | 42.9 | UNIT 1 & PART UNIT 2, ENTERPRISE WAY | EDENBRIDGE | TN8 6HF | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 2720.22 | 29280 | GIA | 163000 | EDENBRIDGE 33/11KV | inside-area | 1.08 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 54 | 4.32 | 68 | 11 | 412693 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2065 | 0.059998 | SPN-S000000008614 | 12333232000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
934 | 42.9 | UNITS 1-8 BLOCK 3, ENTERPRISE WAY | EDENBRIDGE | TN8 6HF | Sevenoaks |  | Vehicle Repair Workshop And Premises; Warehouse And Premises | industrial | 2 | 2573.43 | 27700 | GIA | 285000 | EDENBRIDGE 33/11KV | inside-area | 1.08 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 57 | 4.09 | 116 | 11 | 414273 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002001506 | B8 Storage or Distribution | 141 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-08-14 |  | 1 | FALSE | 51.2065 | 0.059998 | SPN-S000000008614 | 7932031000;9454001000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
935 | 42.9 | GEMINI HOUSE, ENTERPRISE WAY | EDENBRIDGE | TN8 6HF | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 2124.6 | 22869 | GIA | 187000 | EDENBRIDGE 33/11KV | inside-area | 1.08 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 69 | 3.38 | 53 | 11 | 419104 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035181112 | B2 to B7 General Industrial and Special Industrial Groups | 3830 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2015-11-26 |  | 0.5 | FALSE | 51.2065 | 0.059998 | SPN-S000000008614 | 5480623000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
936 | 42.9 | AIRBORN INTERNATIONAL LTD, STATION ROAD | EDENBRIDGE | TN8 6HL | Sevenoaks |  | Factory And Premises | industrial | 1 | 2061.22 | 22187 | GIA | 154000 | EDENBRIDGE 33/11KV | inside-area | 1.1 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 71 | 3.28 | 124 | 11 | 419786 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035182902 | General Industrial and Special Industrial Groups | 2099 | B | Grid Supplied Electricity | 4 | 3 | Air Conditioning | 2024-06-27 |  | 1 | FALSE | 51.2066 | 0.06102 | SPN-S000000008614 | 13919642000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
937 | 42.9 | FACTORY 2, STATION ROAD | EDENBRIDGE | TN8 6HL | Sevenoaks |  | Factory And Premises | industrial | 1 | 2061.22 | 22187 | GIA | 154000 | EDENBRIDGE 33/11KV | inside-area | 1.1 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 71 | 3.28 | 124 | 11 | 419786 | SPN-S000000441555 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035182902 | General Industrial and Special Industrial Groups | 2099 | B | Grid Supplied Electricity | 4 | 3 | Air Conditioning | 2024-06-27 |  | 1 | FALSE | 51.2066 | 0.06102 | SPN-S000000008614 | 15145901000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
938 | 42.7 | UNITS 4-7, WESTMEAD, WEST POINT BUSINESS PARK, NEW HYTHE LANE | AYLESFORD | ME20 6XJ | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 12963.93 | 139542 | GIA | 917000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.41 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 10 | 20.6 | 324 | 23 | 1679399 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10092971261 | B8 Storage or Distribution | 1216 | D | Grid Supplied Electricity | 3 | 12 | Heating and Natural Ventilation | 2019-05-26 |  | 1 | FALSE | 51.3142 | 0.45363 | SPN-S000000008653 | 12672450000;10362974000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
939 | 42.7 | UNIT 1, AYLESFORD COMMERCIAL PARK, NEW HYTHE LANE | AYLESFORD | ME20 7FE | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 11094.61 | 119421 | GIA | 995000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.67 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 12 | 17.63 | 277 | 23 | 1699520 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 297 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10092970625 | Storage or Distribution | 3166 | C | Natural Gas | 4 | 1 | Heating and Natural Ventilation | 2025-12-15 |  | 0.8 | FALSE | 51.312 | 0.45513 | SPN-S000000008653 | 8914773000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
940 | 42.7 | UNIT A, RIVERSIDE BUSINESS PARK, NEW HYTHE LANE | AYLESFORD | ME20 6WT | Tonbridge & Malling | BRAKES | Cold Store And Premises | industrial | 1 | 9037.39 | 97278 | GIA | 850000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.32 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 15 | 14.36 | 1084 | 23 | 1721663 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 334 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3156 | 0.45709 | SPN-S000000008653 | 4231625000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
941 | 42.7 | D S G RETAIL LTD T/A TEAM KNOWHOW, SORTMILL ROAD | SNODLAND | ME6 5UA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 7870.2 | 84714 | GIA | 615000 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.29 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 17 | 12.51 | 197 | 23 | 1734227 | SPN-S000000394290 | 800 | 560 | 60-80% | TOWNSEND HOOK 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3251 | 0.44663 | SPN-S000000008653 | 12113775000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
942 | 42.7 | FERRY HOUSE, NEW HYTHE LANE | AYLESFORD | ME20 7DA | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 7700 | 82882 | GIA | 151000 | TOWNSEND HOOK 33/6.6KV | inside-area | 2.43 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 17 | 12.24 | 346 | 23 | 1736059 | SPN-S000000392361 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3076 | 0.46691 | SPN-S000000008653 | 8180974000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
943 | 42.7 | VECTOR POINT, SORTMILL ROAD | SNODLAND | ME6 5UA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 7487.95 | 80600 | GIA | 730000 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.29 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 18 | 11.9 | 187 | 23 | 1738341 | SPN-S000000394290 | 800 | 560 | 60-80% | TOWNSEND HOOK 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3251 | 0.44663 | SPN-S000000008653 | 2582531000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
944 | 42.7 | 15, LARKFIELD TRADING ESTATE, NEW HYTHE LANE | AYLESFORD | ME20 6SW | Tonbridge & Malling |  | Trade Warehouse And Premises; Warehouse And Premises | industrial | 3 | 7050.17 | 75887 | GIA | 642500 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.35 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 19 | 11.2 | 176 | 23 | 1743054 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000964791 | Storage or Distribution | 4879 | E | Natural Gas | 4 |  | Heating and Natural Ventilation | 2022-11-23 |  | 0.75 | FALSE | 51.3146 | 0.45191 | SPN-S000000008653 | 186682148;186683148;14861194000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
945 | 42.7 | BLOCK C, NEW HYTHE LANE | AYLESFORD | ME20 6SW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 5100.35 | 54900 | GIA | 360000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.35 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 26 | 8.1 | 128 | 23 | 1764041 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000964791 | Storage or Distribution | 4879 | E | Natural Gas | 4 |  | Heating and Natural Ventilation | 2022-11-23 |  | 1 | FALSE | 51.3146 | 0.45191 | SPN-S000000008653 | 15056298000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
946 | 42.7 | UNIT C, RIVERSIDE BUSINESS PARK, NEW HYTHE LANE | AYLESFORD | ME20 6WT | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3555.26 | 38268 | GIA | 365000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.32 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 37 | 5.65 | 89 | 23 | 1780673 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 334 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10002917474 | Storage or Distribution | 3390 | B | Natural Gas | 3 | 3 | Heating and Natural Ventilation | 2025-01-16 |  | 1 | FALSE | 51.3156 | 0.45709 | SPN-S000000008653 | 4373912000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
947 | 42.7 | UNIT 2C, AYLESFORD COMMERCIAL PARK, NEW HYTHE LANE | AYLESFORD | ME20 7FE | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 3228.55 | 34752 | GIA | 350000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.67 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 41 | 5.13 | 81 | 23 | 1784189 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 297 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10092970625 | Storage or Distribution | 3166 | C | Natural Gas | 4 | 1 | Heating and Natural Ventilation | 2025-12-15 |  | 1 | FALSE | 51.312 | 0.45513 | SPN-S000000008653 | 10027741000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
948 | 42.7 | UNIT B9 & 10, LARKFIELD TRADING ESTATE, NEW HYTHE LANE | AYLESFORD | ME20 6SW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2724.2 | 29323 | GIA | 248000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.35 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 49 | 4.33 | 68 | 23 | 1789618 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000964791 | Storage or Distribution | 4879 | E | Natural Gas | 4 |  | Heating and Natural Ventilation | 2022-11-23 |  | 0.6 | FALSE | 51.3146 | 0.45191 | SPN-S000000008653 | 14215330000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
949 | 42.7 | UNIT 2A, AYLESFORD COMMERCIAL PARK, NEW HYTHE LANE | AYLESFORD | ME20 7FE | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2614.58 | 28143 | GIA | 307500 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.67 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 51 | 4.15 | 65 | 23 | 1790798 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 297 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10092970623 | Storage or Distribution | 4642 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2026-01-14 |  | 1 | FALSE | 51.312 | 0.45513 | SPN-S000000008653 | 10027712000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
950 | 42.7 | UNIT D, RIVERSIDE BUSINESS PARK, NEW HYTHE LANE | AYLESFORD | ME20 7PW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2364.59 | 25452 | GIA | 295000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.57 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 56 | 3.76 | 59 | 23 | 1793489 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 314 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10094697141 | B2 to B7 General Industrial and Special Industrial Groups | 2305 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2014-05-28 |  | 0.5 | FALSE | 51.3132 | 0.45706 | SPN-S000000008653 | 11601775000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
951 | 42.7 | UNIT 2B, AYLESFORD COMMERCIAL PARK, NEW HYTHE LANE | AYLESFORD | ME20 7FE | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2202.85 | 23711 | GIA | 260000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.67 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 60 | 3.5 | 55 | 23 | 1795230 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 297 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10092970624 | Storage or Distribution | 2790 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2026-01-14 |  | 1 | FALSE | 51.312 | 0.45513 | SPN-S000000008653 | 10027722000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
952 | 42.7 | JENNYCHEM HOUSE, SORTMILL ROAD | SNODLAND | ME6 5UA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1993.06 | 21453 | GIA | 157000 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.29 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 66 | 3.17 | 50 | 23 | 1797488 | SPN-S000000394290 | 800 | 560 | 60-80% | TOWNSEND HOOK 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000964607 | Offices and Workshop Businesses | 1805 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-08-11 |  | 1 | FALSE | 51.3251 | 0.44663 | SPN-S000000008653 | 7111969000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
953 | 42.7 | LENVALE HOUSE 2, EAST STREET | SNODLAND | ME6 5BA | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1974.17 | 21250 | GIA | 89500 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.26 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 67 | 3.14 | 49 | 23 | 1797691 | SPN-S000000391473 | 315 | 220 | 60-80% | TOWNSEND HOOK 33/6.6KV | 57 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062393468 | Storage or Distribution | 2371 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-07-16 |  | 1 | FALSE | 51.3283 | 0.44722 | SPN-S000000008653 | 9637690000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
954 | 42.5 | TUDOR ROOF TILE CO LTD, DENGEMARSH ROAD | ROMNEY MARSH | TN29 9JH | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 3605.57 | 38810 | GIA | 93500 | RYE 33/11KV | inside-area | 12.77 | Rye Grid | Ninfield | East Sussex Zone | 1.9 | primary | 1.9 | Green | 12.6 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.9 | Rye Grid 33kV | 7 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.2 | 9.6 | Winter | 14.7541 | 1.8 | Green (Over 5% headroom) | 13547 | 35 | 5.73 | 216 | 2 | 46491 | SPN-R000000846906-000-105Z | 200 | 60 | 20-40% | ROMNEY WARREN 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 50001139 | B2 to B7 General Industrial and Special Industrial Groups | 3370 | C | Natural Gas | 4 | 1 | Heating and Natural Ventilation | 2015-12-02 |  | 1 | FALSE | 50.9321 | 0.9076 | SPN-S000000008476 | 12366497000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
955 | 42.5 | GRANT INTERNATIONAL, DENGEMARSH ROAD | ROMNEY MARSH | TN29 9JH | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2941.76 | 31665 | GIA | 107000 | RYE 33/11KV | inside-area | 12.77 | Rye Grid | Ninfield | East Sussex Zone | 1.9 | primary | 1.9 | Green | 12.6 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.9 | Rye Grid 33kV | 7 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.2 | 9.6 | Winter | 14.7541 | 1.8 | Green (Over 5% headroom) | 13547 | 43 | 4.67 | 74 | 2 | 53636 | SPN-R000000846906-000-105Z | 200 | 60 | 20-40% | ROMNEY WARREN 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 50107804 | B1 Offices and Workshop businesses | 902 | C | Oil | 3 |  | Heating and Natural Ventilation | 2019-05-20 |  | 0.5 | FALSE | 50.9321 | 0.9076 | SPN-S000000008476 | 15006247000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
956 | 42.4 | UNIT D3, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Warehouse And Premises | industrial | 1 | 1823 | 19623 | GIA | 115000 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.9 | 46 | 19 | 458018 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10009433262 | General Industrial and Special Industrial Groups | 1207 | B | Other | 3 |  | Unconditioned | 2025-04-09 |  | 1 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 12671359000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
957 | 42.4 | UNIT R1, NORTHFLEET INDUSTRIAL ESTATE, LOWER ROAD | GRAVESEND | DA11 9SN | Dartford | SABOTCASTLE LTD | Warehouse And Premises | industrial | 1 | 1723.55 | 18552 | GIA | 108000 | GRAVESEND WEST 33/11KV | inside-area | 0.25 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.74 | 43 | 19 | 459089 | SPN-S000000313723 | 300 | 30 | 0-20% | GRAVESEND WEST 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000544690 | B2 to B7 General Industrial and Special Industrial Groups | 525 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-08-15 |  | 0.67 | FALSE | 51.4517 | 0.31774 | SPN-S000000008511 | 9574521000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
958 | 42.4 | UNIT J1, TOWER WORKS, LOWER ROAD | GRAVESEND | DA11 9BB | Gravesham |  | Warehouse And Premises | industrial | 1 | 1648.91 | 17749 | GIA | 113000 | GRAVESEND WEST 33/11KV | inside-area | 1.09 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.62 | 41 | 19 | 459892 | SPN-R000000851106-000-023Z | 500 | 350 | 60-80% | GRAVESEND WEST 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4597 | 0.31515 | SPN-S000000008511 | 814755000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
959 | 42.4 | R3, NORTHFLEET INDUSTRIAL ESTATE, LOWER ROAD | GRAVESEND | DA11 9SB | Dartford |  | Warehouse And Premises | industrial | 1 | 1487.2 | 16008 | GIA | 99000 | GRAVESEND WEST 33/11KV | inside-area | 0.34 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.36 | 37 | 19 | 461633 | SPN-S000000311077 | 800 | 240 | 20-40% | EBBSFLEET 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.45 | 0.32571 | SPN-S000000008511 | 399044147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
960 | 42.4 | UNITS B1-B2, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Factory And Premises | industrial | 1 | 1479 | 15920 | GIA | 79500 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.35 | 89 | 19 | 461721 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537761 | B2 to B7 General Industrial and Special Industrial Groups | 1442 | E | Oil | 3 | 1 | Heating and Natural Ventilation | 2016-04-11 |  | 1 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 12150867000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
961 | 42.4 | UNIT J3 TOWER WORKS, LOWER ROAD | GRAVESEND | DA11 9BB | Gravesham |  | Factory And Premises | industrial | 1 | 1323.51 | 14246 | GIA | 118000 | GRAVESEND WEST 33/11KV | inside-area | 1.09 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.1 | 79 | 19 | 463395 | SPN-R000000851106-000-023Z | 500 | 350 | 60-80% | GRAVESEND WEST 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4597 | 0.31515 | SPN-S000000008511 | 12004478000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
962 | 42.4 | UNIT C3, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Warehouse And Premises | industrial | 1 | 1321 | 14219 | GIA | 90500 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.1 | 33 | 19 | 463422 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537811 | General Industrial and Special Industrial Groups | 1512 | C | Grid Supplied Electricity | 3 |  | Heating and Mechanical Ventilation | 2023-12-19 |  | 1 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 11292255000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
963 | 42.4 | UNIT C4, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Warehouse And Premises | industrial | 1 | 1321 | 14219 | GIA | 91000 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.1 | 33 | 19 | 463422 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537769 | General Industrial and Special Industrial Groups | 1324 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-12-20 |  | 1 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 8725328000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
964 | 42.4 | UNIT C1, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Warehouse And Premises | industrial | 1 | 1281.1 | 13790 | GIA | 87000 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.04 | 32 | 19 | 463851 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537766 | B2 to B7 General Industrial and Special Industrial Groups | 1292 | D | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2016-07-11 |  | 1 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 10964785000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
965 | 42.4 | UNIT C2, MANOR WAY BUSINESS PARK, MANOR WAY | SWANSCOMBE | DA10 0PP | Dartford |  | Warehouse And Premises | industrial | 1 | 1279.1 | 13768 | GIA | 89500 | GRAVESEND WEST 33/11KV | inside-area | 0.75 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 2.03 | 32 | 19 | 463873 | SPN-S000000311058 | 315 | 94 | 20-40% | SWANSCOMBE 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000537810 | B2 to B7 General Industrial and Special Industrial Groups | 1508 | E | Oil | 3 | 1 | Heating and Natural Ventilation | 2016-07-11 |  | 1 | FALSE | 51.4516 | 0.31016 | SPN-S000000008511 | 11292257000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
966 | 42.4 | UNIT J2 TOWER WORKS, LOWER ROAD | GRAVESEND | DA11 9BB | Gravesham |  | Factory And Premises | industrial | 1 | 1245.88 | 13411 | GIA | 110000 | GRAVESEND WEST 33/11KV | inside-area | 1.09 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 1.98 | 75 | 19 | 464230 | SPN-R000000851106-000-023Z | 500 | 350 | 60-80% | GRAVESEND WEST 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4597 | 0.31515 | SPN-S000000008511 | 12004474000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
967 | 42.4 | UNIT K6, LOWER ROAD, NORTHFLEET INDUSTRIAL ESTATE, NORTHFLEET | GRAVESEND | DA11 9BL | Gravesham |  | Warehouse And Premises | industrial | 1 | 1237 | 13315 | GIA | 116000 | GRAVESEND WEST 33/11KV | inside-area | 0.13 | Northfleet East | Northfleet | West Kent Zone | 9.3 | primary | 9.3 | Green | 19 | 9.6 | Thermal | 0 | 2 | 0 | 2 | 7.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.2 | 16.6 | Winter | 49.4505 | 9 | Green (Over 5% headroom) | 66310 | 100 | 1.97 | 31 | 19 | 464326 | SPN-S000000312297 | 500 | 150 | 20-40% | GRAVESEND WEST 33/11KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012014134 | B2 to B7 General Industrial and Special Industrial Groups | 1248 | C | Grid Supplied Electricity | 3 | 3 | Heating and Natural Ventilation | 2020-07-19 |  | 1 | FALSE | 51.4515 | 0.32171 | SPN-S000000008511 | 13275314000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
968 | 42.3 | UNIT 10, PLATT INDUSTRIAL ESTATE, MAIDSTONE ROAD | SEVENOAKS | TN15 8JA | Tonbridge & Malling |  | Factory And Premises; Workshop And Premises | industrial | 4 | 5667.43 | 61004 | GIA | 414500 | WROTHAM HEATH 33/11KV | inside-area | 1.36 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 20 | 9.01 | 340 | 8 | 234173 | SPN-S000000400329 | 1000 | 900 | 80-100% | WROTHAM HEATH 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062551103 | General Industrial and Special Industrial Groups | 1822 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2025-02-05 |  | 0.67 | FALSE | 51.295 | 0.32132 | SPN-S000000008519 | 14519216000;8552717000;14519214000;14519216000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
969 | 42.3 | UNIT 1, PLATT MILL INDUSTRIAL ESTATE, MILL PLACE, MAIDSTONE ROAD | SEVENOAKS | TN15 8JL | Tonbridge & Malling |  | Warehouse And Premises; Workshop And Premises | industrial | 3 | 4388.03 | 47232 | GIA | 310500 | WROTHAM HEATH 33/11KV | inside-area | 1.35 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 26 | 6.97 | 197 | 8 | 247945 | SPN-S000000393344 | 800 | 560 | 60-80% | WROTHAM HEATH 33/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062551097 | B1 Offices and Workshop businesses | 586 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2017-02-10 |  | 1 | FALSE | 51.2943 | 0.32265 | SPN-S000000008519 | 5361922000;5361924000;5450605000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
970 | 42.3 | 5-6, PLATT INDUSTRIAL ESTATE, MAIDSTONE ROAD | SEVENOAKS | TN15 8JL | Tonbridge & Malling |  | Warehouse And Premises | industrial | 2 | 3144.72 | 33849 | GIA | 228500 | WROTHAM HEATH 33/11KV | inside-area | 1.35 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 36 | 5 | 79 | 8 | 261328 | SPN-S000000393344 | 800 | 560 | 60-80% | WROTHAM HEATH 33/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062551101 | Storage or Distribution | 616 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-01-18 |  | 1 | FALSE | 51.2943 | 0.32265 | SPN-S000000008519 | 5019268000;13532202000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
971 | 42.3 | UNITS 1A 1B & 1C, LEAROYD ROAD | NEW ROMNEY | TN28 8XU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2636.69 | 28381 | GIA | 146000 | ROMNEY WARREN 33/11KV | inside-area | 1.67 | Ruckinge Grid | Sellindge | East Kent Zone | 1.7 | primary | 1.7 | Green | 13 | 9.9 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | Green (Over 5% headroom) | 12121 | 43 | 4.19 | 66 | 5 | 92698 | SPN-S000000364894 | 800 | 560 | 60-80% | ROMNEY WARREN 33/11KV | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50004812 | B8 Storage or Distribution | 1001 | C | Other | 3 |  | Unconditioned | 2013-10-29 |  | 0.75 | FALSE | 50.9836 | 0.95043 | SPN-S000000008469 | 3982897000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
972 | 42.3 | LIBERON WAXES LTD UNIT 1, LEAROYD ROAD | NEW ROMNEY | TN28 8XU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 2 | 2499.5 | 26904 | GIA | 156500 | ROMNEY WARREN 33/11KV | inside-area | 1.67 | Ruckinge Grid | Sellindge | East Kent Zone | 1.7 | primary | 1.7 | Green | 13 | 9.9 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | Green (Over 5% headroom) | 12121 | 45 | 3.97 | 62 | 5 | 94175 | SPN-S000000364894 | 800 | 560 | 60-80% | ROMNEY WARREN 33/11KV | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 50.9836 | 0.95043 | SPN-S000000008469 | 15069817000;15069818000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
973 | 42.3 | UNIT 16, MOUNTFIELD ROAD, MOUNTFIELD INDUSTRIAL ESTATE | NEW ROMNEY | TN28 8LH | Folkestone & Hythe |  | Store And Premises | industrial | 1 | 2445.06 | 26318 | GIA | 146000 | ROMNEY WARREN 33/11KV | inside-area | 1.62 | Ruckinge Grid | Sellindge | East Kent Zone | 1.7 | primary | 1.7 | Green | 13 | 9.9 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | Green (Over 5% headroom) | 12121 | 46 | 3.89 | 61 | 5 | 94761 | SPN-S000000363452 | 500 | 250 | 40-60% | ROMNEY WARREN 33/11KV | 176 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50004196 | Storage or Distribution | 2705 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2026-07-11 |  | 1 | FALSE | 50.9838 | 0.95202 | SPN-S000000008469 | 10038725000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
974 | 42.3 | UNIT 16, ORCHARD PLACE, COMP ROAD | SEVENOAKS | TN15 8QU | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 2212.7 | 23817 | GIA | 226000 | WROTHAM HEATH 33/11KV | inside-area | 2.2 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 51 | 3.52 | 55 | 8 | 271360 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10013922181 | B2 to B7 General Industrial and Special Industrial Groups | 200 | C | Other | 3 |  | Unconditioned | 2013-09-18 |  | 1 | FALSE | 51.2864 | 0.35264 | SPN-S000000008519 | 201700000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
975 | 42.1 | ASDA, MILL WAY | SITTINGBOURNE | ME10 2PD | Swale |  | Superstore And Premises | bigbox | 1 | 7852.24 | 84521 | GIA | 1310000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 45 | 12.48 | 707 | 31 | 2883088 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 |  | Retail/Financial and Professional Services | 14846 | B | Natural Gas | 4 |  | Air Conditioning | 2023-06-05 |  | 1 | FALSE | 51.3515 | 0.73965 | SPN-S000000008585 | 14981471000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
976 | 41.8 | UNIT 3, NORTHERN GATEWAY DISTRIBUTION CENTRE, CENTRAL ROAD | DARTFORD | DA1 5XA | Dartford |  | Warehouse And Premises | industrial | 3 | 30600.75 | 329383 | GIA | 3375000 | DARTFORD GRID B 11KV | inside-area | 0.64 | DARTFORD GRID B 11KV | Littlebrook | SOUTH EAST | 14.5 | primary | 14.5 | Green | 58.5 | 39.3 | Thermal | 16 | 28.1 | 0 | 44.1 | 10 |  |  |  | 0 |  | RED | 2 | 21.5 | 0 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | Green (Over 5% headroom) | 103387 | 31 | 48.63 | 765 | 54 | 2443366 | LPN-S000000073711 | 800 | 400 | 40-60% | DARTFORD GRID B 11KV | 106 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10023445972 | B2 to B7 General Industrial and Special Industrial Groups | 9983 | A | Grid Supplied Electricity | 5 | 2 | Heating and Mechanical Ventilation | 2019-08-22 |  | 1 | FALSE | 51.4533 | 0.21995 | LPN-S000000000716 | 12015234000;12015210000;10723235000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
977 | 41.7 | UNITS 2-2A & 3-4, LEAVERS ESTATE | TONBRIDGE | TN11 8JU | Sevenoaks |  | Factory And Premises | industrial | 1 | 1639.19 | 17644 | GIA | 91000 | PENSHURST 33/11KV | inside-area | 5.14 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.8 | primary | 8.8 | Green | 14.9 | 5.9 | Thermal | 0 | 0 | 0 | 0 | 8.9 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 14.2 | 10.6 | Winter | 60.5634 | 8.6 | Green (Over 5% headroom) | 62745 | 100 | 2.6 | 98 | 1 | 14086 | SPN-S000000441341 | 300 | 150 | 40-60% | PENSHURST 33/11KV | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035182647 | B2 to B7 General Industrial and Special Industrial Groups | 570 | C | Natural Gas | 3 | 2 | Air Conditioning | 2019-09-26 |  | 1 | FALSE | 51.1989 | 0.16935 | SPN-S000000008457 | 6697935000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
978 | 41.7 | PALLET WORKS PENSHURST STATION | TONBRIDGE | TN11 8JD | Sevenoaks | PALLET HANDLING LTD | Factory And Premises | industrial | 1 | 1308.6 | 14086 | GIA | 79000 | PENSHURST 33/11KV | inside-area | 4.5 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.8 | primary | 8.8 | Green | 14.9 | 5.9 | Thermal | 0 | 0 | 0 | 0 | 8.9 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 14.2 | 10.6 | Winter | 60.5634 | 8.6 | Green (Over 5% headroom) | 62745 | 100 | 2.08 | 79 | 1 | 17644 | SPN-S000000451611 | 315 | 220 | 60-80% | PENSHURST 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1933 | 0.1771 | SPN-S000000008457 | 11383274000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
979 | 41.7 | ADJ THE PADDOCK, DOVER ROAD | DEAL | CT14 8HE | Dover | R C CLARINGBOULD & SON LTD | Store And Premises | industrial | 1 | 1274 | 13713 | GIA | 52500 | BETTESHANGER LOCAL 33/11KV | inside-area | 5.26 | Betteshanger Grid | Sellindge | East Kent Zone | 8.8 | primary | 8.8 | Green | 24 | 14.4 | Thermal | 0 | 0 | 0 | 0 | 8.2 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.5 | 17.1 | Winter | 40 | 9.4 | Green (Over 5% headroom) | 62745 | 100 | 2.02 | 32 | 5 | 263022 | SPN-R000000830406-000-061Z | 100 | 10 | 0-20% | BETTESHANGER LOCAL 33/11KV | 225 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1862 | 1.3782 | SPN-S000000008304 | 534230145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
980 | 41.7 | JOHN BYWATER LTD, PIKE ROAD | DOVER | CT15 4ND | Dover |  | Workshop And Premises | industrial | 1 | 1210.6 | 13031 | GIA | 81500 | BETTESHANGER LOCAL 33/11KV | inside-area | 5.3 | Betteshanger Grid | Sellindge | East Kent Zone | 8.8 | primary | 8.8 | Green | 24 | 14.4 | Thermal | 0 | 0 | 0 | 0 | 8.2 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.5 | 17.1 | Winter | 40 | 9.4 | Green (Over 5% headroom) | 62745 | 100 | 1.92 | 54 | 5 | 263704 | SPN-R000000830407-000-134Z | 200 | 100 | 40-60% | BETTESHANGER LOCAL 33/11KV | 119 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2079 | 1.275 | SPN-S000000008304 | 10250039000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
981 | 41.7 | ELLENS ROAD | DEAL | CT14 9JJ | Dover | D I Y MOTORIST | Store And Premises | industrial | 1 | 1104.95 | 11894 | GIA | 54500 | BETTESHANGER LOCAL 33/11KV | inside-area | 3.01 | Betteshanger Grid | Sellindge | East Kent Zone | 8.8 | primary | 8.8 | Green | 24 | 14.4 | Thermal | 0 | 0 | 0 | 0 | 8.2 | Betteshanger Grid 33kV | 23.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 23.5 | 17.1 | Winter | 40 | 9.4 | Green (Over 5% headroom) | 62745 | 100 | 1.76 | 28 | 5 | 264841 | SPN-R000000830406-000-005Z | 100 | 50 | 40-60% | BETTESHANGER LOCAL 33/11KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2082 | 1.3727 | SPN-S000000008304 | 123557145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
982 | 41.5 | LAKEVIEW EAST, GALLEON BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QE | Dartford |  | Offices And Premises | office | 1 | 1595.67 | 17176 | NIA | 317500 | CROSSWAYS | inside-area | 0.32 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 2.54 | 112 | 35 | 5902125 | SPN-S000000324354 | 1000 | 700 | 60-80% | CROSSWAYS | 216 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10023437853 | Offices and Workshop Businesses | 1791 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2025-02-11 |  | 1 | FALSE | 51.4529 | 0.25374 | SPN-S000000008626 | 10888090000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
983 | 41.5 | BELLWAY HOUSE, ANCHOR BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QH | Dartford |  | Offices And Premises | office | 1 | 1398.51 | 15053 | NIA | 300000 | CROSSWAYS | inside-area | 0.37 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 2.22 | 98 | 35 | 5904248 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 124 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000544252 | B1 Offices and Workshop businesses | 5490 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2021-11-12 |  | 0.75 | FALSE | 51.4541 | 0.25254 | SPN-S000000008626 | 12364387000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
984 | 41.5 | 1ST AND 2ND FLRS CP15, VICTORY WAY, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QD | Dartford |  | Offices And Premises | office | 1 | 1120.54 | 12061 | NIA | 250000 | CROSSWAYS | inside-area | 0.49 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 100 | 1.78 | 78 | 35 | 5907240 | SPN-S000000316998 | 1000 | 300 | 20-40% | STONE MARSHES 33/11KV | 186 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4557 | 0.24881 | SPN-S000000008626 | 10888327000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
985 | 41.5 | BERTH 6 & 7 WAREHOUSE (EXCL PT REAR), NORTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SR | Medway |  | Warehouse And Premises | industrial | 1 | 18942.49 | 203895 | GIA | 855000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 30 | 30.1 | 474 | 25 | 911847 | SPN-S000000324509 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 366 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4012 | 0.54713 | SPN-S000000008645 | 14650827000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
986 | 41.5 | UNITS 20 &21, DECIMUS PARK, KINGSTANDING WAY | TUNBRIDGE WELLS | TN2 3GP | Tunbridge Wells |  | Warehouse And Premises | industrial | 6 | 17967.84 | 193404 | GIA | 1409500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.26 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 32 | 28.55 | 449 | 50 | 1629512 | SPN-S000000451313 | 1000 | 900 | 80-100% | TUNBRIDGE WELLS TOWN 11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000068375 | B1 Offices and Workshop businesses | 868 | D | Natural Gas | 3 | 1 | Heating and Mechanical Ventilation | 2014-06-25 |  | 1 | FALSE | 51.1614 | 0.29315 | SPN-S000000008504 | 10517388000;5096726000;4628807000;14979620000;13806134000;14532856000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
987 | 41.5 | BERTHS 3-4, SOUTHSIDE THREE, CHATHAM DOCKYARD | CHATHAM | ME4 4SW | Medway |  | Factory And Premises | industrial | 1 | 14890.51 | 160280 | GIA | 730000 | CHATHAM HILL 33/11KV | inside-area | 2.66 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 38 | 23.66 | 893 | 25 | 955462 | SPN-S000000311882 | 200 | 60 | 20-40% | CHATHAM HILL 33/11KV | 376 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.4005 | 0.55166 | SPN-S000000008645 | 10599820000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
988 | 41.5 | 2ND FLR 50 PEMBROKE COURT, CHATHAM MARITIME | CHATHAM | ME4 4EL | Medway |  | Offices And Premises | office | 2 | 3059.34 | 32930 | NIA | 595000 | CHATHAM HILL 33/11KV | inside-area | 2.38 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 4.86 | 214 | 25 | 1082812 | SPN-S000000311614 | 1000 | 700 | 60-80% | CHATHAM HILL 33/11KV | 160 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44014236 | Offices and Workshop Businesses | 5012 | A | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2025-10-21 |  | 0.8 | FALSE | 51.3989 | 0.538 | SPN-S000000008645 | 11071358000;11071356000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
989 | 41.5 | GND - 2ND FLRS SOUTH BLOCK COMPASS CENTRE, CHATHAM MARITIME | CHATHAM | ME4 4YH | Medway |  | Offices And Premises | office | 1 | 2982.15 | 32100 | NIA | 455000 | CHATHAM HILL 33/11KV | inside-area | 2.35 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 4.74 | 209 | 25 | 1083642 | SPN-S000000316877 | 500 | 250 | 40-60% | CHATHAM HILL 33/11KV | 164 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | B1 Offices and Workshop businesses | 3486 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2012-05-29 |  | 0.83 | FALSE | 51.3985 | 0.53526 | SPN-S000000008645 | 12834671000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
990 | 41.5 | BRITTON HOUSE, HIGH STREET | GILLINGHAM | ME7 1BE | Medway |  | Offices And Premises | office | 1 | 2063.58 | 22212 | NIA | 220000 | CHATHAM HILL 33/11KV | inside-area | 1.26 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 3.28 | 144 | 25 | 1093530 | SPN-S000000311825 | 500 | 50 | 0-20% | CHATHAM HILL 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000899911 | B1 Offices and Workshop businesses | 682 | E | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2014-06-29 |  | 0.5 | FALSE | 51.3889 | 0.5427 | SPN-S000000008645 | 13044793000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
991 | 41.5 | 155-157, ST JOHNS ROAD | TUNBRIDGE WELLS | TN4 9UP | Tunbridge Wells |  | Offices And Premises | office | 1 | 1972.6 | 21233 | NIA | 272500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.79 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 3.13 | 138 | 50 | 1801683 | SPN-S000000441547 | 500 | 250 | 40-60% | TUNBRIDGE WELLS TOWN 11KV | 103 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1457 | 0.26058 | SPN-S000000008504 | 399240148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
992 | 41.5 | UNIT 1A, LAMBERTS ROAD | TUNBRIDGE WELLS | TN2 3EH | Tunbridge Wells |  | Factory And Premises | industrial | 1 | 1813.71 | 19523 | GIA | 147000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.08 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.88 | 109 | 50 | 1803393 | SPN-S000000442092 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 18 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1523 | 0.28416 | SPN-S000000008504 | 409371148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
993 | 41.5 | CAXTON HOUSE 101-103, HOPEWELL DRIVE | CHATHAM | ME5 7NP | Medway |  | Warehouse And Premises | industrial | 1 | 1681.82 | 18103 | GIA | 105000 | CHATHAM HILL 33/11KV | inside-area | 1.42 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 2.67 | 42 | 25 | 1097639 | SPN-S000000311853 | 500 | 350 | 60-80% | CHATHAM HILL 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 100062392768 | B1 Offices and Workshop businesses | 1048 | A | Grid Supplied Electricity | 4 | 335 | Air Conditioning | 2016-05-05 |  | 0.5 | FALSE | 51.3654 | 0.54671 | SPN-S000000008645 | 8114395000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
994 | 41.5 | UNITS 1 & 2 R/O 9, CANNON LANE | TONBRIDGE | TN9 1PP | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 1610.98 | 17340 | GIA | 87500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.95 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.56 | 72 | 50 | 1805576 | SPN-S000000443020 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002908459 | Storage or Distribution | 858 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-03-08 |  | 0.5 | FALSE | 51.1978 | 0.28554 | SPN-S000000008504 | 11760950000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
995 | 41.5 | FESTIVAL HOUSE, CHAPMAN WAY | TUNBRIDGE WELLS | TN2 3EF | Tunbridge Wells |  | Workshop And Premises | industrial | 1 | 1555.7 | 16745 | GIA | 135000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.97 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.47 | 70 | 50 | 1806171 | SPN-S000000443398 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 59 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008663395 | Storage or Distribution | 2000 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-07-19 |  | 1 | FALSE | 51.1527 | 0.27694 | SPN-S000000008504 | 2836139000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
996 | 41.5 | UNITS 8A/8B & 9 CANNON BRIDGE WORKS, CANNON LANE | TONBRIDGE | TN9 1PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1524.81 | 16413 | GIA | 169000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.95 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.42 | 38 | 50 | 1806503 | SPN-S000000443020 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062628759 | B2 to B7 General Industrial and Special Industrial Groups | 355 | E | LPG | 3 |  | Heating and Natural Ventilation | 2021-07-08 |  | 1 | FALSE | 51.1978 | 0.28554 | SPN-S000000008504 | 14601644000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
997 | 41.5 | 12, DRAYTON ROAD | TONBRIDGE | TN9 2BE | Tonbridge & Malling |  | Factory And Premises | industrial | 1 | 1487.3 | 16009 | GIA | 142000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 1.21 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.36 | 89 | 50 | 1806907 | SPN-S000000441570 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1868 | 0.27646 | SPN-S000000008504 | 185830148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
998 | 41.5 | UNITS 2 & 3 (AKA UNITS C AND D), CANNON BRIDGE INDUSTRIAL ESTATE, CANNON LANE | TONBRIDGE | TN9 1PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1474.91 | 15876 | GIA | 129000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.95 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.34 | 37 | 50 | 1807040 | SPN-S000000443020 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1978 | 0.28554 | SPN-S000000008504 | 14195939000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
999 | 41.5 | UNIT 1, PRIORY ROAD | TONBRIDGE | TN9 2AF | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1403.66 | 15109 | GIA | 118000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.85 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.23 | 35 | 50 | 1807807 | SPN-S000000442274 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062594361 | B1 Offices and Workshop businesses | 1479 | C | Oil | 3 |  | Heating and Natural Ventilation | 2018-01-12 |  | 1 | FALSE | 51.1903 | 0.27688 | SPN-S000000008504 | 5031274000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1000 | 41.5 | R/O C BREWER & SONS LTD, NORTH FARM ROAD | TUNBRIDGE WELLS | TN2 3DR | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1325.1 | 14263 | GIA | 116000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.01 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.11 | 33 | 50 | 1808653 | SPN-S000000442197 | 800 | 560 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554296 | B8 Storage or Distribution | 1117 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2021-07-20 |  | 0.67 | FALSE | 51.1525 | 0.2797 | SPN-S000000008504 | 390574148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1001 | 41.5 | C BREWER & SONS LTD, NORTH FARM ROAD | TUNBRIDGE WELLS | TN2 3DR | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1312.1 | 14123 | GIA | 125000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 5.01 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.09 | 33 | 50 | 1808793 | SPN-S000000442197 | 800 | 560 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554296 | B8 Storage or Distribution | 1117 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2021-07-20 |  | 0.67 | FALSE | 51.1525 | 0.2797 | SPN-S000000008504 | 390573148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1002 | 41.5 | UNIT 1 (AKA UNIT A), CANNON BRIDGE INDUSTRIAL ESTATE, CANNON LANE | TONBRIDGE | TN9 1PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1306.7 | 14065 | GIA | 97500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.95 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 2.08 | 33 | 50 | 1808851 | SPN-S000000443020 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002908459 | Storage or Distribution | 858 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-03-08 |  | 1 | FALSE | 51.1978 | 0.28554 | SPN-S000000008504 | 14297769000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1003 | 41.5 | 302, CANTERBURY STREET | GILLINGHAM | ME7 5JP | Medway |  | Factory And Premises | industrial | 1 | 1204 | 12960 | GIA | 58000 | CHATHAM HILL 33/11KV | inside-area | 0.67 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 1.91 | 72 | 25 | 1102782 | SPN-S000000311869 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44038377 | B1 Offices and Workshop businesses | 1366 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-03-20 |  | 1 | FALSE | 51.3773 | 0.55024 | SPN-S000000008645 | 57196147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1004 | 41.5 | UNIT 11, CANNON BRIDGE WORKS, CANNON LANE | TONBRIDGE | TN9 1PP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1116.86 | 12022 | GIA | 113000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.95 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.77 | 28 | 50 | 1810894 | SPN-S000000443020 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1978 | 0.28554 | SPN-S000000008504 | 7554778000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1005 | 41.5 | UNITS 1 & 2 AT 101-109, BEACON ROAD | CHATHAM | ME5 7BP | Medway |  | Warehouse And Premises | industrial | 1 | 1109.1 | 11938 | GIA | 42250 | CHATHAM HILL 33/11KV | inside-area | 0.57 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 1.76 | 28 | 25 | 1103804 | SPN-S000000311854 | 500 | 150 | 20-40% | CHATHAM HILL 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3735 | 0.54546 | SPN-S000000008645 | 397160147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1006 | 41.5 | 14-15, SPA INDUSTRIAL PARK, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EN | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1077.34 | 11596 | GIA | 151000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.99 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.71 | 27 | 50 | 1811320 | SPN-S000000443773 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554234 | B8 Storage or Distribution | 1024 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-10-16 |  | 1 | FALSE | 51.1536 | 0.28806 | SPN-S000000008504 | 10483594000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1007 | 41.5 | UNIT 2A OWENS WAY, GADS HILL | GILLINGHAM | ME7 2RR | Medway |  | Factory And Premises | industrial | 1 | 1075 | 11571 | GIA | 68000 | CHATHAM HILL 33/11KV | inside-area | 2.68 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 1.71 | 64 | 25 | 1104171 | SPN-S000000311961 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3909 | 0.57283 | SPN-S000000008645 | 13557152000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1008 | 41.5 | UNIT 2B OWENS WAY, GADS HILL | GILLINGHAM | ME7 2RR | Medway |  | Factory And Premises | industrial | 1 | 1075 | 11571 | GIA | 57500 | CHATHAM HILL 33/11KV | inside-area | 2.68 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 1.71 | 64 | 25 | 1104171 | SPN-S000000311961 | 800 | 560 | 60-80% | CHATHAM HILL 33/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3909 | 0.57283 | SPN-S000000008645 | 13557149000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1009 | 41.5 | RAINHAM ROAD | GILLINGHAM | ME7 5LS | Medway | JUBILEE COMPONENTS LTD | Factory And Premises | industrial | 1 | 1058.6 | 11395 | GIA | 52000 | CHATHAM HILL 33/11KV | inside-area | 0.68 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 1.68 | 64 | 25 | 1104347 | SPN-S000000311863 | 300 | 30 | 0-20% | CHATHAM HILL 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 200000899690 | A1/A2 Retail and Financial/Professional services | 97 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-01-19 |  | 1 | FALSE | 51.3743 | 0.54881 | SPN-S000000008645 | 164591147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1010 | 41.5 | BRIDGE HOUSE, NORTH FARM ROAD | TUNBRIDGE WELLS | TN2 3DN | Tunbridge Wells |  | Workshop And Premises | industrial | 1 | 1053.59 | 11341 | GIA | 113000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.9 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.67 | 47 | 50 | 1811575 | SPN-R000000935106-000-003Z | 200 | 180 | 80-100% | TUNBRIDGE WELLS GRID 132/11 | 59 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008663299 | Offices and Workshop Businesses | 897 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2025-06-10 |  | 0.67 | FALSE | 51.1536 | 0.28093 | SPN-S000000008504 | 13974650000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1011 | 41.5 | PT 83-85 & 87, ST JOHNS ROAD | TUNBRIDGE WELLS | TN4 9TU | Tunbridge Wells |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1038.8 | 11182 | GIA | 88000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 6.1 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.65 | 47 | 50 | 1811734 | SPN-S000000442031 | 1000 | 500 | 40-60% | TUNBRIDGE WELLS GRID 132/11 | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1429 | 0.25968 | SPN-S000000008504 | 404341148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1012 | 41.5 | 12, TANNERY ROAD | TONBRIDGE | TN9 1RF | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1037.25 | 11165 | GIA | 97500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.58 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.65 | 26 | 50 | 1811751 | SPN-S000000451154 | 800 | 560 | 60-80% | TONBRIDGE EAST 33/6.6KV | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000966031 | General Industrial and Special Industrial Groups | 1101 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2025-10-02 |  | 1 | FALSE | 51.1939 | 0.27832 | SPN-S000000008504 | 398623148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1013 | 41.5 | DRAYTON ROAD | TONBRIDGE | TN9 2BG | Tonbridge & Malling | SPRINGWELL MOULDINGS LTD | Factory And Premises | industrial | 1 | 1003.4 | 10800 | GIA | 54500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 1.18 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.59 | 60 | 50 | 1812116 | SPN-S000000441570 | 500 | 350 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 24 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1871 | 0.27644 | SPN-S000000008504 | 404725148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1014 | 41.5 | AMETHYST GROUP LTD, LODGE ROAD | TONBRIDGE | TN12 0QW | Maidstone |  | Warehouse And Premises | industrial | 1 | 12508.6 | 134641 | GIA | 840000 | STAPLEHURST 33/6.6KV | inside-area | 0.45 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 6 | 19.88 | 313 | 7 | 279261 | SPN-S000000393957 | 1000 | 700 | 60-80% | STAPLEHURST 33/6.6KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10022893169 | B8 Storage or Distribution | 12118 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2016-06-27 |  | 1 | FALSE | 51.1703 | 0.54812 | SPN-S000000008493 | 13394396000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1015 | 41.5 | LINGFIELD, LINDRIDGE LANE | TONBRIDGE | TN12 0JJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 8238.07 | 88674 | OTH | 37750 | STAPLEHURST 33/6.6KV | inside-area | 0.89 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 9 | 13.09 | 206 | 7 | 325228 | SPN-R000000849305-000-024Z | 50 | 35 | 60-80% | STAPLEHURST 33/6.6KV | 331 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1716 | 0.53448 | SPN-S000000008493 | 341928148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1016 | 41.5 | RHS DK HOLDINGS LTD, STATION APPROACH | TONBRIDGE | TN12 0QR | Maidstone |  | Factory And Premises | industrial | 1 | 4829.9 | 51989 | GIA | 275000 | STAPLEHURST 33/6.6KV | inside-area | 0.58 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 15 | 7.68 | 290 | 7 | 361913 | SPN-S000000393957 | 1000 | 700 | 60-80% | STAPLEHURST 33/6.6KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1707 | 0.55047 | SPN-S000000008493 | 9644166000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1017 | 41.5 | STATION YARD, ROLVENDEN HILL | CRANBROOK | TN17 4QZ | Ashford |  | Factory And Premises | industrial | 1 | 4428.5 | 47668 | GIA | 212000 | TENTERDEN 33/6.6KV | inside-area | 1.87 | Ruckinge Grid | Sellindge | East Sussex Zone | 1.1 | primary | 1.1 | Green | 11.9 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.8 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | Green (Over 5% headroom) | 7843 | 16 | 7.04 | 266 | 5 | 121042 | SPN-R000000837606-000-306Z | 315 | 158 | 40-60% | TENTERDEN 33/6.6KV | 194 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0627 | 0.66053 | SPN-S000000008376 | 15053868000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1018 | 41.5 | HEADCORN ROAD | TONBRIDGE | TN12 0BU | Maidstone | MAGNETIC SHIELDS LTD | Workshop And Premises | industrial | 1 | 4206.68 | 45280 | GIA | 198000 | STAPLEHURST 33/6.6KV | inside-area | 0.86 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 17 | 6.68 | 189 | 7 | 368622 | SPN-S000000393611 | 300 | 150 | 40-60% | STAPLEHURST 33/6.6KV | 156 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10014312793 | D1 Non-residential Institutions - Education | 104 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-06-01 |  | 1 | FALSE | 51.1657 | 0.55697 | SPN-S000000008493 | 148596148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1019 | 41.5 | CASTLETONS OAK SAWMILLS, BENENDEN ROAD | ASHFORD | TN27 8DX | Ashford |  | Workshop And Premises | industrial | 1 | 2417.22 | 26019 | GIA | 77000 | TENTERDEN 33/6.6KV | inside-area | 4.82 | Ruckinge Grid | Sellindge | East Sussex Zone | 1.1 | primary | 1.1 | Green | 11.9 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.8 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | Green (Over 5% headroom) | 7843 | 30 | 3.84 | 109 | 5 | 142691 | SPN-R000000837605-000-141Z | 200 | 140 | 60-80% | TENTERDEN 33/6.6KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0935 | 0.63279 | SPN-S000000008376 | 215046148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1020 | 41.5 | APPLEDORE ROAD | TENTERDEN | TN30 7DE | Ashford | CERIUM CHEMICAL COMPANY | Workshop, Office And Premises | industrial | 1 | 2176.28 | 23425 | GIA | 120000 | TENTERDEN 33/6.6KV | inside-area | 2.01 | Ruckinge Grid | Sellindge | East Sussex Zone | 1.1 | primary | 1.1 | Green | 11.9 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.8 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | Green (Over 5% headroom) | 7843 | 33 | 3.46 | 98 | 5 | 145285 | SPN-S000000363487 | 200 | -20 | -20-0% | TENTERDEN 33/6.6KV | 62 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062567735 | B8 Storage or Distribution | 463 | E | Oil | 3 |  | Heating and Natural Ventilation | 2019-05-17 |  | 1 | FALSE | 51.0626 | 0.71476 | SPN-S000000008376 | 320082148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1021 | 41.5 | 4, LODGE ROAD | TONBRIDGE | TN12 0QY | Maidstone |  | Warehouse And Premises | industrial | 1 | 2029.8 | 21849 | GIA | 142000 | STAPLEHURST 33/6.6KV | inside-area | 0.48 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 36 | 3.23 | 51 | 7 | 392053 | SPN-S000000393957 | 1000 | 700 | 60-80% | STAPLEHURST 33/6.6KV | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 200003679535 | Retail/Financial and Professional Services | 193 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-11-21 |  | 1 | FALSE | 51.1705 | 0.54867 | SPN-S000000008493 | 148961148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1022 | 41.4 | TESCO 475, MARGATE ROAD | BROADSTAIRS | CT10 2QJ | Thanet |  | Superstore And Premises | bigbox | 1 | 13818.19 | 148738 | GIA | 2020000 | ST PETERS 33/11KV | inside-area | 1.86 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 23 | 21.96 | 1244 | 31 | 1345075 | SPN-S000000343300 | 1000 | 700 | 60-80% | THANET 33/11KV | 326 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3589 | 1.4 | SPN-S000000008478 | 13213017000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1023 | 41.4 | GARDEN CENTRE, MONTEFIORE AVENUE | RAMSGATE | CT11 8BW | Thanet |  | Garden Centre And Premises | bigbox | 1 | 10019.85 | 107853 | NIA | 189000 | ST PETERS 33/11KV | inside-area | 3.14 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 32 | 15.92 | 902 | 31 | 1385960 | SPN-S000000342196 | 500 | 250 | 40-60% | ST PETERS 33/11KV | 248 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013308930 | Retail/Financial and Professional Services | 296 | D | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2026-07-15 |  | 1 | FALSE | 51.3445 | 1.4279 | SPN-S000000008478 | 8058866000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1024 | 41.4 | ASDA SUPERSTORE, WESTWOOD ROAD | BROADSTAIRS | CT10 2AL | Thanet |  | Superstore And Premises | bigbox | 1 | 9367.73 | 100833 | GIA | 1570000 | ST PETERS 33/11KV | inside-area | 1.24 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 34 | 14.89 | 843 | 31 | 1392980 | SPN-S000000343532 | 315 | 220 | 60-80% | ST PETERS 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3608 | 1.4143 | SPN-S000000008478 | 9628986000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1025 | 41.4 | UNIT 1A BROADSTAIRS RETAIL PARK, MARGATE ROAD | BROADSTAIRS | CT10 2QW | Thanet |  | Retail Warehouse And Premises | bigbox | 1 | 3549.71 | 38209 | GIA | 515000 | ST PETERS 33/11KV | inside-area | 1.96 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 90 | 5.64 | 319 | 31 | 1455604 | SPN-S000000342227 | 315 | 220 | 60-80% | THANET 33/11KV | 140 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10013308698 | A1/A2 Retail and Financial/Professional services | 5471 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2013-07-09 |  | 1 | FALSE | 51.3574 | 1.4009 | SPN-S000000008478 | 8035672000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1026 | 41.4 | UNIT A1, EAST KENT RETAIL PARK, WESTWOOD ROAD | BROADSTAIRS | CT10 2RQ | Thanet |  | Retail Warehouse And Premises | bigbox | 1 | 3073.54 | 33083 | GIA | 460000 | ST PETERS 33/11KV | inside-area | 1.72 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.88 | 277 | 31 | 1460730 | SPN-S000000343300 | 1000 | 700 | 60-80% | THANET 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003079345 | A1/A2 Retail and Financial/Professional services | 1145 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2022-05-13 |  | 1 | FALSE | 51.3616 | 1.3984 | SPN-S000000008478 | 12017569000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1027 | 41.4 | UNIT 1 BROADSTAIRS RETAIL PARK, MARGATE ROAD | BROADSTAIRS | CT10 2QW | Thanet |  | Retail Warehouse & Premises | bigbox | 1 | 2929.69 | 31535 | GIA | 380000 | ST PETERS 33/11KV | inside-area | 1.96 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.66 | 264 | 31 | 1462278 | SPN-S000000342227 | 315 | 220 | 60-80% | THANET 33/11KV | 140 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 10012957145 | A1/A2 Retail and Financial/Professional services | 972 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2013-07-05 |  | 0.75 | FALSE | 51.3574 | 1.4009 | SPN-S000000008478 | 8035671000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1028 | 41.4 | THE NURSERIES, STAPLEHURST ROAD | TONBRIDGE | TN12 9BS | Maidstone | HIGHGROVE LTD | Garden Centre And Premises | bigbox | 1 | 2886.67 | 31072 | GIA | 74000 | MARDEN 33/11KV | inside-area | 3.61 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 4.59 | 260 | 24 | 888196 | SPN-R000000843207-000-066Z | 200 | 180 | 80-100% |  | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1969 | 0.52974 | SPN-S000000008433 | 3911421000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1029 | 41.4 | QUEEN STREET | RAMSGATE | CT11 9EJ | Thanet | WAITROSE LTD | Superstore And Premises | bigbox | 1 | 2719.56 | 29273 | GIA | 270000 | ST PETERS 33/11KV | inside-area | 4.36 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4.32 | 245 | 31 | 1464540 | SPN-S000000343482 | 1000 | 700 | 60-80% | RAMSGATE 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062283699 | A1/A2 Retail and Financial/Professional services | 128 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2015-08-29 |  | 1 | FALSE | 51.3327 | 1.417 | SPN-S000000008478 | 394944145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1030 | 41.4 | UNIT C AT WESTWOOD RETAIL PARK, WESTWOOD ROAD | BROADSTAIRS | CT10 2FG | Thanet |  | Retail Warehouse And Premises | bigbox | 1 | 2129.6 | 22923 | GIA | 347500 | ST PETERS 33/11KV | inside-area | 1.82 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.38 | 192 | 31 | 1470890 | SPN-S000000342017 | 800 | 560 | 60-80% | THANET 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062627239 | A1/A2 Retail and Financial/Professional services | 4160 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2016-11-08 |  | 1 | FALSE | 51.3622 | 1.3958 | SPN-S000000008478 | 6946351000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1031 | 41.4 | 56, CHATHAM STREET | RAMSGATE | CT11 7PR | Thanet | ASDA | Supermarket And Premises | bigbox | 1 | 2086.81 | 22462 | GIA | 422500 | ST PETERS 33/11KV | inside-area | 3.87 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.32 | 188 | 31 | 1471351 | SPN-S000000342178 | 800 | 560 | 60-80% | RAMSGATE 33/11KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3371 | 1.4156 | SPN-S000000008478 | 9012299000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1032 | 40.9 | OARE ROAD | FAVERSHAM | ME13 7TJ | Swale | GIST (FORMALLY KNOWN AS BOC) | Chill Store, Warehouse And Premises | industrial | 1 | 25487.93 | 274350 | GIA | 1480000 | FAVERSHAM 33/11KV | inside-area | 2.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 21 | 40.5 | 637 | 21 | 819685 | SPN-S000000391868 | 500 | 350 | 60-80% | FAVERSHAM 33/11KV | 131 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3262 | 0.88243 | SPN-S000000008405 | 332613147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1033 | 40.9 | BUILDING 800, GUILLAT AVENUE, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8GU | Swale |  | Offices And Premises | office | 4 | 7880.09 | 84821 | NIA | 890000 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.33 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 69 | 12.52 | 552 | 25 | 1130556 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023202012 | B2 to B7 General Industrial and Special Industrial Groups | 2970 | E | District Heating | 4 | 1 | Heating and Mechanical Ventilation | 2013-10-15 |  | 0.75 | FALSE | 51.3121 | 0.72601 | SPN-S000000008444 | 13259748000;4898459000;4172151000;13259748000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1034 | 40.9 | 750, SHIMMIN ROAD, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8SX | Swale |  | Offices And Premises | office | 1 | 6107.16 | 65737 | NIA | 625000 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.45 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 89 | 9.7 | 428 | 25 | 1149640 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3108 | 0.725 | SPN-S000000008444 | 10038955000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1035 | 40.9 | 700, WINCH ROAD, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8AG | Swale |  | Computer Centre And Premises | office | 1 | 2591.72 | 27897 | GIA | 330000 | SITTINGBOURNE WEST 33/11KV | inside-area | 2.96 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 4.12 | 181 | 25 | 1187480 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002532043 | B2 to B7 General Industrial and Special Industrial Groups | 1086 | C | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2021-04-30 |  | 0.67 | FALSE | 51.3153 | 0.72409 | SPN-S000000008444 | 7707120000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1036 | 40.9 |  | SITTINGBOURNE | ME9 8AQ | Swale | BROAD OAK ENTERPRISES LTD | Workshop And Premises | industrial | 1 | 1714.29 | 18452 | GIA | 57500 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.38 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.72 | 77 | 25 | 1196925 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3129 | 0.73248 | SPN-S000000008444 | 335484147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1037 | 40.9 | BUILDING 740, HEELEY CLOSE, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8HL | Swale |  | Laboratory And Premises | industrial | 1 | 1666.3 | 17936 | NIA | 225000 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.36 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.65 | 167 | 25 | 1197441 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10035066013 | B2 to B7 General Industrial and Special Industrial Groups | 1411 | D | District Heating | 4 | 2 | Heating and Mechanical Ventilation | 2021-05-02 |  | 0.75 | FALSE | 51.3121 | 0.72761 | SPN-S000000008444 | 5210156000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1038 | 40.9 | THE CHALK PIT, LADE WOOD HILL | SITTINGBOURNE | ME9 0ED | Swale |  | Workshop And Premises | industrial | 1 | 1599.79 | 17220 | GIA | 96000 | SITTINGBOURNE WEST 33/11KV | inside-area | 7.18 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.54 | 72 | 25 | 1198157 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.2806 | 0.75063 | SPN-S000000008444 | 9071689000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1039 | 40.9 | DUNSTER HOUSE, STAPLE STREET | FAVERSHAM | ME13 9HY | Swale |  | Warehouse And Premises | industrial | 1 | 1480.74 | 15939 | GIA | 111000 | FAVERSHAM 33/11KV | inside-area | 1.75 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 2.35 | 37 | 21 | 1078096 | SPN-R000000840510-000-035Z | 200 | 140 | 60-80% | FAVERSHAM 33/11KV | 41 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10094602776 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 422 | A | Waste Heat | 4 |  | Heating and Natural Ventilation | 2023-08-04 |  | 0.5 | FALSE | 51.3093 | 0.93615 | SPN-S000000008405 | 8428913000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1040 | 40.9 | R S FRENCH, WATERHAM BUSINESS PARK, HIGH STREET ROAD | FAVERSHAM | ME13 9EJ | Swale |  | Workshop And Premises | industrial | 1 | 1477.56 | 15904 | GIA | 109000 | FAVERSHAM 33/11KV | inside-area | 4.9 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 2.35 | 66 | 21 | 1078131 | SPN-S000000342968 | 500 | 250 | 40-60% | FAVERSHAM 33/11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10094600364 | B2 to B7 General Industrial and Special Industrial Groups | 993 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-05-10 |  | 0.5 | FALSE | 51.3258 | 0.97884 | SPN-S000000008405 | 11955387000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1041 | 40.9 | OARE ROAD | FAVERSHAM | ME13 7JT | Swale | EAST KENT JOINERY LTD | Factory And Premises | industrial | 1 | 1471.6 | 15840 | GIA | 66000 | FAVERSHAM 33/11KV | inside-area | 1.82 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 2.34 | 88 | 21 | 1078195 | SPN-S000000391883 | 500 | 150 | 20-40% | FAVERSHAM 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3163 | 0.88611 | SPN-S000000008405 | 334040147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1042 | 40.9 | UNIT 3, FAVERSHAM SHIPYARD INDUSTRIAL ESTATE, UPPER BRENTS | FAVERSHAM | ME13 7DX | Swale |  | Workshop And Premises | industrial | 1 | 1431.37 | 15407 | GIA | 84500 | FAVERSHAM 33/11KV | inside-area | 1.48 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 2.27 | 64 | 21 | 1078628 | SPN-S000000391892 | 800 | 560 | 60-80% | FAVERSHAM 33/11KV | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3167 | 0.89129 | SPN-S000000008405 | 11367418000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1043 | 40.9 | 1A, ABBEY STREET | FAVERSHAM | ME13 7BE | Swale |  | Artists Workshop And Premises | industrial | 1 | 1366 | 14703 | GIA | 56000 | FAVERSHAM 33/11KV | inside-area | 1.4 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 2.17 | 61 | 21 | 1079332 | SPN-S000000391894 | 300 | 150 | 40-60% | FAVERSHAM 33/11KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062379473 | Non-residential Institutions: Libraries, Museums, and Galleries | 1430 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-03-21 |  | 0.5 | FALSE | 51.3183 | 0.89366 | SPN-S000000008405 | 6990938000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1044 | 40.9 | GARLAND HOUSE, RAWLING STREET | SITTINGBOURNE | ME9 0RT | Swale |  | Warehouse And Premises | industrial | 1 | 1305.59 | 14053 | GIA | 79500 | SITTINGBOURNE WEST 33/11KV | inside-area | 4.51 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.07 | 33 | 25 | 1201324 | SPN-S000000394222 | 100 | 30 | 20-40% | SITTINGBOURNE WEST 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062090959 | B8 Storage or Distribution | 1305 | A | Grid Supplied Electricity | 4 |  | Heating and Mechanical Ventilation | 2013-05-24 |  | 0.5 | FALSE | 51.3026 | 0.73445 | SPN-S000000008444 | 13810556000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1045 | 40.9 | AGRII, LONDON ROAD | FAVERSHAM | ME13 9LG | Swale |  | Warehouse And Premises | industrial | 1 | 1255.2 | 13511 | GIA | 93000 | FAVERSHAM 33/11KV | inside-area | 5.26 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 1.99 | 31 | 21 | 1080524 | SPN-S000000343492 | 315 | 220 | 60-80% | FAVERSHAM 33/11KV | 196 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.2915 | 0.97926 | SPN-S000000008405 | 14988527000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1046 | 40.9 | UNITS 1-6, UPPER BRENTS INDUSTRIAL ESTATE, NORTH QUAY, UPPER BRENTS | FAVERSHAM | ME13 7DZ | Swale | 3D DISPLAYS LTD | Workshop And Premises | industrial | 1 | 1218.8 | 13119 | GIA | 53500 | FAVERSHAM 33/11KV | inside-area | 1.55 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 1.94 | 55 | 21 | 1080916 | SPN-S000000393216 | 500 | 250 | 40-60% | FAVERSHAM 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.322 | 0.89511 | SPN-S000000008405 | 8018258000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1047 | 40.9 | EAST KENT INTERNATIONAL FREIGHT TERMINAL | FAVERSHAM | ME13 9EN | Swale | KENT TRUCK SERVICES | Vehicle Repair Workshop And Premises | industrial | 1 | 1211.3 | 13038 | GIA | 101000 | FAVERSHAM 33/11KV | inside-area | 5.52 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 1.92 | 55 | 21 | 1080997 | SPN-R000000851608-000-178Z | 200 | 140 | 60-80% | FAVERSHAM 33/11KV | 157 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062380780 | B1 Offices and Workshop businesses | 1169 | C | LPG | 3 |  | Heating and Natural Ventilation | 2021-07-22 |  | 1 | FALSE | 51.3248 | 0.98862 | SPN-S000000008405 | 1308600000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1048 | 40.9 | SORTING OFFICE, EAST STREET | FAVERSHAM | ME13 8AA | Swale |  | Sorting Office And Premises | industrial | 1 | 1086.32 | 11693 | NIA | 71000 | FAVERSHAM 33/11KV | inside-area | 1.34 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 1.73 | 76 | 21 | 1082342 | SPN-S000000394047 | 500 | 150 | 20-40% | FAVERSHAM 33/11KV | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3149 | 0.89261 | SPN-S000000008405 | 13775242000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1049 | 40.9 | 771, SHIMMIN ROAD, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8AG | Swale |  | Workshop And Premises | industrial | 1 | 1021.6 | 10996 | GIA | 50500 | SITTINGBOURNE WEST 33/11KV | inside-area | 2.96 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 1.62 | 46 | 25 | 1204381 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002532043 | B2 to B7 General Industrial and Special Industrial Groups | 1086 | C | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2021-04-30 |  | 0.67 | FALSE | 51.3153 | 0.72409 | SPN-S000000008444 | 9670770000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1050 | 40.9 | ASDA STORES LTD, THAMES WAY | GRAVESEND | DA11 0DQ | Gravesham |  | Superstore And Premises | bigbox | 1 | 11737.44 | 126341 | GIA | 1540000 | ROSHERVILLE 33/6.6KV | inside-area | 0.49 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 25 | 18.65 | 1056 | 14 | 1864515 | SPN-S000000311495 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4442 | 0.36056 | SPN-S000000008470 | 13537069000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1051 | 40.9 | WYEVALE GARDEN CENTRE, ERIDGE ROAD | TUNBRIDGE WELLS | TN4 8HP | Tunbridge Wells |  | Garden Centre And Premises | bigbox | 1 | 6909.02 | 74368 | NIA | 145000 | TUNBRIDGE WELLS TOWN 11KV | inside-area | 2.4 | Tunbridge Wells Total | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 7.4 | 2.8 | Thermal | 0 | 5.6 | 0 | 5.6 | 4.1 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 7.2 | 6.5 | Winter | 62.5 | 4.5 | Green (Over 5% headroom) | 31373 | 42 | 10.98 | 622 | 2 | 103686 | SPN-S000000443159 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS TOWN 11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1237 | 0.24794 | SPN-S000000007371 | 12185392000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1052 | 40.9 | WICKES, STUART ROAD | GRAVESEND | DA11 0BZ | Gravesham |  | Retail Warehouse And Premises | bigbox | 1 | 4220.5 | 45429 | GIA | 375000 | ROSHERVILLE 33/6.6KV | inside-area | 0.71 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 69 | 6.71 | 380 | 14 | 1945427 | SPN-S000000324224 | 800 | 400 | 40-60% | ROSHERVILLE 33/6.6KV | 38 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4437 | 0.36432 | SPN-S000000008470 | 6297482000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1053 | 40.9 | UNIT A, IMPERIAL RETAIL PARK, THAMES WAY | GRAVESEND | DA11 0DQ | Gravesham |  | Retail Warehouse And Premises | bigbox | 1 | 4202.7 | 45237 | GIA | 492500 | ROSHERVILLE 33/6.6KV | inside-area | 0.49 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 69 | 6.68 | 378 | 14 | 1945619 | SPN-S000000311495 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062310618 | Retail/Financial and Professional Services | 3454 | B | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2024-04-11 |  | 1 | FALSE | 51.4442 | 0.36056 | SPN-S000000008470 | 12460998000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1054 | 40.9 | BST PT GND PT 1ST & 2ND FLR 72-73, NEW ROAD | GRAVESEND | DA11 0AF | Gravesham |  | Superstore And Premises | bigbox | 1 | 3353.3 | 36095 | GIA | 285000 | ROSHERVILLE 33/6.6KV | inside-area | 0.92 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 87 | 5.33 | 302 | 14 | 1954761 | SPN-S000000312267 | 1000 | 500 | 40-60% | GRAVESEND TOWN 33/6.6KV | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012013454 | Retail/Financial and Professional Services | 1455 | A | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-03-16 |  | 0.75 | FALSE | 51.4423 | 0.36778 | SPN-S000000008470 | 8835944000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1055 | 40.9 | THAMES WAY | GRAVESEND | DA11 9QJ | Gravesham | BUILDER CENTER LTD | Builders Merchants And Premises | bigbox | 1 | 2150.99 | 23153 | GIA | 322500 | ROSHERVILLE 33/6.6KV | inside-area | 0.56 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 3.42 | 194 | 14 | 1967703 | SPN-S000000314624 | 800 | 560 | 60-80% | ROSHERVILLE 33/6.6KV | 228 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012011256 | Retail/Financial and Professional Services | 3051 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-07-16 |  | 1 | FALSE | 51.4386 | 0.34864 | SPN-S000000008470 | 96519147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1056 | 40.8 | PIVINGTON MILL | ASHFORD | TN27 0PG | Ashford | COLE IRONCRAFT LTD; SCALDERHURST LTD | Warehouse And Premises; Workshop And Premises | industrial | 2 | 7514.94 | 80890 | GIA | 361000 | LITTLE CHART 33/6.6KV | inside-area | 2.35 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 5 | 11.94 | 338 | 9 | 525448 | SPN-S000000361131 | 500 | 150 | 20-40% | LITTLE CHART 33/6.6KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012861543 | B1 Offices and Workshop businesses | 322 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-11-28 |  | 1 | FALSE | 51.1862 | 0.74657 | SPN-S000000008428 | 11388060000;84813000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1057 | 40.8 | HIGHWAYS DEPOT, CANTERBURY ROAD | ASHFORD | TN25 4DF | Ashford |  | Storage Depot And Premises | industrial | 1 | 4160 | 44778 | OTH | 41500 | LITTLE CHART 33/6.6KV | inside-area | 7.51 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 10 | 6.61 | 104 | 9 | 561560 | SPN-R000000842809-000-096Z | 200 | 100 | 40-60% | LITTLE CHART 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2179 | 0.8672 | SPN-S000000008428 | 328012148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1058 | 40.8 | ASHFORD ROAD | ASHFORD | TN27 0JL | Ashford | DEPOT | Storage Depot And Premises | industrial | 1 | 2579.1 | 27761 | OTH | 45750 | LITTLE CHART 33/6.6KV | inside-area | 3.25 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 15 | 4.1 | 64 | 9 | 578577 | SPN-S000000361744 | 200 | 100 | 40-60% | LITTLE CHART 33/6.6KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062563582 | B2 to B7 General Industrial and Special Industrial Groups | 2315 | D | Oil | 3 |  | Heating and Natural Ventilation | 2017-04-01 |  | 1 | FALSE | 51.2065 | 0.79624 | SPN-S000000008428 | 1351234000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1059 | 40.8 | CATCHPOLE AND RYE SARACENS DAIRY, JOBBS LANE | ASHFORD | TN27 0SA | Ashford |  | Workshop And Premises | industrial | 1 | 2557.77 | 27532 | GIA | 121000 | LITTLE CHART 33/6.6KV | inside-area | 1.72 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 16 | 4.06 | 115 | 9 | 578806 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012861615 | B8 Storage or Distribution | 1342 | B | Other | 4 |  | Unconditioned | 2020-02-21 |  | 0.75 | FALSE | 51.1643 | 0.7734 | SPN-S000000008428 | 13700547000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1060 | 40.8 | FORD MILL, THE STREET | ASHFORD | TN27 0QA | Ashford |  | Warehouse And Premises | industrial | 1 | 2368.1 | 25490 | GIA | 126000 | LITTLE CHART 33/6.6KV | inside-area | 0.14 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 17 | 3.76 | 59 | 9 | 580848 | SPN-S000000361139 | 400 | 280 | 60-80% | LITTLE CHART 33/6.6KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1807 | 0.77896 | SPN-S000000008428 | 224823148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1061 | 40.7 | TRAVIS PERKINS, NORFOLK ROAD | GRAVESEND | DA12 2PS | Gravesham |  | Builders Merchants And Premises | bigbox | 1 | 2000.6 | 21534 | GIA | 152000 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.38 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 3.18 | 180 | 10 | 396392 | SPN-S000000312283 | 300 | 90 | 20-40% | GRAVESEND TOWN 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062311780 | B2 to B7 General Industrial and Special Industrial Groups | 554 | D | Oil | 3 |  | Heating and Natural Ventilation | 2021-10-13 |  | 0.5 | FALSE | 51.4414 | 0.38944 | SPN-S000000008409 | 406670147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1062 | 40.3 | EUROPA, LITTLEBROOK DC1, SHIELD ROAD | DARTFORD | DA1 5UR | Dartford |  | Warehouse And Premises | industrial | 1 | 27865.8 | 299945 | GIA | 2860000 | PURFLEET PRIMARY | inside-area | 1.88 | Purfleet Grid 33 | Warley | HAROLD HILL | 7.7 | primary | 7.7 | Green | 21.2 | 11.9 | Thermal | 0 | 0 | 0 | 0 | 8.1 | Purfleet Grid 33kV | 23.5 | GREEN | 36.6 | 19.8 | GREEN | 10 | 1007.5 | 2 | 20.4 | 17 | Summer | 43.5294 | 7.4 | Green (Over 5% headroom) | 54902 | 18 | 44.28 | 697 | 1 | 47562 | [9 empty] | Warley | WARLEY | 8 | 1710.9 | 1710.9 | 0 | 0 | 205.9 | 2027-08 | [12 empty] | 51.4633 | 0.24357 | EPN-S0000000H7013 | 9892741000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1063 | 40 | UNIT 1, POWERHOUSE DRIVE | DARTFORD | DA1 5XU | Dartford |  | Warehouse And Premises | industrial | 1 | 220757.62 | 2376213 | GIA | 13630000 | CROSSWAYS | inside-area | 1.61 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 4 | 350.8 | 5519 | 35 | 3543088 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094158014 | B8 Storage or Distribution | 214598 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2021-07-29 |  | 1 | FALSE | 51.4653 | 0.24442 | SPN-S000000008626 | 13524330000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1064 | 40 | UNIT 1, HARRIS WAY | DARTFORD | DA1 5XT | Dartford |  | Warehouse And Premises | industrial | 2 | 84688.9 | 911583 | GIA | 10820000 | CROSSWAYS | inside-area | 1.51 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 10 | 134.58 | 2117 | 35 | 5007718 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094158013 | B8 Storage or Distribution | 42234 | A | Natural Gas | 5 |  | Air Conditioning | 2021-09-30 |  | 1 | FALSE | 51.4636 | 0.24091 | SPN-S000000008626 | 14304459000;14304459000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1065 | 40 | 3, CLIPPER BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QB | Dartford |  | Warehouse And Premises | industrial | 3 | 47683.43 | 513260 | GIA | 5590000 | CROSSWAYS | inside-area | 1.18 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 18 | 75.77 | 1192 | 35 | 5406041 | SPN-S000000314562 | 500 | 350 | 60-80% | CROSSWAYS | 375 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4551 | 0.2658 | SPN-S000000008626 | 14122130000;14672032000;14122127000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1066 | 40 | ASDA DISTRIBUTION CENTRE, GALLEON BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 6QL | Dartford |  | Warehouse And Premises | industrial | 1 | 31789.7 | 342181 | GIA | 3600000 | CROSSWAYS | inside-area | 0.52 | Northfleet East | Northfleet | West Kent Zone | 13.1 | primary | 13.1 | Green | 24 | 7.2 | Thermal | 1 | 8.2 | 0 | 9.2 | 13.4 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | Green (Over 5% headroom) | 93405 | 27 | 50.52 | 795 | 35 | 5577120 | SPN-S000000311176 | 1000 | 500 | 40-60% | CROSSWAYS | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4535 | 0.25646 | SPN-S000000008626 | 170899147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1067 | 40 | UNIT B1, ASHFORD BUSINESS PARK, BARREY ROAD | ASHFORD | TN24 0SG | Ashford |  | Warehouse And Premises | industrial | 1 | 10526.89 | 113310 | GIA | 680000 | SEVINGTON 33/11KV | inside-area | 1.04 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 16.73 | 263 | 28 | 942115 | SPN-S000000364337 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1299 | 0.90543 | SPN-S000000008595 | 10030403000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1068 | 40 | UNIT C1, FOSTER ROAD, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Factory And Premises | industrial | 1 | 7035.03 | 75724 | GIA | 480000 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 11.18 | 422 | 28 | 979701 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560432 | A1/A2 Retail and Financial/Professional services | 2615 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2021-04-19 |  | 0.67 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 8975469000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1069 | 40 | THE BOULEVARD, ORBITAL PARK | ASHFORD | TN24 0SA | Ashford | MEGGITT PLC | Factory And Premises | industrial | 1 | 5014.6 | 53977 | GIA | 395000 | SEVINGTON 33/11KV | inside-area | 0.4 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 7.97 | 301 | 28 | 1001448 | SPN-S000000371114 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 128 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1302 | 0.89574 | SPN-S000000008595 | 5863069000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1070 | 40 | UNIT D, FOSTER ROAD, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Warehouse And Premises | industrial | 1 | 3401.51 | 36614 | GIA | 195000 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 5.41 | 85 | 28 | 1018811 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012882189 | Storage or Distribution | 1907 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-07-16 |  | 1 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 15039262000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1071 | 40 | UNIT 7, HALL AVENUE, ORBITAL PARK | ASHFORD | TN24 0AA | Ashford |  | Warehouse And Premises; Warehouse, Offices And Premises | industrial | 3 | 3358.16 | 36147 | GIA | 335000 | SEVINGTON 33/11KV | inside-area | 0.69 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 5.34 | 235 | 28 | 1019278 | SPN-S000000371288 | 500 | 350 | 60-80% | SEVINGTON 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012870226 | B8 Storage or Distribution | 1376 | B | Grid Supplied Electricity | 5 |  | Heating and Mechanical Ventilation | 2016-12-07 |  | 0.67 | FALSE | 51.1282 | 0.9006 | SPN-S000000008595 | 11588596000;10567732000;13538643000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1072 | 40 | COBALT HOUSE, MONUMENT WAY, ORBITAL PARK | ASHFORD | TN24 0HB | Ashford |  | Warehouse And Premises | industrial | 1 | 3243.49 | 34913 | GIA | 272500 | SEVINGTON 33/11KV | inside-area | 0.12 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 5.15 | 81 | 28 | 1020512 | SPN-S000000364953 | 800 | 400 | 40-60% | SEVINGTON 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1273 | 0.8905 | SPN-S000000008595 | 13842784000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1073 | 40 | THE BOULEVARD, ORBITAL PARK | ASHFORD | TN24 0GA | Ashford | MARUWA EUROPE LTD | Factory And Premises | industrial | 1 | 3010.1 | 32400 | GIA | 310000 | SEVINGTON 33/11KV | inside-area | 0.24 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 4.78 | 181 | 28 | 1023025 | SPN-S000000371004 | 800 | 560 | 60-80% | SEVINGTON 33/11KV | 187 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012852085 | B1 Offices and Workshop businesses | 4233 | D | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2015-11-26 |  | 1 | FALSE | 51.1291 | 0.89403 | SPN-S000000008595 | 2215988000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1074 | 40 | UNITS B&C, FOSTER ROAD, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Warehouse And Premises | industrial | 1 | 2866.35 | 30853 | GIA | 250000 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 4.55 | 72 | 28 | 1024572 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004378748 | Storage or Distribution | 1281 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-07-16 |  | 1 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 15039260000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1075 | 40 | UNITS 200-2 - 200-4 GOODCHEAP FARM, GOODCHEAP LANE | ASHFORD | TN25 5NS | Ashford |  | Warehouse And Premises | industrial | 2 | 2839.92 | 30569 | GIA | 106750 | SEVINGTON 33/11KV | inside-area | 3.59 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 4.51 | 71 | 28 | 1024856 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Storage or Distribution | 2053 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-10-18 |  | 0.5 | FALSE | 51.1521 | 0.9257 | SPN-S000000008595 | 13623682000;7875782000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1076 | 40 | L'ARTISAN DU CHOCOLAT LTD, THE LONG BARROW, ORBITAL PARK | ASHFORD | TN24 0GA | Ashford |  | Factory And Premises | industrial | 1 | 2188.8 | 23560 | GIA | 227000 | SEVINGTON 33/11KV | inside-area | 0.24 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 3.48 | 131 | 28 | 1031865 | SPN-S000000371004 | 800 | 560 | 60-80% | SEVINGTON 33/11KV | 187 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012877167 | Offices and Workshop Businesses | 2176 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2024-11-08 |  | 0.5 | FALSE | 51.1291 | 0.89403 | SPN-S000000008595 | 5197896000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1077 | 40 | CROWBRIDGE ROAD, ORBITAL PARK | ASHFORD | TN24 0GR | Ashford | TYREWEB LTD | Warehouse And Premises | industrial | 1 | 1972.7 | 21234 | GIA | 224000 | SEVINGTON 33/11KV | inside-area | 0.42 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 3.13 | 49 | 28 | 1034191 | SPN-S000000371114 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012846670 | A1/A2 Retail and Financial/Professional services | 1792 | C | Natural Gas | 4 | 1 | Heating and Mechanical Ventilation | 2017-10-12 |  | 0.5 | FALSE | 51.1313 | 0.89467 | SPN-S000000008595 | 5359727000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1078 | 40 | UNIT H, FOSTER ROAD, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Warehouse And Premises | industrial | 1 | 1893.98 | 20387 | GIA | 167000 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 3.01 | 47 | 28 | 1035038 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560434 | Storage or Distribution | 2046 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-07-16 |  | 1 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 15039263000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1079 | 39.8 | ALDI DISTRIBUTION CENTRE, THOMSETT WAY | QUEENBOROUGH | ME11 5AR | Swale |  | Warehouse And Premises | industrial | 1 | 60036.65 | 646228 | GIA | 5490000 | QUEENBOROUGH 33/6.6KV | inside-area | 0.81 | Sheerness Grid | Kemsley | Mid Kent Zone | 13 | primary | 13 | Green | 22.9 | 5.9 | Thermal | 0 | 1.5 | 7.8 | 1.5 | 11.8 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | Green (Over 5% headroom) | 92692 | 14 | 95.4 | 1501 | 15 | 493824 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023204023 | B8 Storage or Distribution | 54609 | A | Natural Gas | 4 |  | Air Conditioning | 2018-07-26 |  | 1 | FALSE | 51.4107 | 0.7579 | SPN-S000000008368 | 12258421000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1080 | 39.6 | EATON MEDC, DORSET ROAD | SHEERNESS | ME12 1LP | Swale |  | Factory And Premises; Factory And Premises Part Undergoing Works | industrial | 2 | 17002.6 | 183014 | GIA | 965000 | SHEERNESS 33/6.6KV | inside-area | 0.74 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 28 | 27.02 | 1020 | 19 | 646130 | SPN-S000000393724 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4307 | 0.75117 | SPN-S000000008483 | 14902674000;14902674000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1081 | 39.6 | UNITS 1-3 CORNER OF BRIELLE WAY, KING STREET | SHEERNESS | ME12 1SU | Swale |  | Warehouse And Premises | industrial | 1 | 1770.13 | 19054 | GIA | 73000 | SHEERNESS 33/6.6KV | inside-area | 0.43 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 2.81 | 44 | 19 | 810090 | SPN-S000000391495 | 800 | 560 | 60-80% | SHEERNESS 33/6.6KV | 21 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.441 | 0.75 | SPN-S000000008483 | 13532298000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1082 | 39.6 | 1ST FLR 51-55, HIGH STREET | SHEERNESS | ME12 1NT | Swale |  | Warehouse And Premises | industrial | 1 | 1735.74 | 18683 | GIA | 53500 | SHEERNESS 33/6.6KV | inside-area | 0.91 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 2.76 | 43 | 19 | 810461 | SPN-S000000393825 | 1000 | 700 | 60-80% | SHEERNESS 33/6.6KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002533277 | Retail/Financial and Professional Services | 3801 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2026-07-17 |  | 0.67 | FALSE | 51.4403 | 0.76135 | SPN-S000000008483 | 12082343000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1083 | 39.6 | SMART HOUSE, BRIELLE WAY | SHEERNESS | ME12 1YW | Swale |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1527.04 | 16437 | GIA | 100000 | SHEERNESS 33/6.6KV | inside-area | 0.64 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 2.43 | 69 | 19 | 812707 | SPN-S000000391526 | 300 | 150 | 40-60% | SHEERNESS 33/6.6KV | 146 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002529314 | Offices and Workshop Businesses | 1396 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-06-03 |  | 1 | FALSE | 51.4317 | 0.74596 | SPN-S000000008483 | 15037966000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1084 | 39.6 | THE COACH STATION & UNIT F, DORSET ROAD | SHEERNESS | ME12 1LT | Swale |  | Workshop And Premises | industrial | 1 | 1484.45 | 15978 | GIA | 160000 | SHEERNESS 33/6.6KV | inside-area | 0.68 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 2.36 | 67 | 19 | 813166 | SPN-S000000393724 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 39 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.4313 | 0.75176 | SPN-S000000008483 | 15027467000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1085 | 39.6 | GREENROSE FROZEN FOODS, DORSET ROAD | SHEERNESS | ME12 1LP | Swale |  | Factory And Premises | industrial | 1 | 1427.6 | 15367 | GIA | 111000 | SHEERNESS 33/6.6KV | inside-area | 0.74 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 2.27 | 86 | 19 | 813777 | SPN-S000000393724 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062377007 | General Industrial and Special Industrial Groups | 2990 | C | Natural Gas | 3 | 1 | Air Conditioning | 2022-11-28 |  | 0.5 | FALSE | 51.4307 | 0.75117 | SPN-S000000008483 | 331962147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1086 | 39.6 | 50-60 & 63-65, HIGH STREET | SHEERNESS | ME12 1RW | Swale |  | Factory And Premises | industrial | 1 | 1230.5 | 13245 | GIA | 66500 | SHEERNESS 33/6.6KV | inside-area | 0.54 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 1.96 | 74 | 19 | 815899 | SPN-S000000393856 | 500 | 250 | 40-60% | SHEERNESS 33/6.6KV | 20 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.442 | 0.74862 | SPN-S000000008483 | 14620697000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1087 | 39.6 | MONARCH CHEMICALS (SOUTHERN) LTD, NEW ROAD | SHEERNESS | ME12 1NB | Swale |  | Warehouse And Premises | industrial | 1 | 1190.53 | 12815 | GIA | 83500 | SHEERNESS 33/6.6KV | inside-area | 0.34 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 1.89 | 30 | 19 | 816329 | SPN-S000000393155 | 500 | 150 | 20-40% | SHEERNESS 33/6.6KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062377191 | B1 Offices and Workshop businesses | 3460 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-11-10 |  | 0.5 | FALSE | 51.435 | 0.75257 | SPN-S000000008483 | 392027147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1088 | 39.6 | BAY 3 AT OLD BRITTANIA BUILDING, NEW ROAD | SHEERNESS | ME12 1NB | Swale |  | Workshop And Premises | industrial | 1 | 1042.12 | 11217 | GIA | 53500 | SHEERNESS 33/6.6KV | inside-area | 0.34 | Sheerness Grid | Kemsley | Mid Kent Zone | 7.2 | primary | 7.2 | Green | 16 | 8.9 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | Green (Over 5% headroom) | 51337 | 100 | 1.66 | 47 | 19 | 817927 | SPN-S000000393155 | 500 | 150 | 20-40% | SHEERNESS 33/6.6KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062377191 | B1 Offices and Workshop businesses | 3460 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-11-10 |  | 0.5 | FALSE | 51.435 | 0.75257 | SPN-S000000008483 | 11629506000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1089 | 39.5 | 1, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4UA | Tonbridge & Malling |  | Offices And Premises | office | 2 | 5254.03 | 56554 | NIA | 1277500 | MEREWORTH 33/11KV | inside-area | 2.87 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 90 | 8.35 | 368 | 30 | 947792 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002918322 | B1 Offices and Workshop businesses | 4082 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2019-04-23 |  | 1 | FALSE | 51.2765 | 0.39436 | SPN-S000000008643 | 5627788000;14929648000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1090 | 39.5 | 50, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4JX | Tonbridge & Malling |  | Offices And Premises | office | 1 | 4495.58 | 48390 | NIA | 1050000 | MEREWORTH 33/11KV | inside-area | 3.21 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 7.14 | 315 | 30 | 955956 | SPN-S000000393544 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000966628 | B1 Offices and Workshop businesses | 5460 | C | Natural Gas | 5 | 2 | Air Conditioning | 2020-03-10 |  | 1 | FALSE | 51.2773 | 0.40056 | SPN-S000000008643 | 404474148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1091 | 39.5 | 1, JUBILEE WAY, KINGS HILL | WEST MALLING | ME19 4NR | Tonbridge & Malling |  | Offices And Premises | office | 1 | 4457.41 | 47979 | NIA | 990000 | MEREWORTH 33/11KV | inside-area | 3.83 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 7.08 | 312 | 30 | 956367 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2818 | 0.40591 | SPN-S000000008643 | 7505919000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1092 | 39.5 | 30, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4AE | Tonbridge & Malling |  | Offices And Premises | office | 1 | 4011.78 | 43182 | NIA | 895000 | MEREWORTH 33/11KV | inside-area | 3.01 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 6.38 | 281 | 30 | 961164 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002909915 | B1 Offices and Workshop businesses | 4172 | C | Natural Gas | 4 | 2 | Heating and Mechanical Ventilation | 2015-05-11 |  | 1 | FALSE | 51.2768 | 0.39675 | SPN-S000000008643 | 9394198000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1093 | 39.5 | GIBSON BUILDING, GIBSON DRIVE | WEST MALLING | ME19 4LZ | Tonbridge & Malling |  | Offices And Premises | office | 1 | 3640.16 | 39182 | NIA | 480000 | MEREWORTH 33/11KV | inside-area | 2.57 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 5.78 | 255 | 30 | 965164 | SPN-S000000393565 | 500 | 350 | 60-80% | MEREWORTH 33/11KV | 57 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000960080 | Offices and Workshop Businesses | 3244 | E | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2026-01-21 |  | 1 | FALSE | 51.2743 | 0.39167 | SPN-S000000008643 | 10942207000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1094 | 39.5 | 25, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4TA | Tonbridge & Malling |  | Offices And Premises | office | 1 | 3420.37 | 36817 | NIA | 760000 | MEREWORTH 33/11KV | inside-area | 3 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 5.44 | 239 | 30 | 967529 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2775 | 0.39491 | SPN-S000000008643 | 1356424000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1095 | 39.5 | 2, ABBEY WOOD ROAD, KINGS HILL BUSINESS PARK | WEST MALLING | ME19 4YT | Tonbridge & Malling |  | Offices And Premises | office | 2 | 3044.55 | 32771 | NIA | 725000 | MEREWORTH 33/11KV | inside-area | 3.1 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 4.84 | 213 | 30 | 971575 | SPN-S000000391580 | 800 | 560 | 60-80% | MEREWORTH 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094698221 | Others: Miscellaneous 24hr Activities | 2191 | B | Natural Gas | 5 |  | Heating and Natural Ventilation | 2024-09-13 |  | 1 | FALSE | 51.2783 | 0.39579 | SPN-S000000008643 | 2284929000;389419148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1096 | 39.5 | GRND & 1ST FLR 1, TOWER VIEW, KINGS HILL | WEST MALLING | ME19 4HA | Tonbridge & Malling |  | Offices And Premises | office | 1 | 2933.17 | 31572 | NIA | 685000 | MEREWORTH 33/11KV | inside-area | 3.33 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 4.66 | 205 | 30 | 972774 | SPN-R000000852706-000-023Z | 50 | 15 | 20-40% | BARMING 33/11KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013923199 | Offices and Workshop Businesses | 3030 | D | Natural Gas | 4 |  | Air Conditioning | 2022-07-20 |  | 0.83 | FALSE | 51.2783 | 0.40131 | SPN-S000000008643 | 14909684000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1097 | 39.5 | ELECTRA POLYMERS LTD, ROUGHWAY MILL | TONBRIDGE | TN11 9SG | Tonbridge & Malling |  | Factory And Premises | industrial | 1 | 1668.73 | 17962 | GIA | 94500 | MEREWORTH 33/11KV | inside-area | 4.06 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.65 | 100 | 30 | 986384 | SPN-R000000864306-000-091Z | 200 | 180 | 80-100% | MEREWORTH 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013923466 | B8 Storage or Distribution | 684 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-06-04 |  | 0.67 | FALSE | 51.2518 | 0.31268 | SPN-S000000008643 | 6755588000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1098 | 39.5 | UNIT 25, THE ALDERS | MAIDSTONE | ME18 5JG | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1429.59 | 15388 | GIA | 93500 | MEREWORTH 33/11KV | inside-area | 0.3 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.27 | 36 | 30 | 988958 | SPN-S000000391394 | 315 | 94 | 20-40% | MEREWORTH 33/11KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002905352 | B2 to B7 General Industrial and Special Industrial Groups | 1577 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-03-28 |  | 1 | FALSE | 51.2532 | 0.37349 | SPN-S000000008643 | 1826927000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1099 | 39.5 | BROOK FARM BUILDINGS, CHURCH LANE | TONBRIDGE | TN12 5JH | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 1406.79 | 15143 | GIA | 86000 | MEREWORTH 33/11KV | inside-area | 4.35 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.24 | 63 | 30 | 989203 | SPN-R000000864308-000-064Z | 315 | 284 | 80-100% | MEREWORTH 33/11KV | 214 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2184 | 0.39126 | SPN-S000000008643 | 2381295000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1100 | 39.5 | UNITS 1-3, ADAMS WHARF BUSINESS PARK, BRANBRIDGES ROAD | TONBRIDGE | TN12 5EJ | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1313 | 14133 | GIA | 142000 | MEREWORTH 33/11KV | inside-area | 5.28 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.09 | 33 | 30 | 990213 | SPN-S000000391435 | 800 | 400 | 40-60% | MEREWORTH 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10092974403 | B8 Storage or Distribution | 1303 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2019-09-25 |  | 1 | FALSE | 51.2107 | 0.39669 | SPN-S000000008643 | 12401240000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1101 | 39.5 | UNIT 3A, ARNOLDS BUSINESS PARK, BRANBRIDGES ROAD | TONBRIDGE | TN12 5LG | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1138.2 | 12251 | GIA | 88500 | MEREWORTH 33/11KV | inside-area | 5.22 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 1.81 | 28 | 30 | 992095 | SPN-S000000391434 | 750 | 525 | 60-80% | MEREWORTH 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002912739 | General Industrial and Special Industrial Groups | 1950 | C | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2022-09-22 |  | 1 | FALSE | 51.2107 | 0.3941 | SPN-S000000008643 | 8333392000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1102 | 39.3 | 5, SHELDON WAY | AYLESFORD | ME20 6SE | Tonbridge & Malling |  | Factory And Premises; Warehouse And Premises; Workshop And Premises | industrial | 7 | 15200.45 | 163616 | GIA | 1275000 | AYLESFORD 33/6.6KV | inside-area | 1.66 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 31 | 24.15 | 912 | 85 | 4902078 | SPN-S000000393251 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3059 | 0.44495 | SPN-S000000008312 | 10636891000;412481148;1556463000;2109689000;2109689000;412480148;10636890000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1103 | 39.3 | NIAB/EMR, EAST MALLING RESEARCH STATION, NEW ROAD | WEST MALLING | ME19 6BH | Tonbridge & Malling |  | Offices And Premises (Part Exempt) | office | 1 | 8793.5 | 94652 | NIA | 392500 | AYLESFORD 33/6.6KV | inside-area | 2.02 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 53 | 13.97 | 616 | 85 | 4971042 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2852 | 0.45203 | SPN-S000000008312 | 12721498000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1104 | 39.3 | UNIT 4, LINK 20 ESTATE, BELLINGHAM WAY | AYLESFORD | ME20 6SP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1835.13 | 19753 | GIA | 237000 | AYLESFORD 33/6.6KV | inside-area | 1.49 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.92 | 46 | 85 | 5045941 | SPN-S000000394875 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10002910452 | B1 Offices and Workshop businesses | 1694 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-11-12 |  | 1 | FALSE | 51.3055 | 0.44728 | SPN-S000000008312 | 2353881000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1105 | 39.3 | UNITS 12B-D, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1816.31 | 19551 | GIA | 171000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.89 | 45 | 85 | 5046143 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2915 | 0.47299 | SPN-S000000008312 | 14796770000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1106 | 39.3 | UNITS 2A 2B 2C 2D & 2F, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NF | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1782.05 | 19182 | GIA | 125000 | AYLESFORD 33/6.6KV | inside-area | 1.09 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.83 | 45 | 85 | 5046512 | SPN-S000000400140 | 800 | 560 | 60-80% | AYLESFORD 33/6.6KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000961530 | C2 Residential Institutions - Hospitals and Care Homes | 1089 | A | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2019-07-11 |  | 0.5 | FALSE | 51.2943 | 0.47932 | SPN-S000000008312 | 3603510000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1107 | 39.3 | CROWN RECORDS MANAGEMENT LTD, MILL HALL | AYLESFORD | ME20 7JN | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1720.56 | 18520 | GIA | 184000 | AYLESFORD 33/6.6KV | inside-area | 0.27 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.73 | 43 | 85 | 5047174 | SPN-S000000394036 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 141 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3025 | 0.46474 | SPN-S000000008312 | 413446148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1108 | 39.3 | UNIT 1 AT 3, SHELDON WAY | AYLESFORD | ME20 6SE | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1695.7 | 18252 | GIA | 152000 | AYLESFORD 33/6.6KV | inside-area | 1.66 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.69 | 42 | 85 | 5047442 | SPN-S000000393251 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062628478 | B8 Storage or Distribution | 1798 | D | Natural Gas | 3 | 3 | Heating and Natural Ventilation | 2017-05-04 |  | 1 | FALSE | 51.3059 | 0.44495 | SPN-S000000008312 | 198813148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1109 | 39.3 | UNIT 6B, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1688.88 | 18179 | GIA | 113000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.68 | 42 | 85 | 5047515 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013922409 | Retail/Financial and Professional Services | 1175 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-09-13 |  | 0.67 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 15031418000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1110 | 39.3 | UNITS 1C & 1D DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1657.39 | 17840 | GIA | 136000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.63 | 41 | 85 | 5047854 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062628301 | B2 to B7 General Industrial and Special Industrial Groups | 714 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2013-09-18 |  | 1 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 11430535000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1111 | 39.3 | UNIT 3 PART B, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1657.31 | 17839 | GIA | 117000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.63 | 41 | 85 | 5047855 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013921884 | Storage or Distribution | 1929 | B | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-02-24 |  | 0.6 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 14806772000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1112 | 39.3 | BOUNDARY HOUSE 523, NEW HYTHE LANE | AYLESFORD | ME20 6SB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1635.33 | 17603 | GIA | 137000 | AYLESFORD 33/6.6KV | inside-area | 1.73 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.6 | 41 | 85 | 5048091 | SPN-S000000392198 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3126 | 0.45138 | SPN-S000000008312 | 4964439000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1113 | 39.3 | UNITS 1 & 2, THE MILL, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 1585.14 | 17062 | GIA | 95500 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.52 | 40 | 85 | 5048632 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10022895514 | B1 Offices and Workshop businesses | 1138 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-01-07 |  | 0.5 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 5477891000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1114 | 39.3 | AYLESFORD HIGHWAYS DEPOT, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Storage Depot And Premises | industrial | 1 | 1386.65 | 14926 | GIA | 125000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.2 | 35 | 85 | 5050768 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10022895514 | B1 Offices and Workshop businesses | 1138 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-01-07 |  | 0.5 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 15116265000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1115 | 39.3 | CELUFORM LTD, NEW HYTHE BUSINESS PARK, PAPYRUS WAY, BELLINGHAM WAY | AYLESFORD | ME20 7SX | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1344.37 | 14471 | GIA | 74500 | AYLESFORD 33/6.6KV | inside-area | 1.24 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.14 | 34 | 85 | 5051223 | SPN-S000000400184 | 1000 | 900 | 80-100% | AYLESFORD 33/6.6KV | 290 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.307 | 0.45263 | SPN-S000000008312 | 4362273000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1116 | 39.3 | UNIT 13B-13C, MILLS ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse Workshop And Premises | industrial | 1 | 1307.04 | 14069 | GIA | 139000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.08 | 59 | 85 | 5051625 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2915 | 0.47299 | SPN-S000000008312 | 13734098000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1117 | 39.3 | 1A-1B, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7NA | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 1304.04 | 14037 | GIA | 90000 | AYLESFORD 33/6.6KV | inside-area | 1.18 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.07 | 59 | 85 | 5051657 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 114 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000961653 | B8 Storage or Distribution | 1908 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-06-09 |  | 0.75 | FALSE | 51.2904 | 0.47134 | SPN-S000000008312 | 10380188000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1118 | 39.3 | PARAGON HOUSE, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 1275.2 | 13726 | GIA | 149000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.03 | 32 | 85 | 5051968 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10022895514 | B1 Offices and Workshop businesses | 1138 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-01-07 |  | 0.5 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 4940706000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1119 | 39.3 | BURLEY PROFILE SPECIALISTS, OLD MILL LANE | AYLESFORD | ME20 7DT | Maidstone |  | Workshop And Premises | industrial | 1 | 1260.74 | 13570 | GIA | 83500 | AYLESFORD 33/6.6KV | inside-area | 2.2 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2 | 57 | 85 | 5052124 | SPN-S000000392172 | 800 | 560 | 60-80% | AYLESFORD 33/6.6KV | 54 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003662558 | B1 Offices and Workshop businesses | 508 | E | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2017-10-11 |  | 1 | FALSE | 51.3056 | 0.49801 | SPN-S000000008312 | 6975090000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1120 | 39.3 | UNITS 1-3, LAKE ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7TQ | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 1211.53 | 13041 | GIA | 128000 | AYLESFORD 33/6.6KV | inside-area | 0.99 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.93 | 55 | 85 | 5052653 | SPN-S000000394248 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 96 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000961514 | B2 to B7 General Industrial and Special Industrial Groups | 1190 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-09-06 |  | 1 | FALSE | 51.2917 | 0.46706 | SPN-S000000008312 | 393855148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1121 | 39.3 | 2C-2D, DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1209.99 | 13024 | GIA | 110000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.92 | 30 | 85 | 5052670 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10092973282 | B8 Storage or Distribution | 1270 | C | Natural Gas | 5 |  | Heating and Natural Ventilation | 2022-07-26 |  | 0.75 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 11268658000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1122 | 39.3 | 2F, DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Warehouse, Office And Premises | industrial | 1 | 1208.19 | 13005 | GIA | 109000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.92 | 85 | 85 | 5052689 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000961693 | B1 Offices and Workshop businesses | 1246 | C | Natural Gas | 5 |  | Heating and Natural Ventilation | 2022-07-27 |  | 1 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 4477629000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1123 | 39.3 | 1E & 1F, DEACON INDUSTRIAL ESTATE, FORSTAL ROAD | AYLESFORD | ME20 7SP | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 1204.7 | 12967 | GIA | 108000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.91 | 54 | 85 | 5052727 | SPN-S000000393787 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013922177 | Storage or Distribution | 607 | B | Grid Supplied Electricity | 5 |  | Heating and Natural Ventilation | 2026-06-19 |  | 1 | FALSE | 51.3014 | 0.48799 | SPN-S000000008312 | 2118387000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1124 | 39.3 | UNIT E2, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 1170.3 | 12597 | GIA | 152000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.86 | 29 | 85 | 5053097 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200003719020 | Storage or Distribution | 1469 | C | Natural Gas | 5 |  | Heating and Natural Ventilation | 2024-03-18 |  | 1 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 181799148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1125 | 39.3 | UNIT 1A, BURNT ASH ROAD, QUARRY WOOD INDUSTRIAL ESTATE | AYLESFORD | ME20 7XB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1166.63 | 12557 | GIA | 140000 | AYLESFORD 33/6.6KV | inside-area | 1.1 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.85 | 29 | 85 | 5053137 | SPN-S000000394249 | 1000 | 700 | 60-80% | AYLESFORD 33/6.6KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013922409 | Retail/Financial and Professional Services | 1175 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-09-13 |  | 1 | FALSE | 51.2915 | 0.47299 | SPN-S000000008312 | 8309998000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1126 | 39.3 | UNITS A & B, LARKFIELD MILL, NEW HYTHE BUSINESS PARK, BELLINGHAM WAY | AYLESFORD | ME20 7HD | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1148.88 | 12366 | GIA | 142000 | AYLESFORD 33/6.6KV | inside-area | 1.44 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.83 | 29 | 85 | 5053328 | SPN-S000000394449 | 500 | 350 | 60-80% | TOWNSEND HOOK 33/6.6KV | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.306 | 0.44839 | SPN-S000000008312 | 7776622000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1127 | 39.3 | UNIT D2, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Warehouse And Premises | industrial | 1 | 1090.51 | 11738 | GIA | 142000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.73 | 27 | 85 | 5053956 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10022895514 | B1 Offices and Workshop businesses | 1138 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-01-07 |  | 1 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 3090982000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1128 | 39.3 | DANE HOUSE 9, SHELDON WAY | AYLESFORD | ME20 6SE | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1005.1 | 10819 | GIA | 99000 | AYLESFORD 33/6.6KV | inside-area | 1.66 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.6 | 25 | 85 | 5054875 | SPN-S000000393251 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062389633 | B1 Offices and Workshop businesses | 1006 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2013-06-04 |  | 1 | FALSE | 51.3059 | 0.44495 | SPN-S000000008312 | 412353148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1129 | 39.2 | BUXTED HOUSE, LONDON ROAD | SEVENOAKS | TN15 6AR | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1512.48 | 16280 | GIA | 235000 | FARNINGHAM 33/11KV | inside-area | 6.34 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 2.4 | 68 | 7 | 255728 | SPN-S000000316110 | 100 | 30 | 20-40% | FARNINGHAM 33/11KV | 204 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002017107 | Offices and Workshop Businesses | 1502 | A | Natural Gas | 5 | 3 | Air Conditioning | 2023-06-06 |  | 1 | FALSE | 51.3314 | 0.28219 | SPN-S000000008403 | 14516898000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1130 | 39.2 | THE OLD WEST BARN, WESTWOOD FARM, HIGHCROSS ROAD | GRAVESEND | DA13 9PH | Dartford |  | Warehouse And Premises | industrial | 1 | 1375.33 | 14804 | GIA | 120000 | FARNINGHAM 33/11KV | inside-area | 5.6 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 2.19 | 34 | 7 | 257204 | SPN-S000000314213 | 500 | 350 | 60-80% | GRAVESEND SOUTH 33/11KV | 193 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10009432381 | B1 Offices and Workshop businesses | 195 | E | Oil | 3 |  | Heating and Natural Ventilation | 2019-06-04 |  | 1 | FALSE | 51.4124 | 0.2956 | SPN-S000000008403 | 11387612000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1131 | 39.2 | 101-103, HORTON KIRBY PAPER MILLS, HORTON ROAD | DARTFORD | DA4 9BD | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1249.56 | 13450 | GIA | 114000 | FARNINGHAM 33/11KV | inside-area | 2.58 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 1.99 | 56 | 7 | 258558 | SPN-S000000324067 | 1000 | 700 | 60-80% | FARNINGHAM 33/11KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.402 | 0.24507 | SPN-S000000008403 | 14270722000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1132 | 39.2 | EAST CHICKEN SHED, MAPLEBANK FARM, MAPLESCOMBE LANE | DARTFORD | DA4 0JY | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1120.88 | 12065 | GIA | 35250 | FARNINGHAM 33/11KV | inside-area | 2.62 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 1.78 | 28 | 7 | 259943 | SPN-R000000840306-000-118Z | 100 | 50 | 40-60% | FARNINGHAM 33/11KV | 122 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3565 | 0.23904 | SPN-S000000008403 | 6437384000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1133 | 39.2 | LONDON ROAD | SEVENOAKS | TN15 6ER | Sevenoaks | J D HOTCHKISS LTD | Workshop And Premises | industrial | 1 | 1079.5 | 11620 | GIA | 73500 | FARNINGHAM 33/11KV | inside-area | 3.9 | Chelsfield Grid | Northfleet | West Kent Zone | 6.9 | primary | 6.9 | Green | 22.9 | 15 | Thermal | 1.1 | 2.4 | 0 | 3.5 | 6.4 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | Green (Over 5% headroom) | 49198 | 100 | 1.72 | 49 | 7 | 260388 | SPN-S000000314975 | 500 | 350 | 60-80% | FARNINGHAM 33/11KV | 103 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013772931 | General Industrial and Special Industrial Groups | 231 | A | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-25 |  | 1 | FALSE | 51.3474 | 0.25569 | SPN-S000000008403 | 107586148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1134 | 39.1 | CHURCH & DWIGHT UK LTD, BOWLES WELL GARDENS | FOLKESTONE | CT19 6PQ | Folkestone & Hythe |  | Factory And Premises | industrial | 2 | 15502.38 | 166866 | GIA | 835000 | FOLKESTONE EAST 33/11KV | inside-area | 0.67 | Folkestone Total | Sellindge | East Kent Zone | 6.8 | primary | 6.8 | Green | 22.9 | 16.2 | Thermal | 0 | 0 | 0 | 0 | 6.1 | Folkestone Grid 33kV | 30.2 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | Green (Over 5% headroom) | 48485 | 29 | 24.63 | 930 | 7 | 184344 | SPN-S000000362083 | 750 | 525 | 60-80% | FOLKESTONE EAST 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0906 | 1.1922 | SPN-S000000008660 | 10223089000;10223089000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1135 | 39.1 | DOBBIES GARDEN CENTRE 7A, RUTHERFORD ROAD, EUREKA SCIENCE & BUSINESS PARK | ASHFORD | TN25 4BN | Ashford |  | Garden Centre & Premises | bigbox | 1 | 10894.5 | 117267 | NIA | 372500 | ASHFORD EAST 33/11KV | inside-area | 1.84 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 19 | 17.31 | 981 | 27 | 1847820 | SPN-S000000371401 | 500 | 150 | 20-40% | ASHFORD EAST 33/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012843499 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 3090 | C | Natural Gas | 4 | 2 | Air Conditioning | 2021-10-28 |  | 0.5 | FALSE | 51.1609 | 0.87272 | SPN-S000000008402 | 15029826000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1136 | 39.1 | BYBROOK BARN PRODUCE, CEMETERY LANE | ASHFORD | TN24 9JZ | Ashford |  | Garden Centre And Premises | bigbox | 1 | 10305.11 | 110923 | GIA | 292500 | ASHFORD EAST 33/11KV | inside-area | 1.43 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 20 | 16.38 | 927 | 27 | 1854164 | SPN-S000000361012 | 315 | 94 | 20-40% | ASHFORD EAST 33/11KV | 167 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062561122 | A1/A2 Retail and Financial/Professional services | 4570 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-07-01 |  | 0.75 | FALSE | 51.1576 | 0.87738 | SPN-S000000008402 | 12279558000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1137 | 39.1 | THE RANGE UNIT 1, FOUGERES WAY | ASHFORD | TN25 4DT | Ashford |  | Retail Warehouse And Premises | bigbox | 1 | 3393.43 | 36527 | GIA | 475000 | ASHFORD EAST 33/11KV | inside-area | 2.53 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 61 | 5.39 | 305 | 27 | 1928560 | SPN-S000000371505 | 1000 | 900 | 80-100% | ASHFORD EAST 33/11KV | 217 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012862397 | Retail/Financial and Professional Services | 6284 | B | Natural Gas | 4 |  | Air Conditioning | 2023-04-04 |  | 1 | FALSE | 51.1593 | 0.86189 | SPN-S000000008402 | 13954776000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1138 | 39.1 | UNIT 2, RUTHERFORD ROAD | ASHFORD | TN25 4BN | Ashford |  | Leisure Centre And Premises | bigbox | 1 | 3304.88 | 35573 | GIA | 270000 | ASHFORD EAST 33/11KV | inside-area | 1.84 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 62 | 5.25 | 264 | 27 | 1929514 | SPN-S000000371401 | 500 | 150 | 20-40% | ASHFORD EAST 33/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012843499 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 3090 | C | Natural Gas | 4 | 2 | Air Conditioning | 2021-10-28 |  | 1 | FALSE | 51.1609 | 0.87272 | SPN-S000000008402 | 7350346000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1139 | 39 | HIGH BANKS NURSERY CRANBROOK ROAD | CRANBROOK | TN18 5EW | Tunbridge Wells |  | Garden Centre & Premises | bigbox | 1 | 4103.56 | 44170 | NIA | 22000 | HAWKHURST 33/11KV | inside-area | 1.35 | Hartley Grid | Ninfield | East Sussex Zone | 3 | primary | 3 | Green | 15 | 10 | Thermal | 0 | 0 | 0 | 0 | 3.8 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 14.1 | 10.6 | Summer | 31.1321 | 3.3 | Green (Over 5% headroom) | 21390 | 48 | 6.52 | 369 | 3 | 70381 | SPN-S000000451541 | 800 | 400 | 40-60% | HAWKHURST 33/11KV | 171 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.064 | 0.5078 | SPN-S000000008363 | 10617942000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1140 | 39 | 457, LEYSDOWN ROAD | SHEERNESS | ME12 4BB | Swale |  | Garden Centre And Premises | bigbox | 1 | 4000.17 | 43057 | OTH | 10250 | EASTCHURCH PRISON 33/6.6KV | inside-area | 2.63 | Sheerness Grid | Kemsley | Mid Kent Zone | 3 | primary | 3 | Green | 10 | 5.7 | Thermal | 0 | 0 | 12 | 0 | 2.2 | Sheerness Grid 33kV | 29.6 | GREEN | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 9.3 | 7 | Winter | 43.0108 | 4 | Green (Over 5% headroom) | 21390 | 50 | 6.36 | 360 | 1 | 20709 | SPN-R000000858705-000-084Z | 100 | 30 | 20-40% | EASTCHURCH PRISON 33/6.6KV | 223 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3974 | 0.89022 | SPN-S000000008587 | 5018423000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1141 | 38.9 | ARGYLE ROAD | SEVENOAKS | TN13 1HG | Sevenoaks | SEVENOAKS DISTRICT COUNCIL | Offices And Premises | office | 1 | 3380.65 | 36389 | NIA | 595000 | SUNDRIDGE 33/11KV | inside-area | 3.89 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 5.37 | 237 | 9 | 268046 | SPN-S000000446615 | 800 | 400 | 40-60% |  | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094318984 | Offices and Workshop Businesses | 153 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-07-07 |  | 1 | FALSE | 51.2733 | 0.18883 | SPN-S000000008496 | 85450148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1142 | 38.9 | UNITS C & D, WESTERHAM TRADE CENTRE, THE FLYERS WAY | WESTERHAM | TN16 1DE | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1503.55 | 16184 | GIA | 171000 | SUNDRIDGE 33/11KV | inside-area | 4.22 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 2.39 | 38 | 9 | 288251 | SPN-S000000446811 | 1000 | 700 | 60-80% |  | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062622216 | General Industrial and Special Industrial Groups | 1463 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-08-27 |  | 1 | FALSE | 51.2707 | 0.075057 | SPN-S000000008496 | 13821310000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1143 | 38.9 | ROYAL MAIL, SOUTH PARK | SEVENOAKS | TN13 1AA | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1392.4 | 14988 | GIA | 61500 | SUNDRIDGE 33/11KV | inside-area | 4.17 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 2.21 | 35 | 9 | 289447 | SPN-S000000446915 | 500 | 50 | 0-20% |  | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2703 | 0.19173 | SPN-S000000008496 | 13779982000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1144 | 38.9 | THE SCRAPYARD 76, LONDON ROAD | SEVENOAKS | TN13 2DN | Sevenoaks |  | Storage Depot And Premises | industrial | 1 | 1289.6 | 13881 | OTH | 22500 | SUNDRIDGE 33/11KV | inside-area | 2.63 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 2.05 | 32 | 9 | 290554 | SPN-S000000446973 | 300 | 90 | 20-40% |  | 106 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094318214 | Offices and Workshop Businesses | 544 | C | Natural Gas | 4 | 3 | Air Conditioning | 2024-07-19 |  | 0.5 | FALSE | 51.2886 | 0.16904 | SPN-S000000008496 | 13204789000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1145 | 38.8 | BARTH-HASS UK LTD, HOP POCKET LANE | TONBRIDGE | TN12 6DQ | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 17337.5 | 186619 | GIA | 600000 | PADDOCK WOOD 33/11KV | inside-area | 0.7 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 25 | 27.55 | 433 | 38 | 1744497 | SPN-S000000442222 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 167 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000063339 | B2 to B7 General Industrial and Special Industrial Groups | 16974 | C | Natural Gas | 4 |  | Heating and Mechanical Ventilation | 2019-12-10 |  | 0.8 | FALSE | 51.1835 | 0.38948 | SPN-S000000008454 | 11072617000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1146 | 38.8 | UNITS 11-13, DANA TRADING ESTATE, TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells | DJM MUSIC; JESTIC FOOD SERVICE EQUIPMENT; ONE WORLD TRADING; RE-STORE; REAL TIME LOGISTICS SOLUTIONS LTD; RESTORE LTD | Factory And Premises; Warehouse And Premises; Workshop And Premises | industrial | 7 | 17151.66 | 184619 | GIA | 1341500 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 25 | 27.26 | 1029 | 38 | 1746497 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024135854 | B8 Storage or Distribution | 5872 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-09-29 |  | 1 | FALSE | 51.1857 | 0.39037 | SPN-S000000008454 | 8064055000;8064054000;7419817000;9472813000;8244796000;7419820000;7419821000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1147 | 38.8 | SWAN MILL PAPER COMPANY LTD, GOLDSEL ROAD | SWANLEY | BR8 8EU | Sevenoaks |  | Factory And Premises | industrial | 1 | 16989.63 | 182875 | GIA | 750000 | SWANLEY 33/11KV | inside-area | 1.65 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 26 | 27 | 1019 | 18 | 889778 | SPN-S000000314840 | 750 | 525 | 60-80% | SWANLEY 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3934 | 0.1746 | SPN-S000000008528 | 382487148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1148 | 38.8 | MANSTON HOUSE, COLUMBUS AVENUE, MANSTON PARK | RAMSGATE | CT12 5BF | Thanet |  | Warehouse And Premises | industrial | 1 | 16206.88 | 174449 | GIA | 690000 | WESTGATE 33/11KV | inside-area | 2.29 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 27 | 25.75 | 405 | 16 | 640831 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003078447 | B2 to B7 General Industrial and Special Industrial Groups | 14134 | C | Natural Gas | 4 | 3 | Heating and Natural Ventilation | 2020-12-23 |  | 1 | FALSE | 51.3545 | 1.3225 | SPN-S000000008510 | 14279981000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1149 | 38.8 | EDEN HOUSE, COLUMBUS AVENUE, MANSTON PARK | RAMSGATE | CT12 5BF | Thanet |  | Factory And Premises | industrial | 1 | 15514.23 | 166994 | GIA | 685000 | WESTGATE 33/11KV | inside-area | 2.29 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 28 | 24.65 | 931 | 16 | 648286 | [9 empty] | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003078447 | B2 to B7 General Industrial and Special Industrial Groups | 14134 | C | Natural Gas | 4 | 3 | Heating and Natural Ventilation | 2020-12-23 |  | 0.67 | FALSE | 51.3545 | 1.3225 | SPN-S000000008510 | 15047508000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1150 | 38.8 | CAPEL COURT YARD, SYCHEM LANE | TONBRIDGE | TN12 6TT | Tunbridge Wells |  | Storage Depot And Premises | industrial | 1 | 15294.24 | 164626 | OTH | 45000 | PADDOCK WOOD 33/11KV | inside-area | 2.77 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 29 | 24.3 | 382 | 38 | 1766490 | SPN-R000000845409-000-058Z | 50 | 35 | 60-80% | PADDOCK WOOD 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.179 | 0.35295 | SPN-S000000008454 | 13988574000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1151 | 38.8 | MEDIA HOUSE, AZALEA DRIVE | SWANLEY | BR8 8HU | Sevenoaks |  | Offices And Premises | office | 1 | 2277.35 | 24513 | NIA | 285000 | SWANLEY 33/11KV | inside-area | 1.5 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 3.62 | 159 | 18 | 1048140 | SPN-S000000316144 | 500 | 350 | 60-80% | SWANLEY 33/11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035184171 | Offices and Workshop Businesses | 2660 | D | Natural Gas | 3 |  | Air Conditioning | 2026-03-30 |  | 1 | FALSE | 51.3928 | 0.16936 | SPN-S000000008528 | 6741711000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1152 | 38.8 | GREENBOX SELF STORAGE, COLLEGE ROAD | SWANLEY | BR8 7LT | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1718.55 | 18498 | GIA | 105000 | SWANLEY 33/11KV | inside-area | 1.25 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.73 | 43 | 18 | 1054155 | SPN-S000000314085 | 500 | 350 | 60-80% | SWANLEY 33/11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4095 | 0.17506 | SPN-S000000008528 | 7206095000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1153 | 38.8 | UNIT F, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1711 | 18417 | GIA | 131000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.72 | 43 | 38 | 1912699 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024135367 | Storage or Distribution | 1631 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-13 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 6053301000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1154 | 38.8 | ALL SAINTS INDUSTRIAL ESTATE, ALL SAINTS AVENUE | MARGATE | CT9 5TJ | Thanet | KAN-DOO TIMBER SUPPLIES LTD | Warehouse And Premises, Land And Storage | industrial | 1 | 1688.55 | 18175 | GIA | 92500 | WESTGATE 33/11KV | inside-area | 3.78 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 2.68 | 42 | 16 | 797105 | SPN-S000000342626 | 315 | 158 | 40-60% | THANET 33/11KV | 282 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062627343 | B8 Storage or Distribution | 159 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2015-11-11 |  | 1 | FALSE | 51.3834 | 1.3769 | SPN-S000000008510 | 517726145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1155 | 38.8 | GND & 1ST FLRS UNIT E, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1677.55 | 18057 | GIA | 128000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.67 | 42 | 38 | 1913059 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000068478 | Storage or Distribution | 1761 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-04-13 |  | 0.8 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 12623344000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1156 | 38.8 | TEARDROP CENTRE, LONDON ROAD | SWANLEY | BR8 8TS | Sevenoaks | HRP LTD | Warehouse And Premises | industrial | 1 | 1634.34 | 17592 | GIA | 205000 | SWANLEY 33/11KV | inside-area | 3.37 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.6 | 41 | 18 | 1055061 | SPN-R000000840309-000-018Z | 200 | 180 | 80-100% | FARNINGHAM 33/11KV | 266 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002019646 | Storage or Distribution | 6979 | B | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2025-12-03 |  | 1 | FALSE | 51.3867 | 0.19814 | SPN-S000000008528 | 2507730000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1157 | 38.8 | GND & 1ST FLRS UNITS J & L, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1633.8 | 17586 | GIA | 131000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.6 | 41 | 38 | 1913530 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10024135554 | B8 Storage or Distribution | 1572 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-09-30 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 13866701000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1158 | 38.8 | STORAGE CONTAINERS 1-32 R/O 77, BIRCHWOOD ROAD | WILMINGTON | DA2 7HQ | Dartford |  | Store And Premises | industrial | 1 | 1620 | 17438 | GIA | 32000 | SWANLEY 33/11KV | inside-area | 2.44 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.57 | 40 | 18 | 1055215 | SPN-S000000314797 | 300 | 150 | 40-60% | SWANLEY 33/11KV | 35 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4237 | 0.17592 | SPN-S000000008528 | 14611535000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1159 | 38.8 | UNITS 5-6, THE PACK HOUSE, WANTSUM WAY | BIRCHINGTON | CT7 0NE | Thanet |  | Warehouse And Premises | industrial | 1 | 1567.15 | 16869 | GIA | 87500 | WESTGATE 33/11KV | inside-area | 5.71 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 2.49 | 39 | 16 | 798411 | SPN-R000000851008-000-100Z | 200 | 180 | 80-100% | WESTGATE 33/11KV | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3576 | 1.2467 | SPN-S000000008510 | 14167721000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1160 | 38.8 | MT BUILDING 203, SPITFIRE WAY | RAMSGATE | CT12 5BU | Thanet |  | Workshop And Premises | industrial | 1 | 1485 | 15984 | GIA | 96500 | WESTGATE 33/11KV | inside-area | 3.25 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 2.36 | 67 | 16 | 799296 | SPN-R000000851011-000-155Z | 50 | 35 | 60-80% | WESTGATE 33/11KV | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3474 | 1.339 | SPN-S000000008510 | 14254283000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1161 | 38.8 | OCURA HEALTHCARE FURNITURE, BROOK HOUSE UNIT 1, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1439.66 | 15496 | GIA | 125000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.29 | 36 | 38 | 1915620 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065015 | B8 Storage or Distribution | 1381 | C | Other | 3 |  | Unconditioned | 2021-05-06 |  | 0.75 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 13708068000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1162 | 38.8 | UNIT 4 MONKTON BUSINESS CENTRE 47, MONKTON STREET | RAMSGATE | CT12 4JF | Thanet |  | Workshop And Premises | industrial | 1 | 1391 | 14973 | GIA | 105000 | WESTGATE 33/11KV | inside-area | 4.92 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 2.21 | 63 | 16 | 800307 | SPN-R000000851011-000-116Z | 200 | 60 | 20-40% | WESTGATE 33/11KV | 205 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3377 | 1.2861 | SPN-S000000008510 | 14877295000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1163 | 38.8 | UNIT Q, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1389.5 | 14956 | GIA | 115000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.21 | 35 | 38 | 1916160 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065019 | B1 Offices and Workshop businesses | 1163 | D | Grid Supplied Electricity | 3 | 10 | Heating and Natural Ventilation | 2020-01-27 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 6700791000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1164 | 38.8 | UNITS 1-2 PRINCIPAL HOUSE, HOP POCKET LANE | TONBRIDGE | TN12 6DQ | Tunbridge Wells |  | Workshop And Premises | industrial | 1 | 1312.18 | 14124 | GIA | 79500 | PADDOCK WOOD 33/11KV | inside-area | 0.7 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.09 | 59 | 38 | 1916992 | SPN-S000000442222 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 167 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062545782 | Storage or Distribution | 1796 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2024-11-18 |  | 0.6 | FALSE | 51.1835 | 0.38948 | SPN-S000000008454 | 2778591000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1165 | 38.8 | HIGHWAYS AGENCY DEPOT, PEDHAM PLACE MAINTENANCE DEPOT, LONDON ROAD | SWANLEY | BR8 8TS | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1295.01 | 13939 | GIA | 68000 | SWANLEY 33/11KV | inside-area | 3.37 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.06 | 58 | 18 | 1058714 | SPN-R000000840309-000-018Z | 200 | 180 | 80-100% | FARNINGHAM 33/11KV | 266 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3867 | 0.19814 | SPN-S000000008528 | 2509105000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1166 | 38.8 | UNITS M & O, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1165 | 12540 | GIA | 92500 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.85 | 29 | 38 | 1918576 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10008669657 | B8 Storage or Distribution | 1110 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-03-31 |  | 0.8 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 15120734000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1167 | 38.8 | 1, WHITE OAK SQUARE, TECHNOLOGY CENTRE, LONDON ROAD | SWANLEY | BR8 7AG | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1157.9 | 12464 | GIA | 108000 | SWANLEY 33/11KV | inside-area | 1.16 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.84 | 52 | 18 | 1060189 | SPN-S000000316123 | 1000 | 500 | 40-60% | SWANLEY 33/11KV | 18 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10035181012 | Offices and Workshop Businesses | 542 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-03-30 |  | 1 | FALSE | 51.3981 | 0.17212 | SPN-S000000008528 | 7075063000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1168 | 38.8 | COLD STORE A, PADDOCK WOOD COLD STORES, TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells | MACK MULTIPLES | Cold Store And Premises | industrial | 1 | 1151 | 12389 | GIA | 101000 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.83 | 138 | 38 | 1918727 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1857 | 0.39037 | SPN-S000000008454 | 4423064000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1169 | 38.8 | HANCOCK HOUSE, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1148.5 | 12362 | GIA | 96500 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.83 | 29 | 38 | 1918754 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10000065019 | B1 Offices and Workshop businesses | 1163 | D | Grid Supplied Electricity | 3 | 10 | Heating and Natural Ventilation | 2020-01-27 |  | 0.75 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 2226186000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1170 | 38.8 | INVICTA PRODUCE LTD, INVICTA WAY, MANSTON PARK | RAMSGATE | CT12 5DD | Thanet |  | Factory, Office And Premises | industrial | 1 | 1133.88 | 12205 | GIA | 86000 | WESTGATE 33/11KV | inside-area | 2.66 | Thanet Grid | Richborough | East Kent Zone | 6.6 | primary | 6.6 | Green | 22.9 | 16.3 | Thermal | 0 | 4.6 | 13 | 4.6 | 4 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | Green (Over 5% headroom) | 47059 | 100 | 1.8 | 68 | 16 | 803075 | SPN-S000000343511 | 800 | 560 | 60-80% | MANSTON 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3511 | 1.3224 | SPN-S000000008510 | 9157222000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1171 | 38.8 | UNITS N & P, PADDOCK WOOD DISTRIBUTION CENTRE | TONBRIDGE | TN12 6UU | Tunbridge Wells |  | Warehouse, Office And Premises | industrial | 1 | 1070.05 | 11518 | GIA | 103000 | PADDOCK WOOD 33/11KV | inside-area | 0.83 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.7 | 75 | 38 | 1919598 | SPN-S000000443962 | 1000 | 700 | 60-80% | PADDOCK WOOD 33/11KV | 63 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062545577 | Storage or Distribution | 1117 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-10-10 |  | 1 | FALSE | 51.1841 | 0.39815 | SPN-S000000008454 | 6650339000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1172 | 38.8 | MKS AT CAPEL COURT YARD, SYCHEM LANE | TONBRIDGE | TN12 6TT | Tunbridge Wells |  | Storage Depot And Premises | industrial | 1 | 1068 | 11496 | OTH | 11250 | PADDOCK WOOD 33/11KV | inside-area | 2.77 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.7 | 27 | 38 | 1919620 | SPN-R000000845409-000-058Z | 50 | 35 | 60-80% | PADDOCK WOOD 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.179 | 0.35295 | SPN-S000000008454 | 12570081000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1173 | 38.8 | COLD STORE B, PADDOCK WOOD COLD STORES, TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells |  | Cold Store And Premises | industrial | 1 | 1055.9 | 11366 | GIA | 84000 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.68 | 127 | 38 | 1919750 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1857 | 0.39037 | SPN-S000000008454 | 3567721000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1174 | 38.8 | COLD STORE C, PADDOCK WOOD COLD STORES, TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells |  | Cold Store And Premises | industrial | 1 | 1055.9 | 11366 | GIA | 84000 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.68 | 127 | 38 | 1919750 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1857 | 0.39037 | SPN-S000000008454 | 3567724000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1175 | 38.8 | COLD STORE D, PADDOCK WOOD COLD STORES, TRANSFESA ROAD | TONBRIDGE | TN12 6UT | Tunbridge Wells |  | Cold Store And Premises | industrial | 1 | 1055.9 | 11366 | GIA | 84000 | PADDOCK WOOD 33/11KV | inside-area | 0.94 | Pembury Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 23 | 16.3 | Thermal | 0 | 3.7 | 0 | 3.7 | 3.5 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.68 | 127 | 38 | 1919750 | SPN-S000000443967 | 500 | 250 | 40-60% | PADDOCK WOOD 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1857 | 0.39037 | SPN-S000000008454 | 3567727000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1176 | 38.8 | MARK LUCK LTD, RAILWAY SIDINGS, WESTED LANE | SWANLEY | BR8 8EE | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1048.05 | 11281 | GIA | 115000 | SWANLEY 33/11KV | inside-area | 2.86 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 1.67 | 47 | 18 | 1061372 | SPN-S000000314549 | 800 | 560 | 60-80% | SWANLEY 33/11KV | 117 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002020122 | B2 to B7 General Industrial and Special Industrial Groups | 1570 | D | Oil | 3 | 1 | Heating and Natural Ventilation | 2014-05-15 |  | 0.6 | FALSE | 51.3877 | 0.19 | SPN-S000000008528 | 13896321000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1177 | 38.7 | FOCUS HOUSE, BRIDGE ROAD | ASHFORD | TN23 1HA | Ashford |  | Offices And Premises | office | 1 | 1345.6 | 14484 | NIA | 184000 | SINGLETON 33/6.6KV | inside-area | 0.94 | Ashford Grid | Sellindge | East Kent Zone | 11 | primary | 11 | Green | 22.9 | 11 | Thermal | 0 | 6.9 | 0 | 6.9 | 6.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | Green (Over 5% headroom) | 78431 | 100 | 2.14 | 94 | 24 | 733630 | SPN-S000000371065 | 500 | 350 | 60-80% | SINGLETON 33/6.6KV | 18 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1509 | 0.85841 | SPN-S000000008610 | 7992087000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1178 | 38.5 | UNIT D1, GREAT LODGE RETAIL PARK, LONGFIELD ROAD | TUNBRIDGE WELLS | TN2 3EW | Tunbridge Wells |  | Retail Warehouse And Premises | bigbox | 2 | 18341.38 | 197425 | GIA | 2110000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 4.63 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 31 | 29.15 | 1651 | 50 | 1625491 | SPN-S000000442313 | 1000 | 700 | 60-80% | TUNBRIDGE WELLS GRID 132/11 | 214 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1578 | 0.29287 | SPN-S000000008504 | 5713251000;5713251000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1179 | 38.5 | NORMAN ROAD | ASHFORD | TN23 7DG | Ashford | B & Q | Retail Warehouse And Premises | bigbox | 1 | 10181.28 | 109590 | GIA | 910000 | ASHFORD CENTRAL | inside-area | 0.93 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 17 | 16.18 | 916 | 36 | 858648 | SPN-S000000371426 | 500 | 350 | 60-80% | ASHFORD CENTRAL | 104 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012845947 | Retail/Financial and Professional Services | 7450 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-02-13 |  | 1 | FALSE | 51.1371 | 0.87023 | SPN-S000000008302 | 3994941000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1180 | 38.5 | THE BUILDER CENTRE, SOUTH STOUR AVENUE | ASHFORD | TN23 7RS | Ashford |  | Builders Merchants And Premises | bigbox | 1 | 2146.7 | 23107 | GIA | 222000 | ASHFORD CENTRAL | inside-area | 0.64 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 80 | 3.41 | 193 | 36 | 945131 | SPN-S000000361016 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 58 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1408 | 0.87382 | SPN-S000000008302 | 334181148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1181 | 38.4 | 209, VALE ROAD | TONBRIDGE | TN9 1SU | Tonbridge & Malling |  | Factory And Premises; Warehouse And Premises | industrial | 10 | 15392.44 | 165683 | GIA | 1479000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.45 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 27 | 24.46 | 924 | 23 | 777061 | SPN-S000000443659 | 800 | 400 | 40-60% | TONBRIDGE EAST 33/6.6KV | 127 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.194 | 0.28526 | SPN-S000000008503 | 11832206000;133957148;133952148;133956148;11832209000;133950148;133958148;133947148;133954148;12661706000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1182 | 38.4 | TRINITY PLACE, SOVEREIGN WAY | TONBRIDGE | TN9 1RS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1819.89 | 19589 | GIA | 166000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.8 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 2.89 | 45 | 23 | 923155 | SPN-S000000441165 | 1000 | 700 | 60-80% | TONBRIDGE EAST 33/6.6KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962116 | Retail/Financial and Professional Services | 535 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-05-10 |  | 0.5 | FALSE | 51.1919 | 0.28069 | SPN-S000000008503 | 10574388000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1183 | 38.4 | 10 & 11, SOVEREIGN WAY | TONBRIDGE | TN9 1RH | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1548.43 | 16667 | GIA | 88000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.86 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 2.46 | 39 | 23 | 926077 | SPN-S000000441165 | 1000 | 700 | 60-80% | TONBRIDGE EAST 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962113 | Storage or Distribution | 811 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-06-23 |  | 1 | FALSE | 51.1912 | 0.28098 | SPN-S000000008503 | 15004034000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1184 | 38.4 | 6, SOVEREIGN WAY | TONBRIDGE | TN9 1RS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1509.39 | 16247 | GIA | 108000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.8 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 2.4 | 38 | 23 | 926497 | SPN-S000000441165 | 1000 | 700 | 60-80% | TONBRIDGE EAST 33/6.6KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962116 | Retail/Financial and Professional Services | 535 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-05-10 |  | 0.5 | FALSE | 51.1919 | 0.28069 | SPN-S000000008503 | 6288449000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1185 | 38.4 | WEIGHBRIDGE DRIFTWAY & DUCK HOUSE BARNS, ASHES LANE | TONBRIDGE | TN11 9QU | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1490.85 | 16047 | GIA | 77500 | TONBRIDGE EAST 33/6.6KV | inside-area | 2.35 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 2.37 | 37 | 23 | 926697 | SPN-S000000442513 | 200 | 140 | 60-80% | TONBRIDGE EAST 33/6.6KV | 218 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2251 | 0.30759 | SPN-S000000008503 | 12592881000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1186 | 38.4 | 12-14, ORCHARD BUSINESS CENTRE, SANDERSON WAY | TONBRIDGE | TN9 1YQ | Tonbridge & Malling |  | Storage Depot And Premises | industrial | 1 | 1350.51 | 14537 | GIA | 114000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.3 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 2.15 | 34 | 23 | 928207 | SPN-S000000443407 | 500 | 350 | 60-80% | TONBRIDGE EAST 33/6.6KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1941 | 0.29228 | SPN-S000000008503 | 14232065000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1187 | 38.4 | WALTERS FARM, MORLEY ROAD | TONBRIDGE | TN9 1RA | Tonbridge & Malling |  | Store And Premises | industrial | 1 | 1245 | 13401 | OTH | 32250 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.68 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 1.98 | 31 | 23 | 929343 | SPN-S000000443812 | 500 | 250 | 40-60% | TONBRIDGE EAST 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962163 | B2 to B7 General Industrial and Special Industrial Groups | 1704 | D | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2013-10-01 |  | 0.5 | FALSE | 51.1923 | 0.28315 | SPN-S000000008503 | 186307148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1188 | 38.4 | 6A, SOVEREIGN WAY | TONBRIDGE | TN9 1RS | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1157.8 | 12462 | GIA | 98500 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.8 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 1.84 | 29 | 23 | 930282 | SPN-S000000441165 | 1000 | 700 | 60-80% | TONBRIDGE EAST 33/6.6KV | 30 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000962116 | Retail/Financial and Professional Services | 535 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-05-10 |  | 0.5 | FALSE | 51.1919 | 0.28069 | SPN-S000000008503 | 6288452000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1189 | 38.4 | UNIT 12, TONBRIDGE TRADE PARK, INGOT WAY | TONBRIDGE | TN9 1GN | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1102.6 | 11868 | GIA | 154000 | TONBRIDGE EAST 33/6.6KV | inside-area | 1.77 | Pembury Grid | Northfleet | West Kent Zone | 6.3 | primary | 6.3 | Green | 22.9 | 16.6 | Thermal | 0 | 3.1 | 2.9 | 3.1 | 4.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | Green (Over 5% headroom) | 44920 | 100 | 1.75 | 28 | 23 | 930876 | SPN-S000000451833 | 800 | 720 | 80-100% | TONBRIDGE EAST 33/6.6KV | 5 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094697585 | B2 to B7 General Industrial and Special Industrial Groups | 498 | A | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2023-07-04 |  | 0.75 | FALSE | 51.1907 | 0.28569 | SPN-S000000008503 | 13937136000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1190 | 38.3 | HOLIDAY EXTRAS & ADJ ROYAL OAK SITE, ASHFORD ROAD | HYTHE | CT21 4JB | Folkestone & Hythe |  | Offices And Premises | office | 1 | 3378.09 | 36361 | NIA | 360000 | STANFORD 33/11KV | inside-area | 2.61 | Sellindge Grid | Sellindge | East Kent Zone | 6.2 | primary | 6.2 | Green | 15.1 | 8.8 | Thermal | 5 | 7 | 5 | 12 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.6 | 11.2 | Winter | 41.7808 | 6.1 | Green (Over 5% headroom) | 44207 | 100 | 5.37 | 236 | 4 | 114529 | SPN-R000000849207-000-110Z | 200 | 100 | 40-60% | STANFORD 33/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0853 | 1.034 | SPN-S000000008492 | 3100956000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1191 | 38.3 | THE WORKSHOP LITTLE WOODLAND FARM, WOODLAND ROAD | FOLKESTONE | CT18 8DP | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 1219.15 | 13123 | GIA | 49500 | STANFORD 33/11KV | inside-area | 3.21 | Sellindge Grid | Sellindge | East Kent Zone | 6.2 | primary | 6.2 | Green | 15.1 | 8.8 | Thermal | 5 | 7 | 5 | 12 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.6 | 11.2 | Winter | 41.7808 | 6.1 | Green (Over 5% headroom) | 44207 | 100 | 1.94 | 55 | 4 | 137767 | SPN-R000000849205-000-272Z | 100 | 70 | 60-80% | STANFORD 33/11KV | 187 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50014144 | B1 Offices and Workshop businesses | 909 | B | LPG | 3 |  | Heating and Natural Ventilation | 2022-01-12 |  | 0.75 | FALSE | 51.1313 | 1.07 | SPN-S000000008492 | 11351090000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1192 | 38.3 | WAREHOUSE 1 NEWINGREEN ESTATE, STONE STREET | HYTHE | CT21 4HR | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1119.66 | 12052 | GIA | 38000 | STANFORD 33/11KV | inside-area | 2.33 | Sellindge Grid | Sellindge | East Kent Zone | 6.2 | primary | 6.2 | Green | 15.1 | 8.8 | Thermal | 5 | 7 | 5 | 12 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.6 | 11.2 | Winter | 41.7808 | 6.1 | Green (Over 5% headroom) | 44207 | 100 | 1.78 | 28 | 4 | 138838 | SPN-R000000849207-000-028Z | 100 | 50 | 40-60% | STANFORD 33/11KV | 227 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0875 | 1.037 | SPN-S000000008492 | 14133678000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1193 | 38.3 | ASDA, STURRY ROAD | CANTERBURY | CT1 1DG | Canterbury |  | Superstore And Premises | bigbox | 1 | 11191.23 | 120461 | GIA | 1810000 | CANTERBURY TOWN 33/11KV | inside-area | 1 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 15 | 17.78 | 1007 | 27 | 938315 | SPN-S000000343062 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 234 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062279028 | Retail/Financial and Professional Services | 11134 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-05-26 |  | 1 | FALSE | 51.2906 | 1.0965 | SPN-S000000008410 | 15004941000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1194 | 38.3 | TESCO STORES, MILLSTROOD ROAD | WHITSTABLE | CT5 3EF | Canterbury |  | Superstore And Premises | bigbox | 1 | 9205.27 | 99085 | GIA | 1930000 | WHITSTABLE 33/11KV | inside-area | 0.75 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 18 | 14.63 | 828 | 11 | 531066 | SPN-S000000341304 | 300 | 150 | 40-60% | WHITSTABLE 33/11KV | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3482 | 1.0434 | SPN-S000000008516 | 13276456000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1195 | 38.3 | MEADOW GRANGE NURSERY, HONEY HILL | WHITSTABLE | CT5 3BP | Canterbury |  | Garden Centre And Premises | bigbox | 1 | 8941.42 | 96245 | NIA | 88000 | WHITSTABLE 33/11KV | inside-area | 3.65 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 19 | 14.21 | 805 | 11 | 533906 | SPN-R000000851608-000-127Z | 200 | 100 | 40-60% | WHITSTABLE 33/11KV | 142 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10097060724 | Restaurants and Cafes/Drinking Establishments/Takeaways | 164 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2024-07-12 |  | 1 | FALSE | 51.3181 | 1.0326 | SPN-S000000008516 | 7826049000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1196 | 38.3 | SAINSBURYS 6 THE BOULEVARD ALTIRA BUSINESS PARK, THANET WAY | HERNE BAY | CT6 6GZ | Canterbury |  | Superstore And Premises | bigbox | 1 | 7895.4 | 84985 | GIA | 1780000 | HERNE BAY 33/11KV | inside-area | 3.9 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 21 | 12.55 | 711 | 16 | 692842 | SPN-S000000343379 | 315 | 220 | 60-80% | HERNE BAY 33/11KV | 312 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3619 | 1.15 | SPN-S000000008417 | 15013242000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1197 | 38.3 | MORRISONS, ST SAVIOURS ROAD | MAIDSTONE | ME15 9NN | Maidstone |  | Superstore And Premises | bigbox | 1 | 6713.73 | 72266 | GIA | 1730000 | SHEPWAY 33/11KV | inside-area | 0.63 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 25 | 10.67 | 604 | 47 | 1427003 | SPN-S000000392240 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003718022 | Retail/Financial and Professional Services | 133 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-03-26 |  | 1 | FALSE | 51.2465 | 0.54701 | SPN-S000000008644 | 14413165000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1198 | 38.3 | ASHFORD ROAD | MAIDSTONE | ME14 5DA | Maidstone | HAYNES | Car Showroom And Premises | bigbox | 1 | 6692.68 | 72039 | GIA | 755000 | WATERSIDE 33/11KV | inside-area | 0.9 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 25 | 10.64 | 602 | 44 | 1654587 | SPN-S000000392276 | 1000 | 700 | 60-80% | MAIDSTONE NORTH 132/11KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10091194369 | B1 Offices and Workshop businesses | 327 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-11-21 |  | 1 | FALSE | 51.2735 | 0.53078 | SPN-S000000008529 | 4759668000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1199 | 38.3 | COUNTRY GARDENS PLC, ASHFORD ROAD | CANTERBURY | CT4 7HF | Canterbury |  | Garden Centre And Premises | bigbox | 1 | 6624.2 | 71302 | GIA | 173000 | CHARTHAM 33/11KV | inside-area | 0.49 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 5.2 | Green | 15 | 9.4 | Thermal | 0 | 5.7 | 0 | 5.7 | 5.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 14.4 | 10.6 | Winter | 37.5 | 5.4 | Green (Over 5% headroom) | 17825 | 25 | 10.53 | 596 | 4 | 76177 | SPN-R000000856006-000-220Z | 100 | 30 | 20-40% | CHARTHAM 33/11KV | 149 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033174413 | A1/A2 Retail and Financial/Professional services | 2925 | C | Natural Gas | 5 |  | Heating and Natural Ventilation | 2016-12-11 |  | 1 | FALSE | 51.2597 | 1.0283 | SPN-S000000008560 | 475956000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1200 | 38.3 | MORRISONS SUPERMARKET, TEN PERCH ROAD, WINCHEAP | CANTERBURY | CT1 3TQ | Canterbury |  | Superstore And Premises | bigbox | 1 | 6073.2 | 65371 | GIA | 1340000 | CANTERBURY TOWN 33/11KV | inside-area | 2.14 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 27 | 9.65 | 547 | 27 | 993405 | SPN-S000000343345 | 1000 | 700 | 60-80% | CANTERBURY TOWN 33/11KV | 321 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10096029785 | Retail/Financial and Professional Services | 5972 | C | Natural Gas | 4 | 208 | Heating and Mechanical Ventilation | 2025-04-19 |  | 0.8 | FALSE | 51.2723 | 1.062 | SPN-S000000008410 | 14783700000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1201 | 38.3 | UNIT 1, STURRY ROAD RETAIL PARK, STURRY ROAD | CANTERBURY | CT1 1WZ | Canterbury |  | Retail Warehouse And Premises | bigbox | 2 | 5617.4 | 60465 | GIA | 857500 | CANTERBURY LOCAL 33/11KV | inside-area | 1.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 29 | 8.93 | 506 | 28 | 1171660 | SPN-S000000342344 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 91 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2939 | 1.106 | SPN-S000000008597 | 538575145;14477093000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1202 | 38.3 | RUMWOOD NURSERIES, NEW ROAD | MAIDSTONE | ME17 3ND | Maidstone |  | Garden Centre And Premises | bigbox | 1 | 5407.37 | 58204 | NIA | 67000 | SHEPWAY 33/11KV | inside-area | 2.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 31 | 8.59 | 487 | 47 | 1441065 | SPN-R000000864405-000-129Z | 200 | 140 | 60-80% | SHEPWAY 33/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2403 | 0.58163 | SPN-S000000008644 | 14848526000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1203 | 38.3 | SAINSBURY'S SUPERMARKETS LTD, KINGSMEAD ROAD | CANTERBURY | CT1 1BW | Canterbury |  | Superstore And Premises | bigbox | 1 | 5097 | 54864 | GIA | 1100000 | CANTERBURY TOWN 33/11KV | inside-area | 0.05 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 32 | 8.1 | 459 | 27 | 1003912 | SPN-S000000342918 | 1000 | 500 | 40-60% | CANTERBURY TOWN 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062279262 | Retail/Financial and Professional Services | 5548 | C | Biomass | 4 |  | Heating and Mechanical Ventilation | 2025-06-06 |  | 1 | FALSE | 51.2845 | 1.0855 | SPN-S000000008410 | 14260084000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1204 | 38.3 | BUSHEYFIELDS ROAD | HERNE BAY | CT6 7LJ | Canterbury | CANTERBURY GARDEN CENTRE | Garden Centre And Premises | bigbox | 1 | 5085.68 | 54742 | NIA | 97000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.21 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 33 | 8.08 | 458 | 28 | 1177383 | SPN-R000000841707-000-031Z | 100 | 30 | 20-40% | CANTERBURY LOCAL 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3414 | 1.1259 | SPN-S000000008597 | 6766732000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1205 | 38.3 | B & Q 132-152, STURRY ROAD | CANTERBURY | CT1 1DP | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 5029.35 | 54135 | GIA | 570000 | CANTERBURY TOWN 33/11KV | inside-area | 1.08 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 33 | 7.99 | 453 | 27 | 1004641 | SPN-S000000342631 | 800 | 560 | 60-80% | CANTERBURY TOWN 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2896 | 1.0989 | SPN-S000000008410 | 1204562000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1206 | 38.3 | THANET WAY | WHITSTABLE | CT5 3JB | Canterbury | B & Q SUPERSTORE | Retail Warehouse And Premises | bigbox | 1 | 4863.3 | 52348 | GIA | 432500 | HERNE BAY 33/11KV | inside-area | 2.03 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 34 | 7.73 | 438 | 16 | 725479 | SPN-S000000341437 | 500 | 250 | 40-60% | WHITSTABLE 33/11KV | 80 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10094582890 | A3/A4/A5 Restaurant and Cafes/Drinking Establishments and Hot Food takeaways | 163 | A | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2023-01-23 |  | 1 | FALSE | 51.3601 | 1.0677 | SPN-S000000008417 | 295248145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1207 | 38.3 | TESCOS, GROVE GREEN DISTRICT CENTRE, GROVEWOOD DRIVE NORTH | MAIDSTONE | ME14 5TQ | Maidstone |  | Superstore And Premises | bigbox | 1 | 4791.82 | 51579 | GIA | 1590000 | WATERSIDE 33/11KV | inside-area | 2.58 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 35 | 7.61 | 431 | 44 | 1675047 | SPN-S000000394091 | 1000 | 700 | 60-80% | MAIDSTONE NORTH 132/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2771 | 0.55619 | SPN-S000000008529 | 8834187000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1208 | 38.3 | J SAINSBURY PLC, ROMNEY PLACE | MAIDSTONE | ME15 6SE | Maidstone |  | Superstore And Premises | bigbox | 1 | 4726 | 50870 | GIA | 1320000 | BARMING 33/11KV | inside-area | 1.36 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 4.1 | Green | 22.8 | 18.7 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 21 | 15.9 | Winter | 18.0952 | 3.8 | Green (Over 5% headroom) | 17825 | 35 | 7.51 | 425 | 3 | 121581 | SPN-S000000394996 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2634 | 0.50719 | SPN-S000000008527 | 8786251000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1209 | 38.3 | SAINSBURYS, REEVES WAY | WHITSTABLE | CT5 3QS | Canterbury |  | Superstore And Premises | bigbox | 1 | 4701.9 | 50611 | GIA | 1210000 | WHITSTABLE 33/11KV | inside-area | 2.08 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 35 | 7.47 | 423 | 11 | 579540 | SPN-S000000342470 | 500 | 250 | 40-60% | WHITSTABLE 33/11KV | 224 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062301226 | Retail/Financial and Professional Services | 4574 | C | Biomass | 4 |  | Heating and Mechanical Ventilation | 2023-03-17 |  | 1 | FALSE | 51.3575 | 1.0614 | SPN-S000000008516 | 13625715000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1210 | 38.3 | UNITS 1 & 2, MAYBROOK RETAIL PARK, VAUXHALL ROAD | CANTERBURY | CT1 1ZG | Canterbury |  | Leisure Centre And Premises | bigbox | 1 | 4546.38 | 48937 | GIA | 219000 | CANTERBURY LOCAL 33/11KV | inside-area | 1.14 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 36 | 7.22 | 364 | 28 | 1183188 | SPN-S000000343604 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033172973 | A1/A2 Retail and Financial/Professional services | 4653 | B | Natural Gas | 4 |  | Air Conditioning | 2020-09-17 |  | 1 | FALSE | 51.293 | 1.1035 | SPN-S000000008597 | 7471309000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1211 | 38.3 | HOMEBASE, ST PETERS STREET | MAIDSTONE | ME16 0SN | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 4525.15 | 48708 | GIA | 402500 | WATERSIDE 33/11KV | inside-area | 0.27 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 37 | 7.19 | 407 | 44 | 1677918 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022892613 | A1/A2 Retail and Financial/Professional services | 3362 | C | Natural Gas | 4 |  | Air Conditioning | 2018-10-10 |  | 0.5 | FALSE | 51.2749 | 0.51705 | SPN-S000000008529 | 2855453000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1212 | 38.3 | MAIDSTONE AUDI, CHATHAM ROAD | MAIDSTONE | ME14 3AA | Maidstone |  | Car Showroom And Premises | bigbox | 1 | 4519.9 | 48652 | GIA | 720000 | WATERSIDE 33/11KV | inside-area | 2.54 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 37 | 7.18 | 407 | 44 | 1677974 | SPN-S000000392415 | 315 | 220 | 60-80% | MAIDSTONE GRID SOUTH | 284 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2996 | 0.51309 | SPN-S000000008529 | 8405953000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1213 | 38.3 | 6, MARSHWOOD CLOSE | CANTERBURY | CT1 1DX | Canterbury | JORDAN & JARRETT LTD | Retail Warehouse And Premises; Warehouse And Premises | bigbox | 2 | 4516.62 | 48616 | GIA | 337000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.85 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 37 | 7.18 | 406 | 28 | 1183509 | SPN-S000000343062 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618827 | Offices and Workshop Businesses | 115 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-07-18 |  | 1 | FALSE | 51.2913 | 1.0996 | SPN-S000000008597 | 9536469000;522165145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1214 | 38.3 | ISLAND ROAD | CANTERBURY | CT2 0EZ | Canterbury | PERRYS | Car Showroom And Premises | bigbox | 1 | 3932.03 | 42324 | GIA | 345000 | CANTERBURY LOCAL 33/11KV | inside-area | 4.75 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 42 | 6.25 | 354 | 28 | 1189801 | SPN-S000000343792 | 315 | 220 | 60-80% | CANTERBURY LOCAL 33/11KV | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100060815415 | A3/A4/A5 Restaurant and Cafes/Drinking Establishments and Hot Food takeaways | 529 | E | Natural Gas | 3 |  | Air Conditioning | 2017-07-18 |  | 1 | FALSE | 51.3107 | 1.148 | SPN-S000000008597 | 289938145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1215 | 38.3 | MARKS & SPENCER PLC, ECLIPSE PARK, SITTINGBOURNE ROAD | MAIDSTONE | ME14 3EN | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 3925 | 42248 | GIA | 1150000 | MAIDSTONE GRID SOUTH | inside-area | 1.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 42 | 6.24 | 353 | 19 | 766536 | SPN-S000000394805 | 800 | 560 | 60-80% | MAIDSTONE GRID SOUTH | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095448067 | A1/A2 Retail and Financial/Professional services | 7727 | A | Natural Gas | 5 |  | Air Conditioning | 2020-07-27 |  | 1 | FALSE | 51.2856 | 0.5466 | SPN-S000000009533 | 12873380000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1216 | 38.3 | JOHNSONS NURSERY, THANET WAY | WHITSTABLE | CT5 3JD | Canterbury |  | Garden Centre And Premises | bigbox | 1 | 3910.77 | 42095 | NIA | 58000 | HERNE BAY 33/11KV | inside-area | 2.01 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 42 | 6.21 | 352 | 16 | 735732 | SPN-S000000341437 | 500 | 250 | 40-60% | WHITSTABLE 33/11KV | 151 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3594 | 1.0676 | SPN-S000000008417 | 295650145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1217 | 38.3 | UNIT 1 EDDINGTON WAY, EDDINGTON BUSINESS PARK | HERNE BAY | CT6 5UJ | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 3873.7 | 41696 | GIA | 367500 | HERNE BAY 33/11KV | inside-area | 2.05 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 43 | 6.16 | 349 | 16 | 736131 | SPN-S000000343354 | 315 | 94 | 20-40% | HERNE BAY 33/11KV | 231 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033166494 | A1/A2 Retail and Financial/Professional services | 4139 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-11-19 |  | 0.5 | FALSE | 51.3621 | 1.1218 | SPN-S000000008417 | 8582594000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1218 | 38.3 | WAITROSE CANTERBURY, ST GEORGES CENTRE, ST GEORGES PLACE | CANTERBURY | CT1 1UL | Canterbury |  | Superstore And Premises | bigbox | 1 | 3858.44 | 41532 | GIA | 730000 | CANTERBURY TOWN 33/11KV | inside-area | 0.97 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 43 | 6.13 | 347 | 27 | 1017244 | SPN-S000000341793 | 750 | 375 | 40-60% | CANTERBURY TOWN 33/11KV | 96 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000677699 | A1/A2 Retail and Financial/Professional services | 8611 | B | Natural Gas | 5 |  | Air Conditioning | 2012-01-27 |  | 1 | FALSE | 51.2763 | 1.0861 | SPN-S000000008410 | 7947308000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1219 | 38.3 | LOCKMEADOW HEALTH CLUB, LOCKMEADOW LEISURE COMPLEX, BARKER ROAD | MAIDSTONE | ME16 8LW | Maidstone |  | Leisure Centre And Premises | bigbox | 1 | 3728.37 | 40132 | GIA | 295000 | WATERSIDE 33/11KV | inside-area | 0.81 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 44 | 5.92 | 298 | 44 | 1686494 | SPN-S000000392170 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2697 | 0.51893 | SPN-S000000008529 | 14424523000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1220 | 38.3 | SITE 1, WINCHEAP INDUSTRIAL ESTATE, COW LANE | CANTERBURY | CT1 3RR | Canterbury |  | Builders Merchant & Premises | bigbox | 1 | 3545.34 | 38162 | GIA | 234000 | CANTERBURY TOWN 33/11KV | inside-area | 1.93 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 47 | 5.63 | 319 | 27 | 1020614 | SPN-S000000341805 | 500 | 150 | 20-40% | CANTERBURY TOWN 33/11KV | 143 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10090317886 | A1/A2 Retail and Financial/Professional services | 3330 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2012-10-17 |  | 0.5 | FALSE | 51.2722 | 1.0664 | SPN-S000000008410 | 14239254000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1221 | 38.3 | WICKES, ST PETERS STREET | MAIDSTONE | ME16 0SN | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 3500.36 | 37678 | GIA | 700000 | WATERSIDE 33/11KV | inside-area | 0.27 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 47 | 5.56 | 315 | 44 | 1688948 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022892203 | A1/A2 Retail and Financial/Professional services | 3525 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2022-06-07 |  | 1 | FALSE | 51.2749 | 0.51705 | SPN-S000000008529 | 3843708000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1222 | 38.3 | MARKET WAY | CANTERBURY | CT2 7JJ | Canterbury | JEWSONS LTD | Builders Merchants & Premises | bigbox | 1 | 3346.7 | 36024 | GIA | 243000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.17 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 49 | 5.32 | 301 | 28 | 1196101 | SPN-S000000343009 | 315 | 220 | 60-80% | CANTERBURY TOWN 33/11KV | 156 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000683355 | Retail/Financial and Professional Services | 1807 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2022-08-25 |  | 1 | FALSE | 51.2899 | 1.0856 | SPN-S000000008597 | 154996145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1223 | 38.3 | UNIT 3, STURRY ROAD | CANTERBURY | CT1 1AD | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 3340 | 35951 | GIA | 452500 | CANTERBURY LOCAL 33/11KV | inside-area | 1.37 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 50 | 5.31 | 301 | 28 | 1196174 | SPN-S000000341679 | 500 | 250 | 40-60% | CANTERBURY LOCAL 33/11KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033154962 | Retail/Financial and Professional Services | 3487 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2023-02-09 |  | 0.5 | FALSE | 51.2925 | 1.1069 | SPN-S000000008597 | 2604515000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1224 | 38.3 | BARKER ROAD | MAIDSTONE | ME16 8DW | Maidstone | B & Q RETAIL LTD | Retail Warehouse And Premises | bigbox | 1 | 3331.97 | 35865 | GIA | 312500 | WATERSIDE 33/11KV | inside-area | 0.75 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 50 | 5.29 | 300 | 44 | 1690761 | SPN-S000000392170 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 43 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003717085 | Retail/Financial and Professional Services | 2456 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-02-10 |  | 1 | FALSE | 51.2704 | 0.51745 | SPN-S000000008529 | 25043148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1225 | 38.3 | UNITS 1-3 AT 13, MAYNARD ROAD | CANTERBURY | CT1 3RH | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 3231.98 | 34789 | GIA | 193000 | CANTERBURY TOWN 33/11KV | inside-area | 1.81 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 51 | 5.14 | 291 | 27 | 1023987 | SPN-S000000342189 | 1000 | 500 | 40-60% | CANTERBURY TOWN 33/11KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033169637 | A1/A2 Retail and Financial/Professional services | 3320 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2015-03-09 |  | 0.67 | FALSE | 51.273 | 1.0675 | SPN-S000000008410 | 9471627000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1226 | 38.3 | SUTTON ROAD | MAIDSTONE | ME15 9NW | Maidstone | DRAKE & FLETCHER | Car Showroom And Premises | bigbox | 1 | 3151.84 | 33926 | GIA | 442500 | SHEPWAY 33/11KV | inside-area | 1.47 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 53 | 5.01 | 284 | 47 | 1465343 | SPN-S000000392174 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2413 | 0.56244 | SPN-S000000008644 | 506239000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1227 | 38.3 | UNIT A LEVEL 3 & 4, THE MALL SHOPPING CENTRE 42-50, KING STREET | MAIDSTONE | ME14 1BS | Maidstone |  | Leisure Centre And Premises | bigbox | 1 | 2965.71 | 31923 | GIA | 124000 | WATERSIDE 33/11KV | inside-area | 0.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 56 | 4.71 | 237 | 44 | 1694703 | SPN-S000000392017 | 1000 | 500 | 40-60% | MAIDSTONE NORTH 132/11KV | 79 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003688759 | Retail/Financial and Professional Services | 2021 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2026-08-10 |  | 0.57 | FALSE | 51.2736 | 0.52514 | SPN-S000000008529 | 13467107000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1228 | 38.3 | MOTORLINE LTD, BIRCHOLT ROAD | MAIDSTONE | ME15 9XT | Maidstone |  | Car Showroom And Premises | bigbox | 1 | 2861.54 | 30801 | GIA | 650000 | SHEPWAY 33/11KV | inside-area | 1.88 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 58 | 4.55 | 258 | 47 | 1468468 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2359 | 0.5586 | SPN-S000000008644 | 7976815000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1229 | 38.3 | 10, BEACH STREET | HERNE BAY | CT6 5PL | Canterbury | MORRISONS | Superstore And Premises | bigbox | 1 | 2810.74 | 30255 | GIA | 330000 | HERNE BAY 33/11KV | inside-area | 2.76 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 59 | 4.47 | 253 | 16 | 747572 | SPN-S000000343162 | 315 | -32 | -20-0% | HERNE BAY 33/11KV | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3697 | 1.1262 | SPN-S000000008417 | 5942717000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1230 | 38.3 | 255, WINCHEAP | CANTERBURY | CT1 3TT | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 2808.22 | 30227 | GIA | 395000 | CANTERBURY TOWN 33/11KV | inside-area | 2.13 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 59 | 4.46 | 253 | 27 | 1028549 | SPN-S000000343345 | 1000 | 700 | 60-80% | CANTERBURY TOWN 33/11KV | 184 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033172925 | Retail/Financial and Professional Services | 4188 | A | Natural Gas | 4 |  | Air Conditioning | 2025-07-14 |  | 0.5 | FALSE | 51.2705 | 1.0652 | SPN-S000000008410 | 3601010000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1231 | 38.3 | MBS HOUSE 80, EDDINGTON LANE | HERNE BAY | CT6 5TR | Canterbury |  | Builders Merchant | bigbox | 1 | 2748.62 | 29586 | GIA | 191000 | HERNE BAY 33/11KV | inside-area | 2.13 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 60 | 4.37 | 247 | 16 | 748241 | SPN-S000000341445 | 500 | 350 | 60-80% | HERNE BAY 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3631 | 1.1223 | SPN-S000000008417 | 8456647000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1232 | 38.3 | MERCEDES BENZ OF MAIDSTONE, BIRCHOLT ROAD | MAIDSTONE | ME15 9YN | Maidstone |  | Car Showroom And Premises | bigbox | 1 | 2732.49 | 29412 | GIA | 510000 | SHEPWAY 33/11KV | inside-area | 1.72 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 61 | 4.34 | 246 | 47 | 1469857 | SPN-S000000393272 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2397 | 0.56502 | SPN-S000000008644 | 7917096000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1233 | 38.3 | PLEASANT VIEW NURSERIES, PLOUGH WENTS ROAD | MAIDSTONE | ME17 3SA | Maidstone |  | Garden Centre And Premises | bigbox | 1 | 2694.88 | 29007 | NIA | 33500 | SHEPWAY 33/11KV | inside-area | 3.2 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 61 | 4.28 | 243 | 47 | 1470262 | SPN-S000000394578 | 100 | 10 | 0-20% | SHEPWAY 33/11KV | 24 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2257 | 0.56878 | SPN-S000000008644 | 61196148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1234 | 38.3 | 59-63, STURRY ROAD | CANTERBURY | CT1 1BU | Canterbury |  | Car Showroom And Premises | bigbox | 1 | 2676.35 | 28808 | GIA | 277500 | CANTERBURY TOWN 33/11KV | inside-area | 0.34 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 62 | 4.25 | 241 | 27 | 1029968 | SPN-S000000341799 | 1000 | 500 | 40-60% | CANTERBURY TOWN 33/11KV | 165 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.286 | 1.09 | SPN-S000000008410 | 536543000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1235 | 38.3 | AUDI, BROAD OAK ROAD | CANTERBURY | CT2 7BE | Canterbury |  | Car Showroom And Premises | bigbox | 1 | 2667.23 | 28710 | GIA | 520000 | CANTERBURY LOCAL 33/11KV | inside-area | 1.1 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 62 | 4.24 | 240 | 28 | 1203415 | SPN-S000000342636 | 315 | 32 | 0-20% | CANTERBURY LOCAL 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2965 | 1.1006 | SPN-S000000008597 | 13487073000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1236 | 38.3 | DUNELM MILL, LONDON ROAD | MAIDSTONE | ME16 0DT | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 2527 | 27200 | GIA | 460000 | WATERSIDE 33/11KV | inside-area | 0.73 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 66 | 4.02 | 227 | 44 | 1699426 | SPN-S000000394948 | 500 | 350 | 60-80% | FAIRMEADOW 11KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022900394 | A1/A2 Retail and Financial/Professional services | 1921 | C | Natural Gas | 3 | 2 | Heating and Mechanical Ventilation | 2021-05-07 |  | 0.5 | FALSE | 51.2771 | 0.50855 | SPN-S000000008529 | 8264236000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1237 | 38.3 | UNIT MSU2 THE WHITEFRIARS CENTRE 2, GRAVEL WALK | CANTERBURY | CT1 2TF | Canterbury |  | Superstore And Premises | bigbox | 1 | 2502.9 | 26941 | GIA | 535000 | CANTERBURY TOWN 33/11KV | inside-area | 0.96 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 66 | 3.98 | 225 | 27 | 1031835 | SPN-S000000343439 | 1000 | 700 | 60-80% | CANTERBURY TOWN 33/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2768 | 1.0806 | SPN-S000000008410 | 8794516000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1238 | 38.3 | HOLLYWOOD BOWL, LOCKMEADOW, BARKER ROAD | MAIDSTONE | ME16 8RG | Maidstone |  | Bowling Alley And Premises | bigbox | 1 | 2495.85 | 26865 | GIA | 201000 | WATERSIDE 33/11KV | inside-area | 0.93 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 66 | 3.97 | 200 | 44 | 1699761 | SPN-S000000394763 | 1000 | 700 | 60-80% | FAIRMEADOW 11KV | 61 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2686 | 0.51821 | SPN-S000000008529 | 8910534000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1239 | 38.3 | 34, ROPER ROAD | CANTERBURY | CT2 7EL | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 2460.58 | 26485 | GIA | 370000 | CANTERBURY TOWN 33/11KV | inside-area | 0.79 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 67 | 3.91 | 221 | 27 | 1032291 | SPN-S000000343391 | 315 | 220 | 60-80% | CANTERBURY TOWN 33/11KV | 100 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2848 | 1.0739 | SPN-S000000008410 | 158668145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1240 | 38.3 | NEXT PLC, ECLIPSE PARK, SITTINGBOURNE ROAD | MAIDSTONE | ME14 3EN | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 2459.78 | 26477 | GIA | 785000 | MAIDSTONE GRID SOUTH | inside-area | 1.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 67 | 3.91 | 221 | 19 | 782307 | SPN-S000000394805 | 800 | 560 | 60-80% | MAIDSTONE GRID SOUTH | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014306808 | Offices and Workshop Businesses | 1016 | C | Natural Gas | 4 | 2 | Air Conditioning | 2022-11-22 |  | 1 | FALSE | 51.2856 | 0.5466 | SPN-S000000009533 | 9521525000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1241 | 38.3 | MOTORLINE PEUGEOT, BROAD OAK ROAD | CANTERBURY | CT2 7PX | Canterbury |  | Car Showroom And Premises | bigbox | 1 | 2353.4 | 25332 | GIA | 305000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 70 | 3.74 | 212 | 28 | 1206793 | SPN-S000000341794 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033160630 | A1/A2 Retail and Financial/Professional services | 2347 | C | Natural Gas | 3 |  | Air Conditioning | 2020-03-30 |  | 1 | FALSE | 51.2922 | 1.0918 | SPN-S000000008597 | 7361494000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1242 | 38.3 | NASONS CANTERBURY LTD, MAYNARD ROAD | CANTERBURY | CT1 3RH | Canterbury |  | Retail Warehouse And Premises | bigbox | 1 | 2262.17 | 24350 | GIA | 132000 | CANTERBURY TOWN 33/11KV | inside-area | 1.81 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 73 | 3.59 | 204 | 27 | 1034426 | SPN-S000000342189 | 1000 | 500 | 40-60% | CANTERBURY TOWN 33/11KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618836 | A1/A2 Retail and Financial/Professional services | 621 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-10-03 |  | 0.5 | FALSE | 51.273 | 1.0675 | SPN-S000000008410 | 12509642000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1243 | 38.3 | MID KENT SHOPPING CENTRE, CASTLE ROAD | MAIDSTONE | ME16 0PU | Maidstone | WAITROSE LTD | Supermarket And Premises | bigbox | 1 | 2223.7 | 23936 | GIA | 214000 | WATERSIDE 33/11KV | inside-area | 1.83 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 74 | 3.53 | 200 | 44 | 1702690 | SPN-S000000391172 | 500 | 250 | 40-60% | FAIRMEADOW 11KV | 27 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003717233 | A1/A2 Retail and Financial/Professional services | 298 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-03-11 |  | 1 | FALSE | 51.2861 | 0.49711 | SPN-S000000008529 | 181610148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1244 | 38.3 | D F S, LONDON ROAD | MAIDSTONE | ME16 0LP | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 2219.2 | 23887 | GIA | 332500 | WATERSIDE 33/11KV | inside-area | 2.36 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 75 | 3.53 | 200 | 44 | 1702739 | SPN-S000000394387 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 246 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003707048 | Retail/Financial and Professional Services | 1920 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-03-08 |  | 1 | FALSE | 51.2872 | 0.48944 | SPN-S000000008529 | 480430000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1245 | 38.3 | TK MAXX, ST PETERS STREET | MAIDSTONE | ME16 0SN | Maidstone |  | Retail Warehouse And Premises | bigbox | 1 | 2039.8 | 21956 | GIA | 395000 | WATERSIDE 33/11KV | inside-area | 0.27 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 81 | 3.24 | 184 | 44 | 1704670 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022892613 | A1/A2 Retail and Financial/Professional services | 3362 | C | Natural Gas | 4 |  | Air Conditioning | 2018-10-10 |  | 0.67 | FALSE | 51.2749 | 0.51705 | SPN-S000000008529 | 5119801000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1246 | 38.2 | RIPLEYS GARDEN CENTRE, ASHFORD ROAD | ASHFORD | TN26 3LF | Ashford |  | Garden Centre And Premises | bigbox | 1 | 3912.67 | 42116 | NIA | 29750 | ASHFORD WEST 33/6.6KV | inside-area | 3.24 | Ashford Grid | Sellindge | East Kent Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.1 | Thermal | 0 | 0 | 0 | 0 | 2.4 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 6.3 | 4.8 | Winter | 36.5079 | 2.3 | Green (Over 5% headroom) | 17112 | 41 | 6.22 | 352 | 4 | 56416 | SPN-R000000850206-000-055Z | 100 | 30 | 20-40% | ASHFORD WEST 33/6.6KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1185 | 0.74077 | SPN-S000000008502 | 14553082000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1247 | 38.2 | COOP, HIGH STREET | CRANBROOK | TN17 3DR | Tunbridge Wells |  | Supermarket And Premises | bigbox | 1 | 2320.4 | 24977 | GIA | 550000 | CRANBROOK 33/11KV | inside-area | 0.09 | Hartley Grid | Ninfield | East Sussex Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.2 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 35.4839 | 2.2 | Green (Over 5% headroom) | 17112 | 69 | 3.69 | 209 | 3 | 44878 | SPN-S000000441909 | 200 | -20 | -20-0% | CRANBROOK 33/11KV | 48 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.0956 | 0.53222 | SPN-S000000008381 | 8831633000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1248 | 38 | N & P SEYMOUR, GOUDHURST ROAD | CRANBROOK | TN17 2PT | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1752.06 | 18859 | GIA | 137000 | GOUDHURST 33/11KV | inside-area | 3.62 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 100 | 2.78 | 44 | 6 | 173141 | SPN-R000000836009-000-156Z | 100 | 50 | 40-60% | GOUDHURST 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1131 | 0.52212 | SPN-S000000008360 | 11340559000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1249 | 38 | UNITS 6-7, SPELMONDEN FARM, SPELMONDEN ROAD | CRANBROOK | TN17 1HD | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1437.46 | 15473 | GIA | 94500 | GOUDHURST 33/11KV | inside-area | 2.67 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 100 | 2.28 | 36 | 6 | 176527 | SPN-S000000451521 | 315 | 158 | 40-60% | GOUDHURST 33/11KV | 378 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1116 | 0.43212 | SPN-S000000008360 | 11933315000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1250 | 38 | UNIT 3, APPLE GROWERS ASSOCIATION, LAMBERHURST ROAD | TONBRIDGE | TN12 8DP | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1342.23 | 14448 | GIA | 52000 | GOUDHURST 33/11KV | inside-area | 4.06 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 100 | 2.13 | 34 | 6 | 177552 | SPN-S000000441187 | 100 | 10 | 0-20% | GOUDHURST 33/11KV | 179 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1287 | 0.4175 | SPN-S000000008360 | 7030388000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1251 | 38 | UNIT 9 THE NEW OAST, SPELMONDEN FARM, SPELMONDEN ROAD | CRANBROOK | TN17 1HE | Tunbridge Wells |  | Warehouse And Premises | industrial | 1 | 1147.9 | 12356 | GIA | 53500 | GOUDHURST 33/11KV | inside-area | 2.83 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 100 | 1.82 | 29 | 6 | 179644 | SPN-S000000451521 | 315 | 158 | 40-60% | GOUDHURST 33/11KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10024137622 | B1 Offices and Workshop businesses | 598 | B | Grid Supplied Electricity | 3 |  | Heating and Mechanical Ventilation | 2019-11-26 |  | 0.67 | FALSE | 51.1089 | 0.43041 | SPN-S000000008360 | 3566956000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1252 | 38 | UNIT 3 THE COW SHED, LITTLE COLDHARBOUR FARM, TONG LANE | TUNBRIDGE WELLS | TN3 8AD | Tunbridge Wells |  | Workshop And Premises | industrial | 1 | 1080 | 11625 | GIA | 70000 | GOUDHURST 33/11KV | inside-area | 5.18 | Hartley Grid | Ninfield | West Kent Zone | 6 | primary | 6 | Green | 13 | 7 | Thermal | 0 | 0 | 0 | 0 | 6.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 13 | 9.7 | Winter | 46.1538 | 6 | Green (Over 5% headroom) | 42781 | 100 | 1.72 | 49 | 6 | 180375 | [9 empty] | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1219 | 0.39728 | SPN-S000000008360 | 12811016000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1253 | 37.9 | HARWOODS LTD, STANFORDS END, HARTFIELD ROAD | EDENBRIDGE | TN8 5NF | Sevenoaks |  | Car Showroom And Premises | bigbox | 1 | 2447.78 | 26348 | GIA | 395000 | EDENBRIDGE 33/11KV | inside-area | 4.02 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 60 | 3.89 | 220 | 11 | 415625 | SPN-S000000442814 | 500 | 350 | 60-80% | EDENBRIDGE 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1817 | 0.074661 | SPN-S000000008614 | 12368081000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1254 | 37.3 | GREENACRES GARDEN CENTRE, BOROUGH GREEN ROAD | SEVENOAKS | TN15 9JA | Tonbridge & Malling |  | Garden Centre And Premises | bigbox | 1 | 6428.76 | 69199 | NIA | 11250 | WROTHAM HEATH 33/11KV | inside-area | 3.22 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 18 | 10.22 | 579 | 8 | 225978 | SPN-R000000851907-000-039Z | 100 | 30 | 20-40% | WROTHAM HEATH 33/11KV | 148 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.2914 | 0.29354 | SPN-S000000008519 | 14163810000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1255 | 37.1 | BUILDING S205, PANATTONI PARK, BARGE WAY | SITTINGBOURNE | ME10 2FD | Swale |  | Warehouse And Premises | industrial | 1 | 19535.9 | 210282 | GIA | 1810000 | GROVEHURST LOCAL | inside-area | 0.58 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 18 | 31.04 | 488 | 31 | 2757327 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3711 | 0.75165 | SPN-S000000008585 | 15015347000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1256 | 37.1 | FLOPLAST LTD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3FP | Swale |  | Factory And Premises | industrial | 1 | 18569.34 | 199879 | GIA | 1290000 | GROVEHURST LOCAL | inside-area | 1.77 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 19 | 29.51 | 1114 | 31 | 2767730 | SPN-S000000394748 | 1000 | 700 | 60-80% | GROVEHURST LOCAL | 174 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002457093 | B2 to B7 General Industrial and Special Industrial Groups | 19163 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2021-05-11 |  | 1 | FALSE | 51.3509 | 0.76121 | SPN-S000000008585 | 4253053000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1257 | 37.1 | UNIT H8 AT 5, TRIBUNE DRIVE | SITTINGBOURNE | ME10 2PG | Swale |  | Workshop And Premises | industrial | 1 | 1708.08 | 18386 | GIA | 102000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 2.71 | 77 | 31 | 2949223 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3522 | 0.73795 | SPN-S000000008585 | 534830145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1258 | 37.1 | UNIT 10 AT 21, TRIBUNE DRIVE | SITTINGBOURNE | ME10 2PG | Swale |  | Factory And Premises | industrial | 1 | 1629.8 | 17543 | GIA | 102000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 2.59 | 98 | 31 | 2950066 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062627058 | B8 Storage or Distribution | 572 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2017-08-21 |  | 0.67 | FALSE | 51.3522 | 0.73795 | SPN-S000000008585 | 333152147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1259 | 37.1 | OYSTER QUAY, CASTLE ROAD | SITTINGBOURNE | ME10 3EU | Swale | TOPBAND PLC | Workshop And Premises | industrial | 1 | 1512.2 | 16277 | GIA | 123000 | GROVEHURST LOCAL | inside-area | 1.74 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 2.4 | 68 | 31 | 2951332 | SPN-S000000391819 | 500 | 250 | 40-60% | GROVEHURST LOCAL | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3505 | 0.7568 | SPN-S000000008585 | 4166236000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1260 | 37.1 | ADAM ROUILLY LTD, CASTLE ROAD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3AG | Swale |  | Factory And Premises | industrial | 1 | 1503.71 | 16186 | GIA | 120000 | GROVEHURST LOCAL | inside-area | 1.72 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 2.39 | 90 | 31 | 2951423 | SPN-S000000394605 | 500 | 350 | 60-80% | SITTINGBOURNE TOWN 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023196566 | B1 Offices and Workshop businesses | 1239 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2017-02-13 |  | 0.5 | FALSE | 51.3507 | 0.75744 | SPN-S000000008585 | 2122321000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1261 | 37.1 | UNITS 42 44 & 46 | SITTINGBOURNE | ME10 2PT | Swale |  | Warehouse And Premises | industrial | 1 | 1336.9 | 14390 | GIA | 87500 | GROVEHURST LOCAL | inside-area | 2.08 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 2.12 | 33 | 31 | 2953219 | SPN-S000000391710 | 500 | 250 | 40-60% | GROVEHURST LOCAL | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3503 | 0.73755 | SPN-S000000008585 | 11478047000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1262 | 37.1 | UNIT D AT FLO PLAST LTD, HOWT GREEN, SHEPPEY WAY | SITTINGBOURNE | ME9 8QU | Swale |  | Factory And Premises | industrial | 1 | 1166.81 | 12559 | GIA | 105000 | GROVEHURST LOCAL | inside-area | 1.8 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.85 | 70 | 31 | 2955050 | SPN-S000000394545 | 800 | 560 | 60-80% | GROVEHURST LOCAL | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3734 | 0.73069 | SPN-S000000008585 | 14573689000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1263 | 37.1 | UNIT H, MILL WAY | SITTINGBOURNE | ME10 2PD | Swale |  | Factory And Premises | industrial | 1 | 1107.1 | 11917 | GIA | 138000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.76 | 66 | 31 | 2955692 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023200883 | B8 Storage or Distribution | 417 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-03-13 |  | 0.5 | FALSE | 51.3515 | 0.73965 | SPN-S000000008585 | 333171147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1264 | 37.1 | UNITS 7-8 SAXON SHORE BUSINESS PARK, CASTLE ROAD | SITTINGBOURNE | ME10 3EU | Swale |  | Workshop And Premises | industrial | 1 | 1100.35 | 11844 | GIA | 63500 | GROVEHURST LOCAL | inside-area | 1.74 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.75 | 50 | 31 | 2955765 | SPN-S000000391819 | 500 | 250 | 40-60% | GROVEHURST LOCAL | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023196249 | General Industrial and Special Industrial Groups | 604 | B | Other | 3 |  | Unconditioned | 2024-07-18 |  | 0.8 | FALSE | 51.3505 | 0.7568 | SPN-S000000008585 | 15086897000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1265 | 37.1 | UNIT 7A/B, MILL WAY | SITTINGBOURNE | ME10 2PG | Swale |  | Warehouse And Premises | industrial | 1 | 1060.6 | 11416 | GIA | 116000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.69 | 27 | 31 | 2956193 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023195911 | Retail/Financial and Professional Services | 936 | A | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-09-03 |  | 0.67 | FALSE | 51.3522 | 0.73795 | SPN-S000000008585 | 3896371000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1266 | 37.1 | UNIT 29, MILL WAY | SITTINGBOURNE | ME10 2PD | Swale |  | Warehouse And Premises | industrial | 1 | 1053 | 11334 | GIA | 119000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.67 | 26 | 31 | 2956275 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023200883 | B8 Storage or Distribution | 417 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-03-13 |  | 0.5 | FALSE | 51.3515 | 0.73965 | SPN-S000000008585 | 11085637000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1267 | 37.1 | UNITS 31A & B, TRIBUNE DRIVE | SITTINGBOURNE | ME10 2PG | Swale |  | Warehouse And Premises | industrial | 1 | 1041.7 | 11213 | GIA | 61000 | GROVEHURST LOCAL | inside-area | 1.89 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.66 | 26 | 31 | 2956396 | SPN-S000000391707 | 500 | 150 | 20-40% | GROVEHURST LOCAL | 68 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023195911 | Retail/Financial and Professional Services | 936 | A | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-09-03 |  | 0.67 | FALSE | 51.3522 | 0.73795 | SPN-S000000008585 | 11277247000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1268 | 37.1 | UNITS C & D | SITTINGBOURNE | ME10 2PJ | Swale |  | Warehouse And Premises | industrial | 1 | 1015.5 | 10931 | GIA | 111000 | GROVEHURST LOCAL | inside-area | 1.47 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 100 | 1.61 | 25 | 31 | 2956678 | SPN-S000000393841 | 500 | 250 | 40-60% | GROVEHURST LOCAL | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3587 | 0.73624 | SPN-S000000008585 | 3554181000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1269 | 36.8 | QED DESIGN & MANUFACTURE LTD, FAIRBOURNE LANE | MAIDSTONE | ME17 1LN | Maidstone |  | Factory And Premises | industrial | 1 | 1480.07 | 15931 | GIA | 87500 | HARRIETSHAM 33/11KV | inside-area | 3.2 | Ashford Grid | Sellindge | Mid Kent Zone | 5.1 | primary | 5.1 | Green | 16 | 10.9 | Thermal | 13.5 | 0 | 5.4 | 13.5 | 3.5 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | Green (Over 5% headroom) | 36364 | 100 | 2.35 | 89 | 5 | 1107502 | SPN-R000000841406-000-133Z | 100 | 10 | 0-20% | HARRIETSHAM 33/11KV | 388 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2295 | 0.66468 | SPN-S000000008414 | 12652671000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1270 | 36.8 | UNIT 3 WAREHOUSE, ROSE LANE INDUSTRIAL ESTATE, ROSE LANE | MAIDSTONE | ME17 2JN | Maidstone |  | Warehouse And Premises | industrial | 1 | 1404.7 | 15120 | GIA | 92000 | HARRIETSHAM 33/11KV | inside-area | 3.64 | Ashford Grid | Sellindge | Mid Kent Zone | 5.1 | primary | 5.1 | Green | 16 | 10.9 | Thermal | 13.5 | 0 | 5.4 | 13.5 | 3.5 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | Green (Over 5% headroom) | 36364 | 100 | 2.23 | 35 | 5 | 1108313 | SPN-R000000841410-000-113Z | 100 | 50 | 40-60% | HARRIETSHAM 33/11KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10091193436 | Storage or Distribution | 1325 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2022-11-08 |  | 1 | FALSE | 51.2191 | 0.7486 | SPN-S000000008414 | 11605164000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1271 | 36.8 | UNITS 1 & 2, NORTHDOWN HOUSE, ASHFORD ROAD | MAIDSTONE | ME17 1BN | Maidstone |  | Warehouse And Premises | industrial | 1 | 1168.63 | 12579 | GIA | 104000 | HARRIETSHAM 33/11KV | inside-area | 1.6 | Ashford Grid | Sellindge | Mid Kent Zone | 5.1 | primary | 5.1 | Green | 16 | 10.9 | Thermal | 13.5 | 0 | 5.4 | 13.5 | 3.5 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | Green (Over 5% headroom) | 36364 | 100 | 1.86 | 29 | 5 | 1110854 | SPN-S000000392138 | 200 | 60 | 20-40% | HARRIETSHAM 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2419 | 0.685 | SPN-S000000008414 | 8336507000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1272 | 36.6 | MARSH ROAD | ASHFORD | TN26 2JD | Ashford | HAMSTREET GARDEN CENTRE | Garden Centre And Premises | bigbox | 1 | 7161.37 | 77084 | NIA | 178000 | WAREHORNE 33/11KV | inside-area | 1.61 | Ruckinge Grid | Sellindge | East Kent Zone | 1.2 | primary | 1.2 | Green | 5 | 3.7 | Thermal | 0 | 0 | 0 | 0 | 0.5 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 4.9 | 4.5 | Winter | 26.5306 | 1.3 | Green (Over 5% headroom) | 8556 | 11 | 11.38 | 645 | 3 | 48910 | SPN-S000000361228 | 500 | 350 | 60-80% | WAREHORNE 33/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012860421 | B1 Offices and Workshop businesses | 207 | G | Oil | 3 |  | Heating and Natural Ventilation | 2019-01-22 |  | 1 | FALSE | 51.061 | 0.85915 | SPN-S000000008507 | 329156148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1273 | 36.5 | SAINSBURYS SUPERMARKET LTD, STATION ROAD | TONBRIDGE | TN12 0QE | Maidstone |  | Superstore And Premises | bigbox | 1 | 3090.95 | 33271 | GIA | 815000 | STAPLEHURST 33/6.6KV | inside-area | 0.59 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 24 | 4.91 | 278 | 7 | 380631 | SPN-S000000391000 | 800 | 560 | 60-80% | STAPLEHURST 33/6.6KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10095448528 | Retail/Financial and Professional Services | 3856 | B | Grid Supplied Electricity | 4 |  | Heating and Mechanical Ventilation | 2023-03-29 |  | 0.67 | FALSE | 51.1691 | 0.55243 | SPN-S000000008493 | 13233292000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1274 | 36.5 | TESCO, SMALLHYTHE ROAD | TENTERDEN | TN30 7LN | Ashford |  | Superstore And Premises | bigbox | 1 | 2861.8 | 30804 | GIA | 625000 | TENTERDEN 33/6.6KV | inside-area | 0.26 | Ruckinge Grid | Sellindge | East Sussex Zone | 1.1 | primary | 1.1 | Green | 11.9 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.8 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | Green (Over 5% headroom) | 7843 | 25 | 4.55 | 258 | 5 | 137906 | SPN-S000000362375 | 300 | 210 | 60-80% | TENTERDEN 33/6.6KV | 257 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004393874 | A1/A2 Retail and Financial/Professional services | 63 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2015-02-02 |  | 1 | FALSE | 51.0642 | 0.68592 | SPN-S000000008376 | 11044289000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1275 | 36.5 | SAYERS LANE | TENTERDEN | TN30 6BW | Ashford | WAITROSE | Superstore And Premises | bigbox | 1 | 2743.3 | 29529 | GIA | 492500 | TENTERDEN 33/6.6KV | inside-area | 0.26 | Ruckinge Grid | Sellindge | East Sussex Zone | 1.1 | primary | 1.1 | Green | 11.9 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.8 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | Green (Over 5% headroom) | 7843 | 27 | 4.36 | 247 | 5 | 139181 | SPN-S000000364552 | 1000 | 500 | 40-60% | TENTERDEN 33/6.6KV | 58 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012861522 | B1 Offices and Workshop businesses | 150 | F | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2013-08-03 |  | 1 | FALSE | 51.0683 | 0.68864 | SPN-S000000008376 | 331862148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1276 | 36.5 | BUMBLES PLANT CENTRE, CRANBROOK ROAD | CRANBROOK | TN17 2BL | Tunbridge Wells |  | Garden Centre And Premises | bigbox | 1 | 2064.72 | 22224 | NIA | 12250 | STAPLEHURST 33/6.6KV | inside-area | 3.79 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 35 | 3.28 | 186 | 7 | 391678 | SPN-R000000849307-000-040Z | 100 | 70 | 60-80% | STAPLEHURST 33/6.6KV | 108 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1339 | 0.55809 | SPN-S000000008493 | 2318016000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1277 | 36.4 | 21-22, PATRICIA WAY, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LQ | Thanet |  | Factory And Premises | industrial | 1 | 20403.18 | 219618 | GIA | 540000 | ST PETERS 33/11KV | inside-area | 1.66 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 16 | 32.42 | 1224 | 31 | 1274195 | SPN-S000000342803 | 800 | 400 | 40-60% | ST PETERS 33/11KV | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3573 | 1.4117 | SPN-S000000008478 | 1781189000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1278 | 36.4 | LEFT HANDSIDE OF FORMER ENGINEERING WORKSHOP | RAMSGATE | CT11 9FT | Thanet |  | Land Used For Storage, Office And Premises | office | 1 | 3272 | 35219 | GIA | 82500 | ST PETERS 33/11KV | inside-area | 5 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 97 | 5.2 | 229 | 31 | 1458594 | SPN-S000000342165 | 500 | 250 | 40-60% | RAMSGATE 33/11KV | 222 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.327 | 1.412 | SPN-S000000008478 | 10101506000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1279 | 36.4 | THE CAREY BUILDING NELSON COLLEGE LONDON, BROADSTAIRS CAMPUS, NORTHWOOD ROAD | BROADSTAIRS | CT10 2RZ | Thanet |  | Offices And Premises | office | 1 | 2516.07 | 27083 | NIA | 277500 | ST PETERS 33/11KV | inside-area | 1.5 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 4 | 176 | 31 | 1466730 | SPN-S000000342399 | 200 | 100 | 40-60% | THANET 33/11KV | 97 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3599 | 1.407 | SPN-S000000008478 | 14974651000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1280 | 36.4 | QUEENS HOUSE, QUEEN STREET | RAMSGATE | CT11 9DH | Thanet |  | Offices And Premises | office | 1 | 2140.5 | 23040 | NIA | 166000 | ST PETERS 33/11KV | inside-area | 4.4 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.4 | 150 | 31 | 1470773 | SPN-S000000342213 | 500 | 50 | 0-20% | RAMSGATE 33/11KV | 200 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3323 | 1.4148 | SPN-S000000008478 | 926427000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1281 | 36.4 | KENT COUNTY COUNCIL SOCIAL SERVICES DEPARTMENT ST PETERS HOUSE, DANE VALLEY ROAD | BROADSTAIRS | CT10 3FD | Thanet |  | Offices And Premises | office | 1 | 2108.3 | 22694 | NIA | 116000 | ST PETERS 33/11KV | inside-area | 0.14 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 3.35 | 148 | 31 | 1471119 | SPN-S000000342709 | 1000 | 500 | 40-60% | ST PETERS 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 100062281752 | B1 Offices and Workshop businesses | 2545 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-02-01 |  | 1 | FALSE | 51.3706 | 1.4171 | SPN-S000000008478 | 9490801000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1282 | 36.4 | ARMOURCOAT, LONGEND LANE | TONBRIDGE | TN12 9SE | Maidstone |  | Workshop And Premises | industrial | 1 | 1762.5 | 18971 | GIA | 115000 | MARDEN 33/11KV | inside-area | 1.7 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.8 | 79 | 24 | 900297 | SPN-R000000843308-000-163Z | 100 | 90 | 80-100% | MARDEN 33/11KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10014311977 | B1 Offices and Workshop businesses | 1915 | E | Grid Supplied Electricity | 3 | 2 | Heating and Natural Ventilation | 2018-05-12 |  | 0.5 | FALSE | 51.18 | 0.4672 | SPN-S000000008433 | 11663679000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1283 | 36.4 | THANET OFFSHORE WIND MILITARY ROAD WAREHOUSE, MILITARY ROAD | RAMSGATE | CT11 9LG | Thanet |  | Warehouse, Office And Premises | industrial | 1 | 1715.71 | 18468 | GIA | 165000 | ST PETERS 33/11KV | inside-area | 4.7 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 2.73 | 120 | 31 | 1475345 | SPN-S000000342213 | 500 | 50 | 0-20% | RAMSGATE 33/11KV | 128 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3296 | 1.4164 | SPN-S000000008478 | 10261347000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1284 | 36.4 | JW TIMBER LTD, LONGEND LANE | TONBRIDGE | TN12 9SE | Maidstone |  | Warehouse And Premises | industrial | 1 | 1706.82 | 18372 | GIA | 78000 | MARDEN 33/11KV | inside-area | 1.7 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.71 | 43 | 24 | 900896 | SPN-R000000843308-000-163Z | 100 | 90 | 80-100% | MARDEN 33/11KV | 177 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.18 | 0.4672 | SPN-S000000008433 | 5621492000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1285 | 36.4 | WALTON HALL, PATTENDEN LANE | TONBRIDGE | TN12 9QL | Maidstone |  | Workshop And Premises | industrial | 1 | 1548.4 | 16667 | GIA | 121000 | MARDEN 33/11KV | inside-area | 0.7 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.46 | 70 | 24 | 902601 | SPN-R000000843305-000-003Z | 50 | 15 | 20-40% | MARDEN 33/11KV | 83 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1817 | 0.48767 | SPN-S000000008433 | 6126981000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1286 | 36.4 | UNIT 4A, WHEELBARROW PARK, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1459.68 | 15712 | GIA | 86000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.32 | 36 | 24 | 903556 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10094441676 | B8 Storage or Distribution | 1114 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2019-05-10 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 11854293000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1287 | 36.4 | OAKLEIGH HOUSE, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1458.82 | 15703 | GIA | 107000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.32 | 36 | 24 | 903565 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1774 | 0.48987 | SPN-S000000008433 | 8992301000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1288 | 36.4 | UNIT 5A WHEELBARROW PARK, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1453.42 | 15644 | GIA | 84000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.31 | 36 | 24 | 903624 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10093304930 | Storage or Distribution | 1127 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-06-28 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 15010090000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1289 | 36.4 | 16, HORNET CLOSE, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LQ | Thanet |  | Factory And Premises | industrial | 1 | 1322.8 | 14238 | GIA | 82500 | ST PETERS 33/11KV | inside-area | 1.66 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 2.1 | 79 | 31 | 1479575 | SPN-S000000342803 | 800 | 400 | 40-60% | ST PETERS 33/11KV | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3573 | 1.4117 | SPN-S000000008478 | 459087145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1290 | 36.4 | AGRII, PATTENDEN LANE | TONBRIDGE | TN12 9QJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1274.38 | 13717 | GIA | 93000 | MARDEN 33/11KV | inside-area | 0.2 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 2.03 | 32 | 24 | 905551 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10094444334 | B2 to B7 General Industrial and Special Industrial Groups | 1396 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-01-06 |  | 1 | FALSE | 51.1774 | 0.48987 | SPN-S000000008433 | 8230763000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1291 | 36.4 | ELLINGTON WORKS, PRINCES ROAD | RAMSGATE | CT11 7SA | Thanet | THANET WARE LTD | Factory And Premises | industrial | 1 | 1229.47 | 13234 | GIA | 37500 | ST PETERS 33/11KV | inside-area | 3.38 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 1.95 | 74 | 31 | 1480579 | SPN-S000000342217 | 500 | 350 | 60-80% | RAMSGATE 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3418 | 1.41 | SPN-S000000008478 | 394662145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1292 | 36.4 | UNIT 2 PYRAMID BUSINESS PARK, POORHOLE LANE | BROADSTAIRS | CT10 2PP | Thanet |  | Warehouse And Premises | industrial | 1 | 1227.16 | 13209 | GIA | 57000 | ST PETERS 33/11KV | inside-area | 1.68 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 1.95 | 31 | 31 | 1480604 | SPN-S000000341997 | 300 | 90 | 20-40% | THANET 33/11KV | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3633 | 1.397 | SPN-S000000008478 | 7348792000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1293 | 36.4 | WAREHOUSE UNITS 3 & 4 & OFFICES 5 & 6, WILLOWS BUSINESS PARK, THE CEDARS, PATTENDEN LANE | TONBRIDGE | TN12 9QS | Maidstone |  | Warehouse, Office And Premises | industrial | 1 | 1137 | 12239 | GIA | 104000 | MARDEN 33/11KV | inside-area | 0.24 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 1.81 | 80 | 24 | 907029 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.48946 | SPN-S000000008433 | 13437794000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1294 | 36.4 | UNIT 11, WHEELBARROW INDUSTRIAL ESTATE, PATTENDEN LANE | TONBRIDGE | TN12 9QD | Maidstone |  | Warehouse And Premises | industrial | 1 | 1045.3 | 11252 | GIA | 81000 | MARDEN 33/11KV | inside-area | 0.23 | Hartley Grid | Ninfield | West Kent Zone | 4.8 | primary | 4.8 | Green | 12 | 6.9 | Thermal | 0 | 0 | 0 | 0 | 4.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 11.8 | 9 | Winter | 42.3729 | 5 | Green (Over 5% headroom) | 34225 | 100 | 1.66 | 26 | 24 | 908016 | SPN-S000000392928 | 500 | 250 | 40-60% | MARDEN 33/11KV | 111 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1777 | 0.49097 | SPN-S000000008433 | 108976000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1295 | 36.4 | BUILDING 2B, WHITEHALL WORKS, WHITEHALL ROAD | RAMSGATE | CT12 6BU | Thanet |  | Warehouse And Premises | industrial | 1 | 1034.8 | 11138 | GIA | 36750 | ST PETERS 33/11KV | inside-area | 3.24 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 1.64 | 26 | 31 | 1482675 | SPN-S000000342747 | 315 | 158 | 40-60% | RAMSGATE 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3437 | 1.4051 | SPN-S000000008478 | 6242447000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1296 | 36.4 | 19-25 BLENHIEM CLOSE, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2YF | Thanet |  | Workshop And Premises | industrial | 1 | 1031.95 | 11108 | GIA | 60500 | ST PETERS 33/11KV | inside-area | 1.76 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 1.64 | 46 | 31 | 1482705 | SPN-S000000342803 | 800 | 400 | 40-60% | ST PETERS 33/11KV | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | 200003079969 | B1 Offices and Workshop businesses | 310 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2018-02-01 |  | 0.5 | FALSE | 51.3562 | 1.4138 | SPN-S000000008478 | 7485766000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1297 | 36.4 | 15, HORNET CLOSE, PYSONS ROAD INDUSTRIAL ESTATE | BROADSTAIRS | CT10 2LA | Thanet |  | Factory And Premises | industrial | 1 | 1023.3 | 11015 | GIA | 66500 | ST PETERS 33/11KV | inside-area | 1.7 | Thanet Grid | Richborough | East Kent Zone | 4.8 | primary | 4.8 | Green | 22.8 | 18 | Thermal | 0 | 0 | 0 | 0 | 4.5 | Thanet Grid 33kV | 25.8 | GREEN | 0 | 49.9 | GREEN | 7 | 286.7 | 3 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | Green (Over 5% headroom) | 34225 | 100 | 1.63 | 61 | 31 | 1482798 | SPN-S000000343316 | 1000 | 700 | 60-80% | THANET 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 0 | 100 | 2025-04 | [12 empty] | 51.3583 | 1.4058 | SPN-S000000008478 | 456343145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1298 | 36.3 | UNIT B, STAPLEHURST NURSERIES, CLAPPER LANE | TONBRIDGE | TN12 0JT | Maidstone |  | Warehouse And Premises | industrial | 1 | 1730.77 | 18630 | GIA | 92500 | HEADCORN 33/6.6KV | inside-area | 4.77 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 100 | 2.75 | 43 | 6 | 149079 | SPN-R000000849309-000-049Z | 100 | 30 | 20-40% | HEADCORN 33/6.6KV | 204 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10093307199 | B8 Storage or Distribution | 982 | B | Natural Gas | 3 | 1 | Air Conditioning | 2018-05-14 |  | 1 | FALSE | 51.1807 | 0.54778 | SPN-S000000008365 | 14045039000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1299 | 36.3 | UNITS B2-B4, BARRADALE FARM, HEADCORN BUSINESS PARK, MAIDSTONE ROAD | ASHFORD | TN27 9PJ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1464.34 | 15762 | GIA | 134000 | HEADCORN 33/6.6KV | inside-area | 1.22 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 100 | 2.33 | 37 | 6 | 151947 | SPN-R000000836505-000-104Z | 100 | 30 | 20-40% | HEADCORN 33/6.6KV | 198 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10091195647 | B1 Offices and Workshop businesses | 418 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2013-10-04 |  | 0.8 | FALSE | 51.1802 | 0.61101 | SPN-S000000008365 | 14683672000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1300 | 36.3 | UNIT 1-2, BARRADALE FARM, HEADCORN BUSINESS PARK, MAIDSTONE ROAD | ASHFORD | TN27 9PJ | Maidstone |  | Workshop And Premises | industrial | 1 | 1354.24 | 14577 | GIA | 125000 | HEADCORN 33/6.6KV | inside-area | 1.22 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 100 | 2.15 | 61 | 6 | 153132 | SPN-R000000836505-000-104Z | 100 | 30 | 20-40% | HEADCORN 33/6.6KV | 198 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10091195647 | B1 Offices and Workshop businesses | 418 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2013-10-04 |  | 0.8 | FALSE | 51.1802 | 0.61101 | SPN-S000000008365 | 7451492000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1301 | 36.3 | WOODFORD DEPOT, MAIDSTONE ROAD | TONBRIDGE | TN12 0RH | Maidstone | HOMELEIGH TIMBER SUPPLIES LTD | Warehouse And Premises | industrial | 1 | 1183.1 | 12735 | GIA | 106000 | HEADCORN 33/6.6KV | inside-area | 5.02 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 100 | 1.88 | 30 | 6 | 154974 | SPN-R000000849309-000-048Z | 200 | 100 | 40-60% | HEADCORN 33/6.6KV | 265 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1863 | 0.54701 | SPN-S000000008365 | 182160148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1302 | 36.3 | THOUSAND ACRE FARM, HIGH HALDEN ROAD | ASHFORD | TN27 8BF | Ashford |  | Workshop And Premises | industrial | 1 | 1150.6 | 12385 | GIA | 62000 | HEADCORN 33/6.6KV | inside-area | 6.6 | Hartley Grid | Ninfield | West Kent Zone | 4.7 | primary | 4.7 | Green | 13 | 8.3 | Thermal | 0 | 4 | 2 | 4 | 3.1 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | Green (Over 5% headroom) | 33512 | 100 | 1.83 | 52 | 6 | 155324 | [9 empty] | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1166 | 0.65716 | SPN-S000000008365 | 12156785000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1303 | 36.1 | 1-2, BINGHAM ROAD | SITTINGBOURNE | ME10 3SU | Swale |  | Offices And Premises | office | 1 | 6790.83 | 73096 | NIA | 700000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.78 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 45 | 10.79 | 475 | 58 | 2450929 | SPN-S000000393241 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 209 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023199430 | General Industrial and Special Industrial Groups | 6968 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2022-07-18 |  | 1 | FALSE | 51.346 | 0.76215 | SPN-S000000008344 | 8117509000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1304 | 36.1 | SWALE HOUSE, EAST STREET | SITTINGBOURNE | ME10 3HT | Swale | SWALE BOROUGH COUNCIL | Offices And Premises | office | 1 | 5815.1 | 62593 | NIA | 360000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.88 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 52 | 9.24 | 407 | 58 | 2461432 | SPN-S000000393507 | 500 | 350 | 60-80% | SITTINGBOURNE TOWN 33/11KV | 19 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062375927 | Offices and Workshop Businesses | 5707 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-08-07 |  | 1 | FALSE | 51.3395 | 0.74103 | SPN-S000000008344 | 294751147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1305 | 36.1 | 13D-13E, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale |  | Warehouse And Premises | industrial | 1 | 1855.8 | 19976 | GIA | 128000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.95 | 46 | 58 | 2504049 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 6428202000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1306 | 36.1 | EXPRESS HOUSE, CASTLE ROAD | SITTINGBOURNE | ME10 3RN | Swale | UK MAIL LTD | Warehouse And Premises | industrial | 1 | 1837.38 | 19777 | GIA | 144000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.92 | 46 | 58 | 2504248 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10035063655 | Offices and Workshop Businesses | 1763 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-10-16 |  | 1 | FALSE | 51.3462 | 0.75036 | SPN-S000000008344 | 7154320000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1307 | 36.1 | BONHAM DRIVE, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RN | Swale | BRITISH REINFORCED CONCRETE ENGINEERING LTD | Factory And Premises | industrial | 1 | 1643.6 | 17692 | GIA | 125000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.53 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.61 | 99 | 58 | 2506333 | SPN-S000000394097 | 500 | 150 | 20-40% | SITTINGBOURNE TOWN 33/11KV | 94 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3462 | 0.75036 | SPN-S000000008344 | 335842147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1308 | 36.1 | 15A, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3UP | Swale |  | Factory And Premises | industrial | 1 | 1550.42 | 16689 | GIA | 116000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.22 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.46 | 93 | 58 | 2507336 | SPN-S000000394503 | 500 | 250 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023197483 | B8 Storage or Distribution | 1343 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2020-02-26 |  | 0.5 | FALSE | 51.3425 | 0.75027 | SPN-S000000008344 | 333403147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1309 | 36.1 | W S HUNT TRANSPORT (MEDWAY) LTD SWALESIDE, CASTLE ROAD | SITTINGBOURNE | ME10 3RL | Swale | W S HUNT TRANSPORT (MEDWAY) LTD | Warehouse And Premises | industrial | 1 | 1472 | 15844 | GIA | 136000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.77 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.34 | 37 | 58 | 2508181 | SPN-S000000391444 | 500 | 50 | 0-20% | SITTINGBOURNE TOWN 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3487 | 0.75285 | SPN-S000000008344 | 336150147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1310 | 36.1 | THE OLD WIRE SHOP UNIT 22, CRAFT MARSH TRADING ESTATE, GAS ROAD | SITTINGBOURNE | ME10 2QE | Swale |  | Workshop And Premises | industrial | 1 | 1370 | 14747 | OTH | 86500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 1.2 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.18 | 62 | 58 | 2509278 | SPN-S000000393383 | 1000 | 700 | 60-80% |  | 218 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3507 | 0.74358 | SPN-S000000008344 | 13390150000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1311 | 36.1 | NEWLANDS FARM, LEWSON STREET | SITTINGBOURNE | ME9 9JQ | Swale |  | Workshop And Premises | industrial | 1 | 1349 | 14521 | GIA | 46250 | SITTINGBOURNE TOWN 33/11KV | inside-area | 4.85 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.14 | 61 | 58 | 2509504 | SPN-R000000834401-000-182Z | 100 | 70 | 60-80% | SITTINGBOURNE TOWN 33/11KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3217 | 0.81514 | SPN-S000000008344 | 11566534000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1312 | 36.1 | KCS HOUSE, UPPER FIELD ROAD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3UP | Swale |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1335 | 14370 | GIA | 137000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.22 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.12 | 60 | 58 | 2509655 | SPN-S000000394503 | 500 | 250 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023197483 | B8 Storage or Distribution | 1343 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2020-02-26 |  | 0.75 | FALSE | 51.3425 | 0.75027 | SPN-S000000008344 | 7068460000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1313 | 36.1 | UNIT 14A EUROLINK INDUSTRIAL CENTRE, UPPER FIELD ROAD | SITTINGBOURNE | ME10 3UP | Swale |  | Workshop And Premises | industrial | 1 | 1296.28 | 13953 | GIA | 94500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.22 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 2.06 | 58 | 58 | 2510072 | SPN-S000000394503 | 500 | 250 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023197814 | General Industrial and Special Industrial Groups | 1409 | B | Biomass | 3 |  | Heating and Natural Ventilation | 2024-11-12 |  | 1 | FALSE | 51.3425 | 0.75027 | SPN-S000000008344 | 13865824000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1314 | 36.1 | UNIT C WIRE BELT BUILDING, CASTLE ROAD | SITTINGBOURNE | ME10 3EP | Swale |  | Workshop And Premises | industrial | 1 | 1201.09 | 12928 | GIA | 86500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.72 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 1.91 | 54 | 58 | 2511097 | SPN-S000000391444 | 500 | 50 | 0-20% | SITTINGBOURNE TOWN 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3481 | 0.75411 | SPN-S000000008344 | 9564394000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1315 | 36.1 | UNIT 2, CROWN QUAY LANE | SITTINGBOURNE | ME10 3JQ | Swale |  | Warehouse And Premises | industrial | 1 | 1128.74 | 12150 | GIA | 44000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.7 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 1.79 | 28 | 58 | 2511875 | SPN-S000000391212 | 800 | 720 | 80-100% | SITTINGBOURNE TOWN 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3423 | 0.74309 | SPN-S000000008344 | 14286178000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1316 | 36.1 | FACTORY UNIT 7, WEST LANE TRADING ESTATE, WEST LANE | SITTINGBOURNE | ME10 3TT | Swale |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1064.2 | 11455 | GIA | 49000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.44 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 1.69 | 48 | 58 | 2512570 | SPN-S000000394515 | 500 | 250 | 40-60% | SITTINGBOURNE TOWN 33/11KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 100062376185 | General Industrial and Special Industrial Groups | 1112 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-02-28 |  | 1 | FALSE | 51.3428 | 0.74701 | SPN-S000000008344 | 2906134000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1317 | 36.1 | EDUCATION HOUSE, CASTLE ROAD, EUROLINK INDUSTRIAL ESTATE | SITTINGBOURNE | ME10 3RL | Swale | B W FULFILMENT LTD EDUCATION DISTRIBUTION SERVICE | Warehouse And Premises | industrial | 1 | 1062.51 | 11437 | GIA | 90500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.77 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 1.69 | 27 | 58 | 2512588 | SPN-S000000391444 | 500 | 50 | 0-20% | SITTINGBOURNE TOWN 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3487 | 0.75285 | SPN-S000000008344 | 4463474000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1318 | 36.1 | UNIT 3, EUROLINK V, TRILOGY, SWALE WAY | SITTINGBOURNE | ME10 3NH | Swale |  | Warehouse And Premises | industrial | 1 | 1045.13 | 11250 | GIA | 110000 | SITTINGBOURNE TOWN 33/11KV | inside-area | 1.2 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 1.66 | 26 | 58 | 2512775 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10094600697 | B2 to B7 General Industrial and Special Industrial Groups | 3937 | A | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2021-04-25 |  | 0.8 | FALSE | 51.3448 | 0.76965 | SPN-S000000008344 | 13453847000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1319 | 36.1 | 8-9 AND 10, ANCHOR BUSINESS PARK, CASTLE ROAD | SITTINGBOURNE | ME10 3AE | Swale |  | Warehouse And Premises | industrial | 1 | 1003.35 | 10800 | GIA | 88500 | SITTINGBOURNE TOWN 33/11KV | inside-area | 0.9 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 4.6 | primary | 4.6 | Green | 26.8 | 16.5 | Thermal | 1.1 | 7.3 | 1.2 | 8.4 | 9.4 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | Green (Over 5% headroom) | 32799 | 100 | 1.59 | 25 | 58 | 2513225 | SPN-S000000391819 | 500 | 250 | 40-60% | GROVEHURST LOCAL | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 200002531501 | B2 to B7 General Industrial and Special Industrial Groups | 795 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-04-07 |  | 1 | FALSE | 51.3498 | 0.75417 | SPN-S000000008344 | 9222592000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1320 | 35.9 | BERKLEY HOUSE, CRETE HALL ROAD | GRAVESEND | DA11 9AA | Gravesham | METROPOLITAN AP5 PROPCO 1 LIMITED | Warehouse And Premises | industrial | 1 | 15155.42 | 163131 | GIA | 1240000 | ROSHERVILLE 33/6.6KV | inside-area | 0.53 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 19 | 24.08 | 379 | 14 | 1827725 | SPN-S000000311112 | 300 | 210 | 60-80% | ROSHERVILLE 33/6.6KV | 35 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4441 | 0.34759 | SPN-S000000008470 | 12272908000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1321 | 35.9 | INTERNATIONAL HOUSE, FOREST ROAD | TUNBRIDGE WELLS | TN2 5FE | Tunbridge Wells |  | Offices And Premises | office | 1 | 7725.05 | 83152 | NIA | 1840000 | TUNBRIDGE WELLS TOWN 11KV | inside-area | 1.63 | Tunbridge Wells Total | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 7.4 | 2.8 | Thermal | 0 | 5.6 | 0 | 5.6 | 4.1 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 7.2 | 6.5 | Winter | 62.5 | 4.5 | Green (Over 5% headroom) | 31373 | 38 | 12.28 | 541 | 2 | 94902 | SPN-S000000442727 | 500 | 350 | 60-80% | TUNBRIDGE WELLS TOWN 11KV | 145 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062554870 | B1 Offices and Workshop businesses | 8725 | B | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2023-09-07 |  | 1 | FALSE | 51.1262 | 0.27899 | SPN-S000000007371 | 14526320000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1322 | 35.9 | 1-3, PELHAM ROAD | GRAVESEND | DA11 0JJ | Gravesham |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1556.2 | 16751 | GIA | 114000 | ROSHERVILLE 33/6.6KV | inside-area | 0.59 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 2.47 | 70 | 14 | 1974105 | SPN-S000000311160 | 500 | 50 | 0-20% | ROSHERVILLE 33/6.6KV | 173 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4369 | 0.35666 | SPN-S000000008470 | 390307147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1323 | 35.9 | UNIT C1 & C2, WEST MILL, IMPERIAL BUSINESS ESTATE | GRAVESEND | DA11 0DL | Gravesham |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1177.35 | 12673 | GIA | 126000 | ROSHERVILLE 33/6.6KV | inside-area | 0.22 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 1.87 | 53 | 14 | 1978183 | SPN-S000000316858 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012011481 | General Industrial and Special Industrial Groups | 497 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-09-20 |  | 1 | FALSE | 51.4435 | 0.35667 | SPN-S000000008470 | 598753000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1324 | 35.9 | UNITS E1 & E2, WEST MILL, IMPERIAL BUSINESS ESTATE | GRAVESEND | DA11 0DL | Gravesham |  | Warehouse And Premises | industrial | 1 | 1082.33 | 11650 | GIA | 145000 | ROSHERVILLE 33/6.6KV | inside-area | 0.22 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 1.72 | 27 | 14 | 1979206 | SPN-S000000316858 | 1000 | 500 | 40-60% | ROSHERVILLE 33/6.6KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012015425 | Storage or Distribution | 478 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-11-07 |  | 1 | FALSE | 51.4435 | 0.35667 | SPN-S000000008470 | 7289616000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1325 | 35.8 | ASDA STORES LTD, LONDON ROAD | SWANLEY | BR8 7UN | Sevenoaks |  | Superstore And Premises | bigbox | 2 | 22910.9 | 246611 | GIA | 3370000 | SWANLEY 33/11KV | inside-area | 1.38 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 19 | 36.41 | 2062 | 18 | 826042 | SPN-S000000316306 | 750 | 375 | 40-60% | SWANLEY 33/11KV | 128 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.397 | 0.1747 | SPN-S000000008528 | 15168670000;9012186000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1326 | 35.7 | MANAGEMENT SUITE, UPPER EAST VILLAGE | DARTFORD | DA9 9SF | Dartford |  | Offices And Premises | office | 1 | 1041.98 | 11216 | NIA | 158000 | STONE MARSHES 33/11KV | inside-area | 1.4 | Northfleet East | Northfleet | West Kent Zone | 8.8 | primary | 8.8 | Green | 27.8 | 13.8 | Thermal | 1.5 | 1 | 0 | 2.5 | 7.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 26.7 | 20.5 | Summer | 40 | 8.2 | Green (Over 5% headroom) | 62745 | 100 | 1.66 | 73 | 2 | 195300 | SPN-S000000324040 | 1000 | 700 | 60-80% | STONE MARSHES 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4392 | 0.27337 | SPN-S000000008544 | 4102280000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1327 | 35.7 | DERING WAY | GRAVESEND | DA12 2QX | Gravesham | COMMA OIL AND CHEMICAL LTD | Factory And Premises | industrial | 1 | 14910.29 | 160493 | GIA | 755000 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.61 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 19 | 23.69 | 895 | 10 | 257433 | SPN-S000000311299 | 800 | 720 | 80-100% | GRAVESEND TOWN 33/6.6KV | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4399 | 0.39232 | SPN-S000000008409 | 2970159000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1328 | 35.7 | UNIT M, FIRCROFT WAY | EDENBRIDGE | TN8 6EL | Sevenoaks |  | Workshop And Premises | industrial | 1 | 1841.8 | 19825 | GIA | 141000 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 100 | 2.93 | 83 | 9 | 232461 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 50002017298 | B8 Storage or Distribution | 1842 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-10-11 |  | 1 | FALSE | 51.2066 | 0.063969 | SPN-S000000008408 | 4752494000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1329 | 35.7 | THAMES SHIPREPAIR SERVICE LTD, WHARF ROAD | GRAVESEND | DA12 2RU | Gravesham |  | Workshop And Premises | industrial | 1 | 1610.78 | 17338 | GIA | 95000 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.44 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 2.56 | 72 | 10 | 400588 | SPN-S000000311103 | 800 | 720 | 80-100% | GRAVESEND TOWN 33/6.6KV | 139 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012032028 | B8 Storage or Distribution | 525 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-07-22 |  | 0.5 | FALSE | 51.4427 | 0.38995 | SPN-S000000008409 | 5646759000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1330 | 35.7 | STORAGE BUILDINGS, HENDEN MANOR, IDE HILL ROAD | SEVENOAKS | TN14 6LA | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1524.8 | 16413 | GIA | 91000 | FOUR ELMS 33/11KV | inside-area | 1.16 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 100 | 2.42 | 38 | 9 | 235873 | SPN-R000000840805-000-172Z | 200 | 180 | 80-100% | FOUR ELMS 33/11KV | 179 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2334 | 0.12164 | SPN-S000000008408 | 13880924000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1331 | 35.7 | EMS INSTALLATION LTD, WHARF ROAD | GRAVESEND | DA12 2RZ | Gravesham |  | Factory And Premises | industrial | 1 | 1489.81 | 16036 | GIA | 146000 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.12 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 2.37 | 89 | 10 | 401890 | SPN-S000000311733 | 800 | 560 | 60-80% | GRAVESEND TOWN 33/6.6KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4425 | 0.38433 | SPN-S000000008409 | 7053472000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1332 | 35.7 | UNIT F, FIRCROFT WAY | EDENBRIDGE | TN8 6EL | Sevenoaks |  | Factory And Premises | industrial | 1 | 1364.1 | 14683 | GIA | 111000 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 100 | 2.17 | 82 | 9 | 237603 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2066 | 0.063969 | SPN-S000000008408 | 12384848000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1333 | 35.7 | PLOT 2, NORFOLK ROAD | GRAVESEND | DA12 2PS | Gravesham |  | Workshop And Premises | industrial | 1 | 1271.23 | 13683 | GIA | 98500 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.38 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 2.02 | 57 | 10 | 404243 | SPN-S000000312283 | 300 | 90 | 20-40% | GRAVESEND TOWN 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200002883428 | General Industrial and Special Industrial Groups | 990 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-08-02 |  | 1 | FALSE | 51.4414 | 0.38944 | SPN-S000000008409 | 9128355000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1334 | 35.7 | UNIT 1, DENTON WHARF, MARK LANE | GRAVESEND | DA12 2QB | Gravesham |  | Warehouse And Premises | industrial | 1 | 1186.06 | 12767 | GIA | 94500 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.84 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 1.88 | 30 | 10 | 405159 | SPN-S000000311311 | 500 | 350 | 60-80% | GRAVESEND TOWN 33/6.6KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10012012353 | Storage or Distribution | 1211 | D | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2022-07-05 |  | 1 | FALSE | 51.4428 | 0.39588 | SPN-S000000008409 | 3903550000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1335 | 35.7 | UNIT J, FIRCROFT WAY | EDENBRIDGE | TN8 6EJ | Sevenoaks |  | Factory And Premises | industrial | 1 | 1068.03 | 11496 | GIA | 97500 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 100 | 1.7 | 64 | 9 | 240790 | SPN-S000000443124 | 500 | 350 | 60-80% | EDENBRIDGE 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062593027 | B2 to B7 General Industrial and Special Industrial Groups | 421 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-02-20 |  | 0.5 | FALSE | 51.2071 | 0.063618 | SPN-S000000008408 | 11938761000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1336 | 35.7 | ALBION PARADE | GRAVESEND | DA12 2RW | Gravesham | FINCH | Workshop And Premises | industrial | 1 | 1061.45 | 11425 | GIA | 56500 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.18 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 1.69 | 48 | 10 | 406501 | SPN-S000000311733 | 800 | 560 | 60-80% | GRAVESEND TOWN 33/6.6KV | 28 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4431 | 0.38425 | SPN-S000000008409 | 89841147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1337 | 35.7 | UNIT E, FIRCROFT WAY | EDENBRIDGE | TN8 6EL | Sevenoaks |  | Factory And Premises | industrial | 1 | 1045.2 | 11250 | GIA | 87000 | FOUR ELMS 33/11KV | inside-area | 3.9 | Dormansland Grid | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 12 | 7.7 | Thermal | 0 | 0 | 1 | 0 | 4.5 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | Green (Over 5% headroom) | 30660 | 100 | 1.66 | 63 | 9 | 241036 | SPN-S000000451299 | 1000 | 700 | 60-80% | EDENBRIDGE 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2066 | 0.063969 | SPN-S000000008408 | 12384846000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1338 | 35.7 | KTM MEAT LTD, NORFOLK ROAD | GRAVESEND | DA12 2PS | Gravesham |  | Warehouse And Premises | industrial | 1 | 1020.93 | 10989 | GIA | 75500 | GRAVESEND TOWN 33/6.6KV | inside-area | 0.38 | Northfleet East | Northfleet | West Kent Zone | 4.3 | primary | 4.3 | Green | 18.3 | 14 | Thermal | 3.5 | 6 | 1.2 | 9.5 | 1.7 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | Green (Over 5% headroom) | 30660 | 100 | 1.62 | 26 | 10 | 406937 | SPN-S000000312283 | 300 | 90 | 20-40% | GRAVESEND TOWN 33/6.6KV | 138 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062311780 | B2 to B7 General Industrial and Special Industrial Groups | 554 | D | Oil | 3 |  | Heating and Natural Ventilation | 2021-10-13 |  | 0.5 | FALSE | 51.4414 | 0.38944 | SPN-S000000008409 | 4861864000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1339 | 35.5 | UNITS D-E, COMPASS CENTRE NORTH, CHATHAM MARITIME | CHATHAM | ME4 4YG | Medway |  | Offices And Premises | office | 1 | 1350.3 | 14534 | NIA | 193000 | CHATHAM HILL 33/11KV | inside-area | 2.44 | Chatham Grid | Kingsnorth | Mid Kent Zone | 8.6 | primary | 8.6 | Green | 47 | 35.6 | Thermal | 8.2 | 7 | 2.8 | 15.2 | 6.1 | Chatham Grid 33kV | 43.2 | GREEN | 17.6 |  | RED | 3 | 60.6 | 0 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | Green (Over 5% headroom) | 61319 | 100 | 2.15 | 95 | 25 | 1101208 | SPN-S000000316877 | 500 | 250 | 40-60% | CHATHAM HILL 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 44022783 | Offices and Workshop Businesses | 449 | C | Natural Gas | 3 |  | Air Conditioning | 2024-05-16 |  | 0.8 | FALSE | 51.3993 | 0.53604 | SPN-S000000008645 | 6691032000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1340 | 35.5 | TONBRIDGE CASTLE, CASTLE STREET | TONBRIDGE | TN9 1BH | Tonbridge & Malling | TONBRIDGE & MALLING BOROUGH COUNCIL | Offices And Premises | office | 1 | 1217.96 | 13110 | NIA | 79500 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.21 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.94 | 85 | 50 | 1809806 | SPN-S000000451468 | 300 | 210 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 108 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1969 | 0.27488 | SPN-S000000008504 | 123575148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1341 | 35.5 | MULTIMEDIA HOUSE, HILL STREET | TUNBRIDGE WELLS | TN1 2BY | Tunbridge Wells |  | Offices And Premises | office | 1 | 1200.42 | 12921 | NIA | 174000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 6.68 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.91 | 84 | 50 | 1809995 | SPN-S000000444090 | 800 | 400 | 40-60% | TUNBRIDGE WELLS TOWN 11KV | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.1373 | 0.2667 | SPN-S000000008504 | 333903148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1342 | 35.5 | GND & LWR GND FLRS, WEALD COURT 103, TONBRIDGE ROAD | TONBRIDGE | TN11 9HL | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1198.8 | 12904 | NIA | 171000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 2.78 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.91 | 84 | 50 | 1810012 | SPN-S000000441816 | 800 | 400 | 40-60% | TONBRIDGE TOWN 33/6.6KV | 50 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 200000966382 | Offices and Workshop Businesses | 1066 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2026-04-02 |  | 0.8 | FALSE | 51.2151 | 0.2439 | SPN-S000000008504 | 10940409000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1343 | 35.5 | BANK HOUSE, BANK STREET | TONBRIDGE | TN9 1BL | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1124.6 | 12105 | NIA | 214000 | TONBRIDGE TOWN 33/6.6KV | inside-area | 0.2 | Tunbridge Wells Total | Northfleet | West Kent Zone | 8.6 | primary | 8.6 | Green | 22.8 | 14.2 | Thermal | 0 | 0 | 0 | 0 | 5.3 | Tunbridge Wells Grid 33kV | 36.7 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | Green (Over 5% headroom) | 61319 | 100 | 1.79 | 79 | 50 | 1810811 | SPN-S000000451468 | 300 | 210 | 60-80% | TONBRIDGE TOWN 33/6.6KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062593613 | B1 Offices and Workshop businesses | 101 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-01-12 |  | 1 | FALSE | 51.1976 | 0.2747 | SPN-S000000008504 | 7163482000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1344 | 35 | TESCO SUPERSTORE, PARK FARM | ASHFORD | TN23 3LU | Ashford |  | Superstore And Premises | bigbox | 1 | 8964.78 | 96496 | GIA | 2120000 | SEVINGTON 33/11KV | inside-area | 1.87 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 14.25 | 807 | 28 | 958929 | SPN-S000000371077 | 500 | 350 | 60-80% | SEVINGTON 33/11KV | 263 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1233 | 0.86518 | SPN-S000000008595 | 11675494000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1345 | 35 | TESCO STORES LTD, HYTHE ROAD | ASHFORD | TN24 0YE | Ashford |  | Superstore And Premises | bigbox | 1 | 8409.28 | 90517 | GIA | 2040000 | SEVINGTON 33/11KV | inside-area | 1.9 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 13.36 | 757 | 28 | 964908 | SPN-S000000361001 | 200 | 60 | 20-40% | SEVINGTON 33/11KV | 333 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062559843 | Retail/Financial and Professional Services | 7078 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2025-02-20 |  | 1 | FALSE | 51.1361 | 0.91503 | SPN-S000000008595 | 13061121000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1346 | 35 | ASDA SUPERSTORE, KIMBERLEY WAY | ASHFORD | TN24 0SE | Ashford |  | Superstore And Premises | bigbox | 1 | 6943.89 | 74743 | GIA | 1580000 | SEVINGTON 33/11KV | inside-area | 1.08 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 11.03 | 625 | 28 | 980682 | SPN-S000000371061 | 800 | 560 | 60-80% | SEVINGTON 33/11KV | 148 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1344 | 0.87853 | SPN-S000000008595 | 9012097000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1347 | 35 | MONUMENT WAY, ORBITAL PARK | ASHFORD | TN24 0HB | Ashford | CAFFYNS PLC; DRAKE & FLETCHER | Car Showroom And Premises | bigbox | 2 | 5271.51 | 56742 | GIA | 1022500 | SEVINGTON 33/11KV | inside-area | 0.12 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 8.38 | 474 | 28 | 998683 | SPN-S000000364953 | 800 | 400 | 40-60% | SEVINGTON 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004393393 | B1 Offices and Workshop businesses | 700 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2012-10-19 |  | 1 | FALSE | 51.1273 | 0.8905 | SPN-S000000008595 | 1568279000;1190694000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1348 | 35 | BROAD OAK, THE BOULEVARD, ORBITAL PARK | ASHFORD | TN24 0GA | Ashford |  | Car Showroom And Premises | bigbox | 1 | 2678.3 | 28829 | GIA | 600000 | SEVINGTON 33/11KV | inside-area | 0.24 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 4.26 | 241 | 28 | 1026596 | SPN-S000000371004 | 800 | 560 | 60-80% | SEVINGTON 33/11KV | 187 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012852085 | B1 Offices and Workshop businesses | 4233 | D | Natural Gas | 4 | 2 | Heating and Natural Ventilation | 2015-11-26 |  | 0.5 | FALSE | 51.1291 | 0.89403 | SPN-S000000008595 | 4361614000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1349 | 35 | UNIT 2A, ASHFORD BUSINESS PARK, BARREY ROAD | ASHFORD | TN24 0SG | Ashford |  | Retail Warehouse And Premises | bigbox | 1 | 2511.38 | 27032 | GIA | 427500 | SEVINGTON 33/11KV | inside-area | 1.04 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 3.99 | 226 | 28 | 1028393 | SPN-S000000364337 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1299 | 0.90543 | SPN-S000000008595 | 10540937000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1350 | 35 | WICKES UNIT J, FOSTER ROAD, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Retail Warehouse And Premises | bigbox | 1 | 2423.72 | 26089 | GIA | 482500 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 3.85 | 218 | 28 | 1029336 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560432 | A1/A2 Retail and Financial/Professional services | 2615 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2021-04-19 |  | 0.67 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 11275869000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1351 | 34.9 | ROMAN HOUSE, ROMAN SQUARE | SITTINGBOURNE | ME10 4BJ | Swale |  | Offices And Premises | office | 1 | 1557.4 | 16764 | NIA | 125000 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.51 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.47 | 109 | 25 | 1198613 | SPN-S000000393350 | 500 | 250 | 40-60% | SITTINGBOURNE WEST 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10035063812 | B1 Offices and Workshop businesses | 364 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-10-19 |  | 1 | FALSE | 51.3395 | 0.73678 | SPN-S000000008444 | 926972000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1352 | 34.9 | BLDG 730, GUILLAT AVENUE, KENT SCIENCE PARK | SITTINGBOURNE | ME9 8GU | Swale |  | Offices And Premises | office | 1 | 1386.49 | 14924 | NIA | 197000 | SITTINGBOURNE WEST 33/11KV | inside-area | 3.33 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.2 | 97 | 25 | 1200453 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023202012 | B2 to B7 General Industrial and Special Industrial Groups | 2970 | E | District Heating | 4 | 1 | Heating and Mechanical Ventilation | 2013-10-15 |  | 0.75 | FALSE | 51.3121 | 0.72601 | SPN-S000000008444 | 11327952000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1353 | 34.9 | DIVISIONAL COUNTY OFFICES, AVENUE OF REMEMBRANCE | SITTINGBOURNE | ME10 4DE | Swale | KENT COUNTY COUNCIL | Offices And Premises | office | 1 | 1297.7 | 13968 | NIA | 93500 | SITTINGBOURNE WEST 33/11KV | inside-area | 1.5 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 17.6 | Green | 45.8 | 24.1 | Thermal | 25.8 | 4.3 | 0 | 30.1 | 16.3 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 44.4 | 32.4 | Winter | 47.2973 | 21 | Green (Over 5% headroom) | 58467 | 100 | 2.06 | 91 | 25 | 1201409 | SPN-S000000393350 | 500 | 250 | 40-60% | SITTINGBOURNE WEST 33/11KV | 263 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 |  | General Assembly and Leisure, Night Clubs, and Theatres | 1243 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2025-05-30 |  | 0.5 | FALSE | 51.3369 | 0.73569 | SPN-S000000008444 | 291519147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1354 | 34.9 | OFFICES AT WESTON WORKS, BRENT HILL | FAVERSHAM | ME13 7EB | Swale |  | Offices And Premises | office | 1 | 1205.5 | 12976 | GIA | 79500 | FAVERSHAM 33/11KV | inside-area | 1.7 | Sittingbourne Grid | Kemsley | Mid Kent Zone | 8.2 | bsp | 15.2 | Green | 41.3 | 19.4 | Thermal | 0 | 0 | 0 | 0 | 13.1 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | Green (Over 5% headroom) | 58467 | 100 | 1.92 | 84 | 21 | 1081059 | SPN-S000000391881 | 500 | 350 | 60-80% | FAVERSHAM 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3184 | 0.88897 | SPN-S000000008405 | 14535126000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1355 | 34.5 | ASDA GREENHITHE SUPERSTORE, CROSSWAYS BOULEVARD | DARTFORD | DA9 9BT | Dartford |  | Superstore And Premises | bigbox | 2 | 16034.94 | 172598 | GIA | 3700000 | SWANSCOMBE 33/11KV | inside-area | 1.93 | Dartford Grid 33kV | Littlebrook | West Kent Zone | 5.6 | primary | 5.6 | Green | 13 | 6.4 | Thermal | 0 | 2.5 | 0 | 2.5 | 8.8 | Dartford Grid A 33kV | 64.9 | GREEN | 139 |  | RED | 2 | 21.5 | 0 | 13 | 9.9 | Winter | 50.7692 | 6.6 | Green (Over 5% headroom) | 39929 | 23 | 25.48 | 1443 | 2 | 74959 | SPN-S000000311025 | 200 | 100 | 40-60% | SWANSCOMBE 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 0 | 2027-10 | 10009428526 | A1/A2 Retail and Financial/Professional services | 8014 | D | Natural Gas | 4 | 3 | Air Conditioning | 2015-07-06 |  | 0.75 | FALSE | 51.4525 | 0.27521 | SPN-S000000008522 | 14546706000;14546706000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1356 | 34.1 | GIVAUDAN, KENNINGTON ROAD | ASHFORD | TN24 0LT | Ashford |  | Works And Premises | industrial | 1 | 23868.57 | 256919 | GIA | 690000 | ASHFORD EAST 33/11KV | inside-area | 0.48 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 9 | 37.93 | 1432 | 27 | 1708168 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062559839 | B1 Offices and Workshop businesses | 877 | E | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2013-12-20 |  | 1 | FALSE | 51.1521 | 0.90148 | SPN-S000000008402 | 7953597000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1357 | 34.1 | EUREKA SCIENCE & BUSINESS PARK, BOCKHANGER | ASHFORD | TN25 4AQ | Ashford | COTY MANUFACTURING UK | Factory And Premises | industrial | 1 | 22225.9 | 239237 | GIA | 1150000 | ASHFORD EAST 33/11KV | inside-area | 2.06 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 9 | 35.32 | 1334 | 27 | 1725850 | SPN-S000000371401 | 500 | 150 | 20-40% | ASHFORD EAST 33/11KV | 301 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.165 | 0.87218 | SPN-S000000008402 | 533403145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1358 | 34.1 | GND FLR 1500, EUREKA PARK, LOWER PEMBERTON | ASHFORD | TN25 4BF | Ashford |  | Offices And Premises | office | 4 | 5481.36 | 59001 | NIA | 1254000 | ASHFORD EAST 33/11KV | inside-area | 2.67 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 37 | 8.71 | 384 | 27 | 1906086 | SPN-S000000364855 | 1000 | 700 | 60-80% | ASHFORD EAST 33/11KV | 175 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012859379 | B1 Offices and Workshop businesses | 3692 | C | Grid Supplied Electricity | 4 |  | Air Conditioning | 2018-12-13 |  | 1 | FALSE | 51.1704 | 0.8674 | SPN-S000000008402 | 15093694000;15139773000;15139777000;15093696000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1359 | 34.1 | ENTERPRISE HOUSE, EUREKA SCIENCE & BUSINESS PARK, BOCKHANGER | ASHFORD | TN25 4AG | Ashford |  | Offices And Premises | office | 1 | 4558.8 | 49070 | NIA | 650000 | ASHFORD EAST 33/11KV | inside-area | 2.73 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 45 | 7.24 | 319 | 27 | 1916017 | SPN-S000000364855 | 1000 | 700 | 60-80% | ASHFORD EAST 33/11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1698 | 0.86559 | SPN-S000000008402 | 533405145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1360 | 34.1 | 210, EUREKA PARK, UPPER PEMBERTON | ASHFORD | TN25 4AZ | Ashford |  | Offices And Premises | office | 3 | 4483.46 | 48260 | NIA | 1045000 | ASHFORD EAST 33/11KV | inside-area | 2.6 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 46 | 7.12 | 314 | 27 | 1916827 | SPN-S000000371404 | 800 | 560 | 60-80% | ASHFORD EAST 33/11KV | 235 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1719 | 0.87074 | SPN-S000000008402 | 8570543000;10953369000;5765178000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1361 | 34.1 | KRONER HOUSE MAIN, EUROGATE BUSINESS PARK | ASHFORD | TN24 8XW | Ashford |  | Offices And Premises | office | 1 | 2136.4 | 22996 | NIA | 327500 | ASHFORD EAST 33/11KV | inside-area | 2.24 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 96 | 3.39 | 150 | 27 | 1942091 | SPN-S000000364546 | 800 | 560 | 60-80% | ASHFORD EAST 33/11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012865305 | B1 Offices and Workshop businesses | 675 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-07-30 |  | 0.5 | FALSE | 51.1622 | 0.86737 | SPN-S000000008402 | 7830830000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1362 | 34.1 | UNIT B, ST JAMES BUSINESS PARK | ASHFORD | TN24 8DH | Ashford |  | Warehouse And Premises | industrial | 1 | 1718.8 | 18501 | GIA | 140000 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.73 | 43 | 27 | 1946586 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1507 | 0.88453 | SPN-S000000008402 | 13542517000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1363 | 34.1 | PARK LEISURE LTD PT INCA HOUSE, TRINITY ROAD, EUREKA SCIENCE & BUSINESS PARK | ASHFORD | TN25 4AB | Ashford |  | Warehouse And Premises | industrial | 1 | 1642.3 | 17678 | GIA | 98500 | ASHFORD EAST 33/11KV | inside-area | 2.47 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.61 | 41 | 27 | 1947409 | SPN-S000000371073 | 500 | 150 | 20-40% | ASHFORD EAST 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012862681 | B1 Offices and Workshop businesses | 1616 | D | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2015-10-02 |  | 1 | FALSE | 51.1717 | 0.87315 | SPN-S000000008402 | 6756546000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1364 | 34.1 | HIGH BAY WAREHOUSE UNIT 15, HENWOOD INDUSTRIAL ESTATE | ASHFORD | TN24 8DH | Ashford |  | Warehouse And Premises | industrial | 1 | 1424.3 | 15331 | GIA | 85000 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.26 | 36 | 27 | 1949756 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848698 | B1 Offices and Workshop businesses | 570 | C | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2018-08-17 |  | 1 | FALSE | 51.1507 | 0.88453 | SPN-S000000008402 | 15050927000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1365 | 34.1 | UNIT 27, CREATIVE ENTERPRISE QUARTER, JAVELIN WAY | ASHFORD | TN24 8FN | Ashford |  | Warehouse And Premises | industrial | 1 | 1387.39 | 14934 | GIA | 170000 | ASHFORD EAST 33/11KV | inside-area | 0.76 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.2 | 35 | 27 | 1950153 | SPN-S000000364093 | 315 | 158 | 40-60% | ASHFORD EAST 33/11KV | 210 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012878564 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 1363 | B | Natural Gas | 4 |  | Heating and Natural Ventilation | 2022-04-25 |  | 1 | FALSE | 51.1509 | 0.89003 | SPN-S000000008402 | 13875207000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1366 | 34.1 | OFFICES UNIT 15, HENWOOD INDUSTRIAL ESTATE | ASHFORD | TN24 8DH | Ashford |  | Warehouse And Premises | industrial | 1 | 1359.5 | 14634 | GIA | 96500 | ASHFORD EAST 33/11KV | inside-area | 1.08 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.16 | 34 | 27 | 1950453 | SPN-S000000363524 |  |  | 40-60% | ASHFORD EAST 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848698 | B1 Offices and Workshop businesses | 570 | C | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2018-08-17 |  | 1 | FALSE | 51.1507 | 0.88453 | SPN-S000000008402 | 15050930000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1367 | 34.1 | UNIT 7A, JAVELIN ENTERPRISE PARK, JAVELIN WAY | ASHFORD | TN24 8DE | Ashford |  | Warehouse And Premises | industrial | 1 | 1285.64 | 13839 | GIA | 92000 | ASHFORD EAST 33/11KV | inside-area | 0.82 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.04 | 32 | 27 | 1951248 | SPN-S000000364093 | 315 | 158 | 40-60% | ASHFORD EAST 33/11KV | 129 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012851545 | C2 Residential Institutions - Residential schools | 310 | D | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2020-06-11 |  | 1 | FALSE | 51.1512 | 0.88844 | SPN-S000000008402 | 12798853000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1368 | 34 | CRANBROOK ROAD | CRANBROOK | TN17 4ET | Tunbridge Wells | CRANDEN DIAMOND PRODUCTS LTD | Workshop And Premises | industrial | 1 | 1518.16 | 16341 | GIA | 101000 | HAWKHURST 33/11KV | inside-area | 4.4 | Hartley Grid | Ninfield | East Sussex Zone | 3 | primary | 3 | Green | 15 | 10 | Thermal | 0 | 0 | 0 | 0 | 3.8 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 14.1 | 10.6 | Summer | 31.1321 | 3.3 | Green (Over 5% headroom) | 21390 | 100 | 2.41 | 68 | 3 | 98210 | SPN-R000000836306-000-150Z | 100 | 30 | 20-40% | HAWKHURST 33/11KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.0712 | 0.56225 | SPN-S000000008363 | 14245148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1369 | 34 | UNITS E & F, CUXTON INDUSTRIAL ESTATE, STATION ROAD | ROCHESTER | ME2 1AB | Medway |  | Workshop And Premises | industrial | 1 | 1100.81 | 11849 | GIA | 46000 | COBHAM 33/11KV | inside-area | 4.28 | Northfleet East | Northfleet | West Kent Zone | 3 | primary | 3 | Green | 13 | 10 | Thermal | 0 | 0 | 0 | 0 | 3 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 13 | 9.7 | Winter | 23.0769 | 3 | Green (Over 5% headroom) | 21390 | 100 | 1.75 | 50 | 0 | 0 | SPN-S000000311437 | 500 | 250 | 40-60% | COBHAM 33/11KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3736 | 0.45978 | SPN-S000000008498 | 124914000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1370 | 33.5 | BBMM SUITES 1-4 AT 10, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4LT | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1781.95 | 19181 | NIA | 440000 | MEREWORTH 33/11KV | inside-area | 2.86 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.83 | 125 | 30 | 985165 | SPN-S000000393147 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 124 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2757 | 0.39577 | SPN-S000000008643 | 7204264000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1371 | 33.5 | 2ND FLOOR 1, TOWER VIEW, KINGS HILL | WEST MALLING | ME19 4HA | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1580.91 | 17017 | NIA | 410000 | MEREWORTH 33/11KV | inside-area | 3.33 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.51 | 111 | 30 | 987329 | SPN-R000000852706-000-023Z | 50 | 15 | 20-40% | BARMING 33/11KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013923199 | Offices and Workshop Businesses | 3030 | D | Natural Gas | 4 |  | Air Conditioning | 2022-07-20 |  | 0.83 | FALSE | 51.2783 | 0.40131 | SPN-S000000008643 | 14861399000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1372 | 33.5 | SUITE 1 AT 17, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4UL | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1362.49 | 14666 | NIA | 292500 | MEREWORTH 33/11KV | inside-area | 2.87 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.17 | 95 | 30 | 989680 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2764 | 0.39432 | SPN-S000000008643 | 10936010000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1373 | 33.5 | SUITE D 1, ABBEY WOOD ROAD, KINGS HILL BUSINESS PARK | WEST MALLING | ME19 4YT | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1346.58 | 14494 | NIA | 347500 | MEREWORTH 33/11KV | inside-area | 3.1 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.14 | 94 | 30 | 989852 | SPN-S000000391580 | 800 | 560 | 60-80% | MEREWORTH 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062387381 | Offices and Workshop Businesses | 2163 | C | Grid Supplied Electricity | 3 |  | Heating and Mechanical Ventilation | 2023-04-05 |  | 1 | FALSE | 51.2783 | 0.39579 | SPN-S000000008643 | 12587013000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1374 | 33.5 | SUITE 2 AT 2, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4TA | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1336.77 | 14389 | NIA | 295000 | MEREWORTH 33/11KV | inside-area | 3 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.12 | 94 | 30 | 989957 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2775 | 0.39491 | SPN-S000000008643 | 10682276000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1375 | 33.5 | SUITE 1 AT 4, ABBEY WOOD ROAD, KINGS HILL BUSINESS PARK | WEST MALLING | ME19 4YT | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1323.12 | 14242 | NIA | 337500 | MEREWORTH 33/11KV | inside-area | 3.1 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 2.1 | 93 | 30 | 990104 | SPN-S000000391580 | 800 | 560 | 60-80% | MEREWORTH 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062387381 | Offices and Workshop Businesses | 2163 | C | Grid Supplied Electricity | 3 |  | Heating and Mechanical Ventilation | 2023-04-05 |  | 1 | FALSE | 51.2783 | 0.39579 | SPN-S000000008643 | 1895471000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1376 | 33.5 | SUITE 1 AT 6, ALEXANDER GROVE, KINGS HILL | WEST MALLING | ME19 4GR | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1040.06 | 11195 | NIA | 272500 | MEREWORTH 33/11KV | inside-area | 2.89 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 1.65 | 73 | 30 | 993151 | SPN-S000000394626 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 104 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 |  | B1 Offices and Workshop businesses | 1170 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-02-28 |  | 1 | FALSE | 51.2738 | 0.39987 | SPN-S000000008643 | 8232813000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1377 | 33.5 | RHS FRONT 18, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4BT | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1018.63 | 10964 | NIA | 275000 | MEREWORTH 33/11KV | inside-area | 3.08 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 1.62 | 71 | 30 | 993382 | SPN-S000000391580 | 800 | 560 | 60-80% | MEREWORTH 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2786 | 0.39482 | SPN-S000000008643 | 13883470000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1378 | 33.5 | SOUTH WEST 18, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4BT | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1018.63 | 10964 | NIA | 275000 | MEREWORTH 33/11KV | inside-area | 3.08 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 1.62 | 71 | 30 | 993382 | SPN-S000000391580 | 800 | 560 | 60-80% | MEREWORTH 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2786 | 0.39482 | SPN-S000000008643 | 15114507000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1379 | 33.5 | SUITE 1 AT 35, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4RR | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1018.4 | 10962 | NIA | 260000 | MEREWORTH 33/11KV | inside-area | 3.29 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 1.62 | 71 | 30 | 993384 | SPN-S000000391580 | 800 | 560 | 60-80% | MEREWORTH 33/11KV | 179 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2792 | 0.39832 | SPN-S000000008643 | 213655000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1380 | 33.5 | NORTH WEST 18, KINGS HILL AVENUE, KINGS HILL | WEST MALLING | ME19 4AE | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1016.88 | 10946 | NIA | 272500 | MEREWORTH 33/11KV | inside-area | 3.01 | Pembury Grid | Northfleet | Mid Kent Zone | 7.1 | primary | 7.1 | Green | 21.2 | 13.6 | Thermal | 0 | 0 | 0 | 0 | 5.8 | Pembury Grid 33kV | 57 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | Green (Over 5% headroom) | 50624 | 100 | 1.62 | 71 | 30 | 993400 | SPN-S000000392487 | 1000 | 700 | 60-80% | MEREWORTH 33/11KV | 154 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 100062387368 | Offices and Workshop Businesses | 3390 | B | Grid Supplied Electricity | 4 |  | Heating and Mechanical Ventilation | 2023-08-30 |  | 1 | FALSE | 51.2768 | 0.39675 | SPN-S000000008643 | 15091869000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1381 | 33.5 | ASHFORD CIVIC CENTRE, TANNERY LANE | ASHFORD | TN23 1PL | Ashford |  | Offices And Premises | office | 1 | 5143.4 | 55363 | NIA | 765000 | ASHFORD CENTRAL | inside-area | 0.61 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 33 | 8.17 | 360 | 36 | 912875 | SPN-S000000361974 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004397678 | B1 Offices and Workshop businesses | 200 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2012-05-21 |  | 1 | FALSE | 51.1467 | 0.87655 | SPN-S000000008302 | 14971781000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1382 | 33.5 | UNIT A2, BEAVER BUSINESS PARK | ASHFORD | TN23 7SH | Ashford |  | Workshop And Premises | industrial | 1 | 1803.4 | 19412 | GIA | 153000 | ASHFORD CENTRAL | inside-area | 1.09 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 95 | 2.87 | 81 | 36 | 948826 | SPN-S000000361020 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062654634 | B1 Offices and Workshop businesses | 1896 | B | Natural Gas | 3 |  | Air Conditioning | 2021-11-10 |  | 1 | FALSE | 51.1355 | 0.868 | SPN-S000000008302 | 11814323000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1383 | 33.5 | UNIT A1, BEAVER BUSINESS PARK | ASHFORD | TN23 7SH | Ashford |  | Workshop And Premises | industrial | 1 | 1800 | 19375 | GIA | 140000 | ASHFORD CENTRAL | inside-area | 1.09 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 96 | 2.86 | 81 | 36 | 948863 | SPN-S000000361020 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1355 | 0.868 | SPN-S000000008302 | 3940015000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1384 | 33.5 | UNIT D, BEAVER BUSINESS PARK | ASHFORD | TN23 7SH | Ashford |  | Factory And Premises | industrial | 1 | 1639.05 | 17643 | GIA | 119000 | ASHFORD CENTRAL | inside-area | 1.09 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.6 | 98 | 36 | 950595 | SPN-S000000361020 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1355 | 0.868 | SPN-S000000008302 | 11049966000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1385 | 33.5 | MANOR FARM, HORNASH LANE | ASHFORD | TN26 1NL | Ashford | SIMON BEAUGIE PICTURE FRAMES LTD | Workshop And Premises | industrial | 1 | 1629 | 17534 | GIA | 100000 | ASHFORD CENTRAL | inside-area | 5.33 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.59 | 73 | 36 | 950704 | SPN-S000000363416 | 200 | 60 | 20-40% | ASHFORD CENTRAL | 139 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0995 | 0.84601 | SPN-S000000008302 | 8623847000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1386 | 33.5 | UNITS 2A & 2B, OLD RAILWAY WORKS, NEWTOWN ROAD | ASHFORD | TN24 0PN | Ashford |  | Workshop And Premises | industrial | 1 | 1607.4 | 17302 | GIA | 13750 | ASHFORD CENTRAL | inside-area | 1.01 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.55 | 72 | 36 | 950936 | SPN-S000000371059 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 134 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1398 | 0.87963 | SPN-S000000008302 | 188330000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1387 | 33.5 | RHS UNIT 2, WOTTON TRADING ESTATE, WOTTON ROAD | ASHFORD | TN23 6LL | Ashford |  | Workshop And Premises | industrial | 1 | 1496.3 | 16106 | GIA | 93500 | ASHFORD CENTRAL | inside-area | 1.48 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.38 | 67 | 36 | 952132 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062559576 | General Industrial and Special Industrial Groups | 975 | E | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2023-08-23 |  | 1 | FALSE | 51.1321 | 0.86713 | SPN-S000000008302 | 464644000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1388 | 33.5 | ANGLO HOUSE, WOTTON ROAD | ASHFORD | TN23 6LN | Ashford |  | Factory And Premises | industrial | 1 | 1364.81 | 14691 | GIA | 92500 | ASHFORD CENTRAL | inside-area | 1.45 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.17 | 82 | 36 | 953547 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062618333 | B2 to B7 General Industrial and Special Industrial Groups | 663 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-06-14 |  | 0.5 | FALSE | 51.1323 | 0.86737 | SPN-S000000008302 | 56041000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1389 | 33.5 | BRUNDRETT HOUSE, TANNERY LANE | ASHFORD | TN23 1PN | Ashford |  | Warehouse And Premises | industrial | 1 | 1322.6 | 14236 | GIA | 102000 | ASHFORD CENTRAL | inside-area | 0.62 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.1 | 33 | 36 | 954002 | SPN-S000000361974 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 92 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004391969 | B8 Storage or Distribution | 658 | G | Other | 3 |  | Unconditioned | 2017-12-17 |  | 0.5 | FALSE | 51.1462 | 0.87687 | SPN-S000000008302 | 11254745000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1390 | 33.5 | 22, BEAVER ROAD | ASHFORD | TN23 7RP | Ashford |  | Warehouse And Premises | industrial | 1 | 1252.12 | 13478 | GIA | 140000 | ASHFORD CENTRAL | inside-area | 0.49 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.99 | 31 | 36 | 954760 | SPN-S000000361016 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1415 | 0.87166 | SPN-S000000008302 | 3970150000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1391 | 33.5 | BRADLEYS, WOTTON ROAD | ASHFORD | TN23 6LL | Ashford |  | Warehouse And Premises | industrial | 1 | 1248.73 | 13441 | GIA | 111000 | ASHFORD CENTRAL | inside-area | 1.48 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.98 | 31 | 36 | 954797 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 52 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | B1 Offices and Workshop businesses | 163 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-07-30 |  | 1 | FALSE | 51.1321 | 0.86713 | SPN-S000000008302 | 2356272000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1392 | 33.5 | POUND LANE | ASHFORD | TN23 3JE | Ashford | ASHFORD PACKAGING EQUIPMENT LTD | Workshop And Premises | industrial | 1 | 1222.2 | 13156 | GIA | 84500 | ASHFORD CENTRAL | inside-area | 2.64 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.94 | 55 | 36 | 955082 | SPN-S000000371152 | 500 | 350 | 60-80% | ASHFORD CENTRAL | 158 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100060796164 | B8 Storage or Distribution | 393 | F | Natural Gas | 3 |  | Heating and Natural Ventilation | 2012-05-30 |  | 1 | FALSE | 51.1242 | 0.85105 | SPN-S000000008302 | 329531148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1393 | 33.5 | 119-122, COUNTY SQUARE, ELWICK ROAD | ASHFORD | TN23 1AE | Ashford |  | Store And Premises | industrial | 1 | 1170 | 12594 | GIA | 79500 | ASHFORD CENTRAL | inside-area | 0.29 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.86 | 29 | 36 | 955644 | SPN-S000000363760 | 1000 | 500 | 40-60% | ASHFORD CENTRAL | 27 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1478 | 0.86957 | SPN-S000000008302 | 14118129000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1394 | 33.5 | UNIT A, THE INVICTA PRESS, LOWER QUEENS ROAD | ASHFORD | TN24 8HH | Ashford |  | Warehouse And Premises | industrial | 1 | 1107.96 | 11926 | GIA | 78000 | ASHFORD CENTRAL | inside-area | 1.04 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.76 | 28 | 36 | 956312 | SPN-S000000361013 | 500 | 350 | 60-80% | ASHFORD CENTRAL | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004382553 | B2 to B7 General Industrial and Special Industrial Groups | 6753 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-08-26 |  | 1 | FALSE | 51.1521 | 0.87855 | SPN-S000000008302 | 12298487000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1395 | 33.5 | UNIT A7, BEAVER BUSINESS PARK | ASHFORD | TN23 7SH | Ashford |  | Warehouse And Premises | industrial | 1 | 1086 | 11690 | GIA | 70000 | ASHFORD CENTRAL | inside-area | 1.09 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.73 | 27 | 36 | 956548 | SPN-S000000361020 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012842483 | B8 Storage or Distribution | 1141 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2017-06-12 |  | 1 | FALSE | 51.1355 | 0.868 | SPN-S000000008302 | 8644823000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1396 | 33.5 | UNIT 3B, OLD RAILWAY WORKS, NEWTOWN ROAD | ASHFORD | TN24 0PN | Ashford |  | Warehouse And Premises | industrial | 1 | 1063.9 | 11452 | GIA | 14500 | ASHFORD CENTRAL | inside-area | 1.01 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.69 | 27 | 36 | 956786 | SPN-S000000371059 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 134 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1398 | 0.87963 | SPN-S000000008302 | 329242148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1397 | 33.5 | UNITS 12 & 13, MACE LANE INDUSTRIAL ESTATE, MACE LANE | ASHFORD | TN24 8PE | Ashford |  | Warehouse And Premises | industrial | 1 | 1038.49 | 11178 | GIA | 92000 | ASHFORD CENTRAL | inside-area | 0.97 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.65 | 26 | 36 | 957060 | SPN-S000000361013 | 500 | 350 | 60-80% | ASHFORD CENTRAL | 140 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560925 | B1 Offices and Workshop businesses | 832 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-02-18 |  | 1 | FALSE | 51.1507 | 0.87908 | SPN-S000000008302 | 15073924000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1398 | 33.5 | UNITS 6A-6B, OLD RAILWAY WORKS, NEWTOWN ROAD | ASHFORD | TN24 0PN | Ashford |  | Warehouse And Premises | industrial | 1 | 1033.9 | 11129 | GIA | 14250 | ASHFORD CENTRAL | inside-area | 1.01 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.64 | 26 | 36 | 957109 | SPN-S000000371059 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 134 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1398 | 0.87963 | SPN-S000000008302 | 410641000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1399 | 33.5 | 73-74, ELLINGHAM WAY | ASHFORD | TN23 6JZ | Ashford |  | Workshop And Premises | industrial | 1 | 1032.28 | 11111 | GIA | 98500 | ASHFORD CENTRAL | inside-area | 2 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.64 | 46 | 36 | 957127 | SPN-S000000364140 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004396351 | Offices and Workshop Businesses | 1037 | G | Oil | 3 |  | Heating and Natural Ventilation | 2026-01-30 |  | 1 | FALSE | 51.1276 | 0.86318 | SPN-S000000008302 | 531501145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1400 | 33.5 | UNIT A -C AUSTIN HOUSE, WOTTON ROAD | ASHFORD | TN23 6LN | Ashford |  | Workshop And Premises | industrial | 1 | 1023.58 | 11018 | GIA | 81000 | ASHFORD CENTRAL | inside-area | 1.45 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.63 | 46 | 36 | 957220 | SPN-S000000362064 | 1000 | 700 | 60-80% | ASHFORD CENTRAL | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1323 | 0.86737 | SPN-S000000008302 | 4459909000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1401 | 33.5 | UNIT C, BEAVER BUSINESS PARK | ASHFORD | TN23 7SH | Ashford |  | Warehouse And Premises | industrial | 1 | 1023.17 | 11013 | GIA | 69000 | ASHFORD CENTRAL | inside-area | 1.09 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.63 | 26 | 36 | 957225 | SPN-S000000361020 | 800 | 560 | 60-80% | ASHFORD CENTRAL | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1355 | 0.868 | SPN-S000000008302 | 11049964000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1402 | 33.3 | KENT COUNTY COUNCIL, ST MICHAELS CLOSE | AYLESFORD | ME20 7BU | Maidstone |  | Offices And Premises | office | 1 | 1439.74 | 15497 | NIA | 173000 | AYLESFORD 33/6.6KV | inside-area | 2.22 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 2.29 | 101 | 85 | 5050197 | SPN-S000000393324 | 1000 | 500 | 40-60% | AYLESFORD 33/6.6KV | 86 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10022895514 | B1 Offices and Workshop businesses | 1138 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-01-07 |  | 0.5 | FALSE | 51.3045 | 0.49864 | SPN-S000000008312 | 15116266000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1403 | 33.3 | EAST MALLING LIMITED, EAST MALLING RESEARCH STATION, NEW ROAD | WEST MALLING | ME19 6BH | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1223.28 | 13167 | NIA | 153000 | AYLESFORD 33/6.6KV | inside-area | 2.02 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.94 | 86 | 85 | 5052527 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2852 | 0.45203 | SPN-S000000008312 | 10410884000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1404 | 33.3 | PT1 GND EDEN HOUSE 454, NEW HYTHE LANE | AYLESFORD | ME20 7UH | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1132.08 | 12186 | NIA | 189000 | AYLESFORD 33/6.6KV | inside-area | 1.64 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 100 | 1.8 | 79 | 85 | 5053508 | SPN-S000000392198 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094697420 | B1 Offices and Workshop businesses | 1172 | B | Natural Gas | 3 | 3 | Air Conditioning | 2017-05-03 |  | 0.6 | FALSE | 51.3121 | 0.45244 | SPN-S000000008312 | 13145149000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1405 | 33.3 | DHL EXEL SUPPLY CHAIN LTD, LAVERSTOKE ROAD, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LE | Maidstone |  | Warehouse And Premises | industrial | 1 | 25001.5 | 269114 | GIA | 2070000 | WATERSIDE 33/11KV | inside-area | 2.5 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 7 | 39.73 | 625 | 44 | 1457512 | SPN-S000000394082 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 202 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014313441 | Storage or Distribution | 23534 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-07-14 |  | 1 | FALSE | 51.2926 | 0.49329 | SPN-S000000008529 | 8128654000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1406 | 33.3 | A GOMEZ LTD, COLDHARBOUR LANE | CANTERBURY | CT4 5HL | Canterbury |  | Warehouse And Premises | industrial | 1 | 21358.69 | 229903 | GIA | 1120000 | WINGHAM 33/11KV | inside-area | 5.18 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 8 | 33.94 | 534 | 18 | 604970 | SPN-S000000343459 | 315 | 158 | 40-60% | WINGHAM 33/11KV | 315 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000680708 | Offices and Workshop Businesses | 22071 | C | Natural Gas | 3 |  | Air Conditioning | 2024-02-15 |  | 1 | FALSE | 51.2393 | 1.1424 | SPN-S000000008517 | 2674047000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1407 | 33.3 | UNIT 20, WARES FARM, REDWALL LANE | MAIDSTONE | ME17 4BA | Maidstone |  | Warehouse And Premises | industrial | 1 | 19306.45 | 207813 | GIA | 2060000 | SHEPWAY 33/11KV | inside-area | 5.78 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 9 | 30.68 | 483 | 47 | 1291456 | SPN-S000000394421 | 500 | 150 | 20-40% | SHEPWAY 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095448842 | B2 to B7 General Industrial and Special Industrial Groups | 10156 | D | Grid Supplied Electricity | 3 |  | Air Conditioning | 2014-03-10 |  | 0.75 | FALSE | 51.2122 | 0.49646 | SPN-S000000008644 | 12437599000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1408 | 33.3 | EDDINGTON LANE | HERNE BAY | CT6 5TR | Canterbury | CROWN PRODUCTS LTD | Factory And Premises | industrial | 1 | 17548.3 | 188888 | GIA | 705000 | HERNE BAY 33/11KV | inside-area | 2.13 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 9 | 27.89 | 1053 | 16 | 588939 | SPN-S000000341445 | 500 | 350 | 60-80% | HERNE BAY 33/11KV | 279 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3631 | 1.1223 | SPN-S000000008417 | 380618000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1409 | 33.3 | UNITS 5-10 SPARROW WAY LAKESVIEW BUSINESS PARK, ISLAND ROAD | CANTERBURY | CT3 4JH | Canterbury |  | Warehouse And Premises | industrial | 1 | 15345.31 | 165175 | GIA | 457500 | CANTERBURY LOCAL 33/11KV | inside-area | 6.85 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 11 | 24.39 | 384 | 28 | 1066950 | SPN-S000000343478 | 1000 | 700 | 60-80% | CANTERBURY LOCAL 33/11KV | 48 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10097061042 | B2 to B7 General Industrial and Special Industrial Groups | 14067 | C | Other | 3 |  | Unconditioned | 2022-03-08 |  | 0.8 | FALSE | 51.3177 | 1.1762 | SPN-S000000008597 | 15013954000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1410 | 33.3 | SESSIONS HOUSE, COUNTY ROAD | MAIDSTONE | ME14 1UZ | Maidstone |  | Offices And Premises | office | 1 | 12957 | 139468 | NIA | 740000 | MAIDSTONE GRID SOUTH | inside-area | 0.71 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 13 | 20.59 | 907 | 19 | 669316 | SPN-S000000392024 | 500 | 50 | 0-20% | WATERSIDE 33/11KV | 113 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2783 | 0.52479 | SPN-S000000009533 | 445846000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1411 | 33.3 | MILITARY ROAD | CANTERBURY | CT1 1YW | Canterbury | CANTERBURY CITY COUNCIL | Offices And Premises | office | 1 | 6947.6 | 74783 | NIA | 570000 | CANTERBURY TOWN 33/11KV | inside-area | 0.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 24 | 11.04 | 486 | 27 | 983993 | SPN-S000000342757 | 500 | 350 | 60-80% | CANTERBURY TOWN 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618849 | B1 Offices and Workshop businesses | 7879 | D | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2013-04-29 |  | 1 | FALSE | 51.2836 | 1.0932 | SPN-S000000008410 | 155287145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1412 | 33.3 | MOBIL DATA SERVICES COMPUTER CENTRE, LODGE ROAD | MAIDSTONE | ME14 5EH | Maidstone |  | Computer Centre And Premises | office | 1 | 6584.7 | 70877 | NIA | 1310000 | WATERSIDE 33/11KV | inside-area | 1.95 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 25 | 10.46 | 461 | 44 | 1655749 | SPN-S000000393430 | 800 | 560 | 60-80% | MAIDSTONE GRID SOUTH | 380 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2788 | 0.547 | SPN-S000000008529 | 198597148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1413 | 33.3 | INVICTA HOUSE, SESSIONS HOUSE SQUARE | MAIDSTONE | ME14 1XX | Maidstone |  | Offices And Premises | office | 1 | 6315.62 | 67981 | NIA | 1160000 | WATERSIDE 33/11KV | inside-area | 0.25 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 26 | 10.04 | 442 | 44 | 1658645 | SPN-S000000394007 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 98 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003729382 | Offices and Workshop Businesses | 8203 | D | Natural Gas | 4 |  | Air Conditioning | 2026-01-26 |  | 1 | FALSE | 51.2788 | 0.52121 | SPN-S000000008529 | 717305000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1414 | 33.3 | NUTWOOD HOUSE, CHAUCER ROAD | CANTERBURY | CT1 1ZZ | Canterbury |  | Offices And Premises | office | 1 | 2673.3 | 28775 | NIA | 430000 | CANTERBURY TOWN 33/11KV | inside-area | 0.64 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 62 | 4.25 | 187 | 27 | 1030001 | SPN-S000000341782 | 500 | 150 | 20-40% | CANTERBURY TOWN 33/11KV | 79 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062279415 | Offices and Workshop Businesses | 3246 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-06-26 |  | 1 | FALSE | 51.282 | 1.0932 | SPN-S000000008410 | 347035000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1415 | 33.3 | ROCHESTER HOUSE, ST GEORGES PLACE | CANTERBURY | CT1 1UT | Canterbury |  | Offices And Premises | office | 1 | 2610.5 | 28099 | NIA | 360000 | CANTERBURY TOWN 33/11KV | inside-area | 0.93 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 63 | 4.15 | 183 | 27 | 1030677 | SPN-S000000341793 | 750 | 375 | 40-60% | CANTERBURY TOWN 33/11KV | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2766 | 1.0858 | SPN-S000000008410 | 7130631000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1416 | 33.3 | BLOCK A & B AT BROOK HOUSE, REEVES WAY | WHITSTABLE | CT5 3SS | Canterbury |  | Offices And Premises | office | 1 | 2199.6 | 23676 | NIA | 292500 | WHITSTABLE 33/11KV | inside-area | 1.85 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 75 | 3.5 | 154 | 11 | 606475 | SPN-S000000343037 | 1000 | 100 | 0-20% | WHITSTABLE 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3566 | 1.0584 | SPN-S000000008516 | 4318649000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1417 | 33.3 | NIMBUS HOUSE, LIPHOOK WAY, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0FZ | Maidstone |  | Offices And Premises | office | 1 | 1947.86 | 20967 | NIA | 236000 | WATERSIDE 33/11KV | inside-area | 2.26 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 85 | 3.1 | 136 | 44 | 1705659 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2926 | 0.49821 | SPN-S000000008529 | 9487852000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1418 | 33.3 | GRIFFINS FARM, PLEASURE HOUSE LANE | MAIDSTONE | ME17 3NW | Maidstone |  | Warehouse And Premises | industrial | 1 | 1852.13 | 19936 | GIA | 146000 | SHEPWAY 33/11KV | inside-area | 5.44 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 89 | 2.94 | 46 | 47 | 1479333 | SPN-S000000394276 | 315 | 220 | 60-80% | SHEPWAY 33/11KV | 191 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2171 | 0.60474 | SPN-S000000008644 | 12138417000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1419 | 33.3 | UNIT A2 LOC8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 1848.83 | 19901 | GIA | 226000 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 90 | 2.94 | 46 | 19 | 788883 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451864 | General Industrial and Special Industrial Groups | 1875 | A+ | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-09-24 |  | 1 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14934394000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1420 | 33.3 | SCANIA MAIDSTONE BROOKLYN PARK, CHATHAM ROAD | MAIDSTONE | ME14 3AA | Maidstone |  | Workshop And Premises | industrial | 1 | 1782.51 | 19187 | GIA | 132000 | WATERSIDE 33/11KV | inside-area | 2.54 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 93 | 2.83 | 80 | 44 | 1707439 | SPN-S000000392415 | 315 | 220 | 60-80% | MAIDSTONE GRID SOUTH | 284 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014308296 | B1 Offices and Workshop businesses | 1767 | B | Natural Gas | 4 |  | Heating and Natural Ventilation | 2015-10-21 |  | 0.67 | FALSE | 51.2996 | 0.51309 | SPN-S000000008529 | 10118726000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1421 | 33.3 | UNIT E2, LOC8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 1770.06 | 19053 | GIA | 188000 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 94 | 2.81 | 44 | 19 | 789731 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451876 | B8 Storage or Distribution | 4100 | A+ | Grid Supplied Electricity | 5 |  | Air Conditioning | 2023-04-20 |  | 0.67 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14963327000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1422 | 33.3 | 217-223, SUTTON ROAD | MAIDSTONE | ME15 9BJ | Maidstone |  | Workshop And Premises | industrial | 1 | 1711.7 | 18425 | GIA | 77000 | SHEPWAY 33/11KV | inside-area | 0.59 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 97 | 2.72 | 77 | 47 | 1480844 | SPN-S000000392075 | 300 | 90 | 20-40% | SHEPWAY 33/11KV | 126 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003713817 | Storage or Distribution | 1792 | C | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2022-07-14 |  | 1 | FALSE | 51.2507 | 0.54165 | SPN-S000000008644 | 181469148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1423 | 33.3 | OBART HOUSE, LIPHOOK WAY, NIMBUS ENTERPRISE PARK, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0FZ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1630.3 | 17548 | GIA | 166000 | WATERSIDE 33/11KV | inside-area | 2.26 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 2.59 | 41 | 44 | 1709078 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014313427 | B1 Offices and Workshop businesses | 2287 | D | Natural Gas | 3 | 2 | Air Conditioning | 2018-05-30 |  | 1 | FALSE | 51.2926 | 0.49821 | SPN-S000000008529 | 6103348000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1424 | 33.3 | COLDRED ROAD | MAIDSTONE | ME15 9XN | Maidstone | EXPRESS DAIRY COMPANY LONDON LTD | Storage Depot And Premises | industrial | 1 | 1614.95 | 17383 | GIA | 107000 | SHEPWAY 33/11KV | inside-area | 1.8 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.57 | 40 | 47 | 1481886 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014313321 | B1 Offices and Workshop businesses | 119 | E | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-10-22 |  | 1 | FALSE | 51.2369 | 0.55967 | SPN-S000000008644 | 30188148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1425 | 33.3 | UNITS 4-8, UNION PARK, BIRCHOLT ROAD | MAIDSTONE | ME15 9XT | Maidstone |  | Warehouse, Store And Premises | industrial | 1 | 1588.3 | 17096 | GIA | 128000 | SHEPWAY 33/11KV | inside-area | 1.88 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.52 | 40 | 47 | 1482173 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 89 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003718471 | General Industrial and Special Industrial Groups | 1553 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-10-11 |  | 1 | FALSE | 51.2359 | 0.5586 | SPN-S000000008644 | 1398979000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1426 | 33.3 | BOLTS HILL | CANTERBURY | CT4 7JZ | Canterbury | INCA GEOMETRIC | Factory And Premises | industrial | 1 | 1558.5 | 16776 | NIA | 60000 | CHARTHAM 33/11KV | inside-area | 1.24 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 5.2 | Green | 15 | 9.4 | Thermal | 0 | 5.7 | 0 | 5.7 | 5.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 14.4 | 10.6 | Winter | 37.5 | 5.4 | Green (Over 5% headroom) | 17825 | 100 | 2.48 | 94 | 4 | 130703 | SPN-S000000341596 | 500 | 250 | 40-60% | CHARTHAM 33/11KV | 36 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2531 | 1.0067 | SPN-S000000008560 | 167679145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1427 | 33.3 | LENLEYS, MARSHWOOD INDUSTRIAL ESTATE, MARSHWOOD CLOSE | CANTERBURY | CT1 1DX | Canterbury | LENLEYS | Warehouse And Premises | industrial | 1 | 1550.09 | 16685 | GIA | 105000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.85 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 2.46 | 39 | 28 | 1215440 | SPN-S000000343062 | 500 | 350 | 60-80% | CANTERBURY LOCAL 33/11KV | 44 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2913 | 1.0996 | SPN-S000000008597 | 461628145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1428 | 33.3 | UNIT 2, PROSPECT RETAIL PARK, PROSPECT WAY | WHITSTABLE | CT5 3SD | Canterbury |  | Large Food Store And Premises | industrial | 1 | 1485 | 15984 | GIA | 217000 | WHITSTABLE 33/11KV | inside-area | 1.64 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 100 | 2.36 | 37 | 11 | 614167 | SPN-S000000343737 | 800 | 560 | 60-80% | WHITSTABLE 33/11KV | 39 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10093442304 | A1/A2 Retail and Financial/Professional services | 1451 | A | Natural Gas | 5 | 1 | Air Conditioning | 2019-02-07 |  | 1 | FALSE | 51.3411 | 1.0157 | SPN-S000000008516 | 10805938000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1429 | 33.3 | UNITS 70-76, JOHN WILSON BUSINESS PARK, THANET WAY | WHITSTABLE | CT5 3QT | Canterbury |  | Warehouse, Office And Premises | industrial | 1 | 1467.5 | 15796 | GIA | 115000 | WHITSTABLE 33/11KV | inside-area | 1.72 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 100 | 2.33 | 103 | 11 | 614355 | SPN-S000000343037 | 1000 | 100 | 0-20% | WHITSTABLE 33/11KV | 17 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3565 | 1.0565 | SPN-S000000008516 | 11008108000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1430 | 33.3 | SWEECHBRIDGE ROAD | HERNE BAY | CT6 6TE | Canterbury | TC MOTORHOMES | Showroom, Workshop And Premises | industrial | 1 | 1444.6 | 15550 | GIA | 72000 | HERNE BAY 33/11KV | inside-area | 5.51 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 100 | 2.3 | 65 | 16 | 762277 | SPN-S000000341380 | 500 | 350 | 60-80% | HERNE BAY 33/11KV | 122 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3659 | 1.1723 | SPN-S000000008417 | 8267411000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1431 | 33.3 | UNIT 1A AT, MONCHELSEA FARM, HEATH ROAD | MAIDSTONE | ME17 4JD | Maidstone |  | Workshop And Premises | industrial | 1 | 1439.36 | 15493 | GIA | 93500 | SHEPWAY 33/11KV | inside-area | 2.57 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.29 | 65 | 47 | 1483776 | SPN-S000000392185 | 300 | 150 | 40-60% | SHEPWAY 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2292 | 0.54356 | SPN-S000000008644 | 13345958000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1432 | 33.3 | MAIDSTONE BOROUGH COUNCIL DEPOT, BIRCHOLT ROAD | MAIDSTONE | ME15 9XY | Maidstone |  | Workshop And Premises | industrial | 1 | 1421.79 | 15304 | GIA | 155000 | SHEPWAY 33/11KV | inside-area | 1.78 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.26 | 64 | 47 | 1483965 | SPN-S000000392174 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014308408 | B1 Offices and Workshop businesses | 83 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2020-05-29 |  | 1 | FALSE | 51.2384 | 0.56367 | SPN-S000000008644 | 7128519000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1433 | 33.3 | AGRICARE, COOTING ROAD, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EP | Dover |  | Warehouse And Premises | industrial | 1 | 1390.4 | 14966 | GIA | 63500 | WINGHAM 33/11KV | inside-area | 3.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 2.21 | 35 | 18 | 819907 | SPN-S000000371222 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2226 | 1.1926 | SPN-S000000008517 | 8069968000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1434 | 33.3 | GOODY DEMOLITION YARD & WORKSHOP, WILCOX CLOSE, AYLESHAM INDUSTRIAL ESTATE | CANTERBURY | CT3 3EP | Dover |  | Workshop And Premises | industrial | 1 | 1383.57 | 14893 | GIA | 143000 | WINGHAM 33/11KV | inside-area | 3.57 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 2.2 | 62 | 18 | 819980 | SPN-S000000371222 | 800 | 560 | 60-80% | WINGHAM 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10034873887 | B8 Storage or Distribution | 2990 | C | LPG | 3 |  | Heating and Natural Ventilation | 2012-06-27 |  | 0.67 | FALSE | 51.2226 | 1.1926 | SPN-S000000008517 | 14778903000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1435 | 33.3 | HYDRAQUIP HOSE & HYDRAULICS, STATION APPROACH | CANTERBURY | CT3 3JF | Canterbury |  | Warehouse And Premises | industrial | 1 | 1363.99 | 14682 | GIA | 57500 | WINGHAM 33/11KV | inside-area | 1.63 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 2.17 | 34 | 18 | 820191 | SPN-S000000371350 | 100 | 50 | 40-60% | WINGHAM 33/11KV | 95 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2437 | 1.1946 | SPN-S000000008517 | 9433236000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1436 | 33.3 | UNIT 1, TOVIL GREEN | MAIDSTONE | ME15 6RJ | Maidstone |  | Workshop And Premises | industrial | 1 | 1340 | 14424 | GIA | 70500 | BARMING 33/11KV | inside-area | 1.45 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 4.1 | Green | 22.8 | 18.7 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 21 | 15.9 | Winter | 18.0952 | 3.8 | Green (Over 5% headroom) | 17825 | 100 | 2.13 | 60 | 3 | 158027 | SPN-S000000394996 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 29 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003734930 | B1 Offices and Workshop businesses | 519 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2015-09-23 |  | 0.67 | FALSE | 51.2628 | 0.50843 | SPN-S000000008527 | 183310148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1437 | 33.3 | BEE EQUIPMENT LIMITED, HIGHLAND COURT FARM | CANTERBURY | CT4 5HW | Canterbury |  | Warehouse And Premises | industrial | 1 | 1339.17 | 14415 | GIA | 38250 | WINGHAM 33/11KV | inside-area | 4.82 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 2.13 | 33 | 18 | 820458 | SPN-S000000343459 | 315 | 158 | 40-60% | WINGHAM 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2394 | 1.1478 | SPN-S000000008517 | 11268230000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1438 | 33.3 | 1, SPECTRUM BUSINESS ESTATE, BIRCHOLT ROAD | MAIDSTONE | ME15 9YP | Maidstone |  | Factory And Premises | industrial | 1 | 1328.5 | 14300 | GIA | 109000 | SHEPWAY 33/11KV | inside-area | 1.66 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.11 | 80 | 47 | 1484969 | SPN-S000000393712 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003680400 | B1 Offices and Workshop businesses | 1344 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2017-07-21 |  | 1 | FALSE | 51.2385 | 0.56038 | SPN-S000000008644 | 192078148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1439 | 33.3 | 108, HOCKERS LANE | MAIDSTONE | ME14 3JJ | Maidstone |  | Store And Premises | industrial | 1 | 1315.15 | 14156 | GIA | 27500 | MAIDSTONE GRID SOUTH | inside-area | 2.44 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 100 | 2.09 | 33 | 19 | 794628 | SPN-S000000392230 | 500 | 250 | 40-60% | MAIDSTONE NORTH 132/11KV | 57 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2856 | 0.56319 | SPN-S000000009533 | 187070148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1440 | 33.3 | G1A AND G7, POWERHUB BUSINESS CENTRE, ST PETERS STREET | MAIDSTONE | ME16 0ST | Maidstone |  | Warehouse And Premises | industrial | 1 | 1311.5 | 14117 | GIA | 89000 | WATERSIDE 33/11KV | inside-area | 0.2 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 2.08 | 33 | 44 | 1712509 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 112 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.277 | 0.51619 | SPN-S000000008529 | 12140283000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1441 | 33.3 | STEER MAIDSTONE 21, BIRCHOLT ROAD | MAIDSTONE | ME15 9XY | Maidstone |  | Factory And Premises | industrial | 1 | 1309 | 14090 | GIA | 104000 | SHEPWAY 33/11KV | inside-area | 1.78 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.08 | 79 | 47 | 1485179 | SPN-S000000392174 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 162 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014307642 | B1 Offices and Workshop businesses | 1414 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-10-27 |  | 1 | FALSE | 51.2384 | 0.56367 | SPN-S000000008644 | 14998262000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1442 | 33.3 | COLD STORE, LESTED FARM, PLOUGH WENTS ROAD | MAIDSTONE | ME17 3SA | Maidstone |  | Cold Store And Premises | industrial | 1 | 1300 | 13993 | GIA | 123000 | SHEPWAY 33/11KV | inside-area | 3.2 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.07 | 156 | 47 | 1485276 | SPN-S000000394578 | 100 | 10 | 0-20% | SHEPWAY 33/11KV | 24 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2257 | 0.56878 | SPN-S000000008644 | 13907143000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1443 | 33.3 | MAYNARD ROAD | CANTERBURY | CT1 3RH | Canterbury | C BREWER & SONS | Warehouse And Premises | industrial | 1 | 1292.76 | 13915 | GIA | 95500 | CANTERBURY TOWN 33/11KV | inside-area | 1.81 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 100 | 2.05 | 32 | 27 | 1044861 | SPN-S000000342189 | 1000 | 500 | 40-60% | CANTERBURY TOWN 33/11KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618843 | A1/A2 Retail and Financial/Professional services | 1061 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-07-01 |  | 1 | FALSE | 51.273 | 1.0675 | SPN-S000000008410 | 512634145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1444 | 33.3 | GATEWAY HOUSE, WALLIS AVENUE | MAIDSTONE | ME15 9NE | Maidstone |  | Factory And Premises | industrial | 1 | 1292.36 | 13911 | GIA | 78000 | SHEPWAY 33/11KV | inside-area | 1.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.05 | 78 | 47 | 1485358 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2421 | 0.56002 | SPN-S000000008644 | 6865340000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1445 | 33.3 | UNITS H3 & H4 & H5 INTEGRA, BIRCHOLT ROAD | MAIDSTONE | ME15 9GQ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1290.37 | 13889 | GIA | 104000 | SHEPWAY 33/11KV | inside-area | 1.98 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.05 | 32 | 47 | 1485380 | SPN-S000000394969 | 1000 | 900 | 80-100% | SHEPWAY 33/11KV | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.236 | 0.56281 | SPN-S000000008644 | 14480814000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1446 | 33.3 | 89, LOWER HERNE ROAD | HERNE BAY | CT6 7ND | Canterbury |  | Factory And Premises | industrial | 1 | 1268.59 | 13655 | GIA | 50500 | CANTERBURY LOCAL 33/11KV | inside-area | 7.51 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 2.02 | 76 | 28 | 1218470 | SPN-S000000341373 | 315 | 158 | 40-60% | CANTERBURY LOCAL 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062303176 | Offices and Workshop Businesses | 1176 | F | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-10-06 |  | 1 | FALSE | 51.3531 | 1.1297 | SPN-S000000008597 | 13571206000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1447 | 33.3 | 87-97, UPPER STONE STREET | MAIDSTONE | ME15 6HE | Maidstone |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1268.5 | 13654 | GIA | 76000 | WATERSIDE 33/11KV | inside-area | 1.08 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 2.02 | 57 | 44 | 1712972 | SPN-S000000392025 | 500 | 350 | 60-80% | MAIDSTONE NORTH 132/11KV | 116 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003693422 | B1 Offices and Workshop businesses | 1343 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-04-26 |  | 1 | FALSE | 51.2685 | 0.52659 | SPN-S000000008529 | 51541148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1448 | 33.3 | ARKAS LTD, HEADCORN ROAD | MAIDSTONE | ME17 3EH | Maidstone |  | Workshop And Premises | industrial | 1 | 1250.93 | 13465 | GIA | 81500 | SHEPWAY 33/11KV | inside-area | 6.5 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.99 | 56 | 47 | 1485804 | SPN-S000000392690 | 200 | 20 | 0-20% | SHEPWAY 33/11KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003695644 | B1 Offices and Workshop businesses | 1047 | D | Oil | 3 |  | Heating and Natural Ventilation | 2014-01-13 |  | 1 | FALSE | 51.2005 | 0.59426 | SPN-S000000008644 | 11955340000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1449 | 33.3 | 1B, CANTERBURY INDUSTRIAL PARK, ISLAND ROAD | CANTERBURY | CT3 4HQ | Canterbury |  | Warehouse And Premises | industrial | 1 | 1247.4 | 13427 | GIA | 66000 | CANTERBURY LOCAL 33/11KV | inside-area | 6.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 1.98 | 31 | 28 | 1218698 | SPN-S000000342849 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033167024 | General Industrial and Special Industrial Groups | 1265 | B | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2023-05-01 |  | 1 | FALSE | 51.3138 | 1.1709 | SPN-S000000008597 | 291302145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1450 | 33.3 | 2A, CANTERBURY INDUSTRIAL PARK, ISLAND ROAD | CANTERBURY | CT3 4HQ | Canterbury |  | Workshop And Premises | industrial | 1 | 1237.38 | 13319 | GIA | 71500 | CANTERBURY LOCAL 33/11KV | inside-area | 6.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 1.97 | 56 | 28 | 1218806 | SPN-S000000342849 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10093444418 | B2 to B7 General Industrial and Special Industrial Groups | 1253 | C | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2020-11-22 |  | 1 | FALSE | 51.3138 | 1.1709 | SPN-S000000008597 | 10200576000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1451 | 33.3 | 2B-2C, CANTERBURY INDUSTRIAL PARK, ISLAND ROAD | CANTERBURY | CT3 4HQ | Canterbury |  | Warehouse And Premises | industrial | 1 | 1223.69 | 13172 | GIA | 64500 | CANTERBURY LOCAL 33/11KV | inside-area | 6.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 1.94 | 31 | 28 | 1218953 | SPN-S000000342849 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618772 | Storage or Distribution | 1439 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-08-10 |  | 1 | FALSE | 51.3138 | 1.1709 | SPN-S000000008597 | 10319804000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1452 | 33.3 | CAVALLINO BUILDING, BOXMEND INDUSTRIAL ESTATE, BIRCHOLT ROAD | MAIDSTONE | ME15 9YG | Maidstone |  | Warehouse And Premises | industrial | 1 | 1217.5 | 13105 | GIA | 103000 | SHEPWAY 33/11KV | inside-area | 2.1 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.93 | 30 | 47 | 1486164 | SPN-S000000394969 | 1000 | 900 | 80-100% | SHEPWAY 33/11KV | 126 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022893888 | Offices and Workshop Businesses | 1465 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2024-02-21 |  | 1 | FALSE | 51.2345 | 0.5615 | SPN-S000000008644 | 7496663000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1453 | 33.3 | UNITS G10 G11 G11A G12 & G12A POWERHUB BUSINESS CENTRE, ST PETERS STREET | MAIDSTONE | ME16 0ST | Maidstone |  | Warehouse And Premises | industrial | 1 | 1214.9 | 13077 | GIA | 90000 | WATERSIDE 33/11KV | inside-area | 0.2 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.93 | 30 | 44 | 1713549 | SPN-S000000394755 | 800 | 400 | 40-60% | WATERSIDE 33/11KV | 112 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10093304359 | D2 General Assembly and Leisure plus Night Clubs and Theatres | 1113 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-06-22 |  | 1 | FALSE | 51.277 | 0.51619 | SPN-S000000008529 | 12232885000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1454 | 33.3 | CHILLINGTON STREET | MAIDSTONE | ME14 2RT | Maidstone | HALL & COMPANY LTD | Warehouse And Premises | industrial | 1 | 1211.4 | 13039 | GIA | 88000 | MAIDSTONE GRID SOUTH | inside-area | 1.26 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 100 | 1.92 | 30 | 19 | 795745 | SPN-S000000394487 | 500 | 250 | 40-60% | MAIDSTONE GRID SOUTH | 75 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2836 | 0.52244 | SPN-S000000009533 | 198545148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1455 | 33.3 | UNIT 3, CUXTON ROAD | MAIDSTONE | ME15 9NG | Maidstone |  | Warehouse And Premises | industrial | 1 | 1211.29 | 13038 | GIA | 89500 | SHEPWAY 33/11KV | inside-area | 1.43 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.92 | 30 | 47 | 1486231 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2413 | 0.56146 | SPN-S000000008644 | 4577712000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1456 | 33.3 | 1A, CANTERBURY INDUSTRIAL PARK, ISLAND ROAD | CANTERBURY | CT3 4HQ | Canterbury |  | Warehouse And Premises | industrial | 1 | 1205.3 | 12974 | GIA | 63500 | CANTERBURY LOCAL 33/11KV | inside-area | 6.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 1.92 | 30 | 28 | 1219151 | SPN-S000000342849 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 53 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618769 | Storage or Distribution | 1363 | B | Grid Supplied Electricity | 3 | 1 | Heating and Natural Ventilation | 2023-05-01 |  | 1 | FALSE | 51.3138 | 1.1709 | SPN-S000000008597 | 291301145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1457 | 33.3 | THE ACTIVE COLLETCION BUREAU LTD SOCORRO HOUSE, LIPHOOK WAY, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LQ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1202 | 12938 | GIA | 143000 | WATERSIDE 33/11KV | inside-area | 2.39 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.91 | 30 | 44 | 1713688 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 183 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003734175 | Offices and Workshop Businesses | 1654 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-07-05 |  | 0.5 | FALSE | 51.2942 | 0.49854 | SPN-S000000008529 | 8263649000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1458 | 33.3 | UNIT 1C, JOSEPH WILSON INDUSTRIAL ESTATE, MILLSTROOD ROAD | WHITSTABLE | CT5 3PS | Canterbury |  | Workshop And Premises | industrial | 1 | 1197.5 | 12890 | GIA | 87500 | WHITSTABLE 33/11KV | inside-area | 0.95 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 11.8 | Green | 32.9 | 18.4 | Thermal | 8 | 1 | 0 | 9 | 13.2 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | Green (Over 5% headroom) | 17825 | 100 | 1.9 | 54 | 11 | 617261 | SPN-S000000342959 | 800 | 240 | 20-40% | WHITSTABLE 33/11KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033172763 | Offices and Workshop Businesses | 1322 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2025-01-06 |  | 1 | FALSE | 51.3457 | 1.0443 | SPN-S000000008516 | 5637072000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1459 | 33.3 | PRESSMETAL HOUSE, ST AUGUSTINES BUSINESS PARK, ESTUARY CLOSE | WHITSTABLE | CT5 2QJ | Canterbury | ALL METAL PRESSINGS | Workshop And Premises | industrial | 1 | 1194.41 | 12857 | GIA | 72000 | HERNE BAY 33/11KV | inside-area | 1.43 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 100 | 1.9 | 54 | 16 | 764970 | SPN-S000000343236 | 1000 | 700 | 60-80% | WHITSTABLE 33/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.3621 | 1.0792 | SPN-S000000008417 | 5605129000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1460 | 33.3 | PT GND 1ST 2ND & 3RD FLRS 11, WEEK STREET | MAIDSTONE | ME14 1QW | Maidstone |  | Store And Premises | industrial | 1 | 1193.45 | 12846 | GIA | 21250 | WATERSIDE 33/11KV | inside-area | 0.4 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.9 | 30 | 44 | 1713780 | SPN-S000000394141 | 800 | 560 | 60-80% | FAIRMEADOW 11KV | 65 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014313478 | Retail/Financial and Professional Services | 495 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-09-24 |  | 0.67 | FALSE | 51.2743 | 0.52277 | SPN-S000000008529 | 6666270000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1461 | 33.3 | UNITS 2-3, CUXTON ROAD | MAIDSTONE | ME15 9NE | Maidstone |  | Factory And Premises | industrial | 1 | 1192.43 | 12835 | GIA | 71000 | SHEPWAY 33/11KV | inside-area | 1.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.89 | 72 | 47 | 1486434 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2421 | 0.56002 | SPN-S000000008644 | 6822880000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1462 | 33.3 | R/O BIG BOX CO, BIRCHOLT ROAD | MAIDSTONE | ME15 9NE | Maidstone |  | Warehouse And Premises | industrial | 1 | 1179.04 | 12691 | GIA | 95500 | SHEPWAY 33/11KV | inside-area | 1.3 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.87 | 29 | 47 | 1486578 | SPN-S000000393847 | 800 | 560 | 60-80% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2421 | 0.56002 | SPN-S000000008644 | 3250724000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1463 | 33.3 | UNIT 4 AT BECKET BUSINESS PARK, BROAD OAK ROAD | CANTERBURY | CT2 0PQ | Canterbury |  | Vehicle Repair Workshop, Offices And Premises | industrial | 1 | 1177.3 | 12672 | GIA | 68500 | CANTERBURY LOCAL 33/11KV | inside-area | 1.28 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 1.87 | 53 | 28 | 1219453 | SPN-R000000859706-000-019Z | 50 | 15 | 20-40% | CANTERBURY LOCAL 33/11KV | 203 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 |  | Offices and Workshop Businesses | 1721 | B | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2025-05-29 |  | 1 | FALSE | 51.2975 | 1.1026 | SPN-S000000008597 | 8163924000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1464 | 33.3 | UNIT 1A AT WOOLTON FARM, BEKESBOURNE LANE | CANTERBURY | CT4 5EA | Canterbury |  | Warehouse And Premises | industrial | 1 | 1174.39 | 12641 | GIA | 46750 | WINGHAM 33/11KV | inside-area | 5.5 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 1.87 | 29 | 18 | 822232 | [9 empty] | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033160333 | B8 Storage or Distribution | 1236 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2013-04-08 |  | 1 | FALSE | 51.2685 | 1.1397 | SPN-S000000008517 | 9572376000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1465 | 33.3 | 2B, SPECTRUM BUSINESS ESTATE, BIRCHOLT ROAD | MAIDSTONE | ME15 9YP | Maidstone |  | Factory And Premises | industrial | 1 | 1155.3 | 12436 | GIA | 107000 | SHEPWAY 33/11KV | inside-area | 1.66 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.84 | 69 | 47 | 1486833 | SPN-S000000393712 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 170 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003680400 | B1 Offices and Workshop businesses | 1344 | D | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2017-07-21 |  | 0.67 | FALSE | 51.2385 | 0.56038 | SPN-S000000008644 | 192082148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1466 | 33.3 | EAST KENT TIMBER, HOWFIELD LANE | CANTERBURY | CT4 7LZ | Canterbury |  | Warehouse And Premises | industrial | 1 | 1153.9 | 12420 | GIA | 49750 | CANTERBURY TOWN 33/11KV | inside-area | 5.01 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 100 | 1.83 | 29 | 27 | 1046356 | SPN-R000000841006-000-211Z | 200 | 60 | 20-40% | CANTERBURY TOWN 33/11KV | 212 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2697 | 1.0176 | SPN-S000000008410 | 931291000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1467 | 33.3 | UNIT A9 LOC 8 BUSINESS PARK, ASHFORD ROAD | MAIDSTONE | ME17 1WR | Maidstone |  | Warehouse And Premises | industrial | 1 | 1145 | 12325 | GIA | 143000 | MAIDSTONE GRID SOUTH | inside-area | 5.17 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 100 | 1.82 | 29 | 19 | 796459 | SPN-R000000953212-000-025Z | 200 | 180 | 80-100% | MAIDSTONE GRID SOUTH | 318 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095451875 | General Industrial and Special Industrial Groups | 2852 | A+ | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2024-09-24 |  | 0.75 | FALSE | 51.2662 | 0.60619 | SPN-S000000009533 | 14373729000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1468 | 33.3 | UNIT 5A, ALTIRA BUSINESS PARK, THE BOULEVARD, THANET WAY | HERNE BAY | CT6 6GZ | Canterbury |  | Workshop And Premises | industrial | 1 | 1126.41 | 12125 | GIA | 89000 | HERNE BAY 33/11KV | inside-area | 3.9 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 100 | 1.79 | 51 | 16 | 765702 | SPN-S000000343379 | 315 | 220 | 60-80% | HERNE BAY 33/11KV | 312 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10093441870 | B8 Storage or Distribution | 309 | A | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-07-03 |  | 0.67 | FALSE | 51.3619 | 1.15 | SPN-S000000008417 | 6942161000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1469 | 33.3 | UNIT 1 FOUNTAIN ENTERPRISE PARK, ENTERPRISE ROAD | MAIDSTONE | ME15 6ZQ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1121.1 | 12067 | GIA | 94000 | SHEPWAY 33/11KV | inside-area | 1.87 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.78 | 28 | 47 | 1487202 | SPN-S000000394145 | 500 | 150 | 20-40% | FAIRMEADOW 11KV | 42 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2594 | 0.52585 | SPN-S000000008644 | 11874447000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1470 | 33.3 | H L HUTCHINSON LTD, HIGHLAND COURT FARM, COLDHARBOUR LANE | CANTERBURY | CT4 5HW | Canterbury |  | Warehouse, Offices And Premises | industrial | 1 | 1119.27 | 12048 | GIA | 98500 | WINGHAM 33/11KV | inside-area | 4.82 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 1.78 | 78 | 18 | 822825 | SPN-S000000343459 | 315 | 158 | 40-60% | WINGHAM 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10096027444 | Offices and Workshop Businesses | 300 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-01-31 |  | 0.75 | FALSE | 51.2394 | 1.1478 | SPN-S000000008517 | 10094606000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1471 | 33.3 | MARINE HOUSE, TYLER WAY | WHITSTABLE | CT5 2RS | Canterbury | BARTON MARINE EQUIPMENT | Warehouse And Premises | industrial | 1 | 1117.73 | 12031 | GIA | 72500 | HERNE BAY 33/11KV | inside-area | 1.59 | Herne Bay Grid | Canterbury | East Kent Zone | 2.5 | gsp | 24.6 | Green | 46.8 | 17.6 | Thermal | 0 | 1.5 | 2.2 | 1.5 | 23.5 | Herne Bay Grid 33kV | 60.5 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | Green (Over 5% headroom) | 17825 | 100 | 1.78 | 28 | 16 | 765796 | SPN-S000000341433 | 500 | 250 | 40-60% | HERNE BAY 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10090314201 | General Industrial and Special Industrial Groups | 1352 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2023-07-14 |  | 1 | FALSE | 51.3623 | 1.0766 | SPN-S000000008417 | 8264722000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1472 | 33.3 | SEIKISUI DIAGNOSIS UK LTD, LIPHOOK WAY, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0LQ | Maidstone |  | Factory And Premises | industrial | 1 | 1116.59 | 12019 | GIA | 119000 | WATERSIDE 33/11KV | inside-area | 2.39 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.77 | 67 | 44 | 1714607 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 183 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003734175 | Offices and Workshop Businesses | 1654 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2022-07-05 |  | 0.5 | FALSE | 51.2942 | 0.49854 | SPN-S000000008529 | 9212212000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1473 | 33.3 | UNIT B, COLDHARBOUR LANE | CANTERBURY | CT4 5HL | Canterbury |  | Warehouse And Premises | industrial | 1 | 1115 | 12002 | GIA | 74500 | WINGHAM 33/11KV | inside-area | 5.18 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 1.77 | 28 | 18 | 822871 | SPN-S000000343459 | 315 | 158 | 40-60% | WINGHAM 33/11KV | 315 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2393 | 1.1424 | SPN-S000000008517 | 12161540000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1474 | 33.3 | BROAD OAK ROAD | CANTERBURY | CT2 7PX | Canterbury | MAGNET JOINERY SALES LTD | Warehouse And Premises | industrial | 1 | 1110 | 11948 | GIA | 90000 | CANTERBURY LOCAL 33/11KV | inside-area | 0.33 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 100 | 1.76 | 28 | 28 | 1220177 | SPN-S000000341794 | 800 | 400 | 40-60% | CANTERBURY LOCAL 33/11KV | 66 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062292608 | A1/A2 Retail and Financial/Professional services | 1081 | E | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2013-03-12 |  | 1 | FALSE | 51.2922 | 1.0918 | SPN-S000000008597 | 149144145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1475 | 33.3 | 10-11, HERONDEN ROAD | MAIDSTONE | ME15 9YR | Maidstone |  | Warehouse And Premises | industrial | 1 | 1090.2 | 11735 | GIA | 93000 | SHEPWAY 33/11KV | inside-area | 1.79 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.73 | 27 | 47 | 1487534 | SPN-S000000393882 | 800 | 240 | 20-40% | SHEPWAY 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003680178 | B2 to B7 General Industrial and Special Industrial Groups | 547 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2017-04-11 |  | 1 | FALSE | 51.2371 | 0.5599 | SPN-S000000008644 | 2511985000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1476 | 33.3 | UNITS 5 & 6, MAIDSTONE EXCHANGE, CUXTON ROAD | MAIDSTONE | ME15 9HF | Maidstone |  | Warehouse And Premises | industrial | 1 | 1069.2 | 11509 | GIA | 158000 | SHEPWAY 33/11KV | inside-area | 1.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.7 | 27 | 47 | 1487760 | SPN-S000000392174 | 1000 | 700 | 60-80% | SHEPWAY 33/11KV | 87 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10094441716 | B8 Storage or Distribution | 513 | B | Grid Supplied Electricity | 4 |  | Heating and Natural Ventilation | 2019-06-27 |  | 1 | FALSE | 51.2406 | 0.56315 | SPN-S000000008644 | 14714539000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1477 | 33.3 | ROYAL MAIL ROAD TRANSPORT WORKSHOP, ASHFORD ROAD | CANTERBURY | CT4 7HB | Canterbury |  | Workshop And Premises | industrial | 1 | 1028.49 | 11071 | GIA | 93000 | CHARTHAM 33/11KV | inside-area | 0.98 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 5.2 | Green | 15 | 9.4 | Thermal | 0 | 5.7 | 0 | 5.7 | 5.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 14.4 | 10.6 | Winter | 37.5 | 5.4 | Green (Over 5% headroom) | 17825 | 100 | 1.63 | 46 | 4 | 136408 | SPN-R000000856006-000-225Z | 200 | 180 | 80-100% | CHARTHAM 33/11KV | 110 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200000682170 | B1 Offices and Workshop businesses | 1112 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-07-26 |  | 1 | FALSE | 51.2626 | 1.0336 | SPN-S000000008560 | 317136000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1478 | 33.3 | 9 NIMBUS ENTERPRISE PARK, LIPHOOK WAY, 20/20 INDUSTRIAL ESTATE | MAIDSTONE | ME16 0FZ | Maidstone |  | Warehouse And Premises | industrial | 1 | 1026.42 | 11048 | GIA | 106000 | WATERSIDE 33/11KV | inside-area | 2.26 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.63 | 26 | 44 | 1715578 | SPN-S000000394087 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 37 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014313427 | B1 Offices and Workshop businesses | 2287 | D | Natural Gas | 3 | 2 | Air Conditioning | 2018-05-30 |  | 1 | FALSE | 51.2926 | 0.49821 | SPN-S000000008529 | 5737388000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1479 | 33.3 | 38, LOWER STONE STREET | MAIDSTONE | ME15 6LX | Maidstone |  | Workshop And Premises | industrial | 1 | 1024.22 | 11025 | GIA | 105000 | WATERSIDE 33/11KV | inside-area | 0.72 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.63 | 46 | 44 | 1715601 | SPN-S000000394161 | 1000 | 700 | 60-80% | MAIDSTONE NORTH 132/11KV | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003695160 | General Industrial and Special Industrial Groups | 1011 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2023-12-14 |  | 1 | FALSE | 51.2715 | 0.52468 | SPN-S000000008529 | 9919313000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1480 | 33.3 | UNIT 1B AT, MONCHELSEA FARM, HEATH ROAD | MAIDSTONE | ME17 4JD | Maidstone |  | Workshop And Premises | industrial | 1 | 1013.04 | 10904 | GIA | 64000 | SHEPWAY 33/11KV | inside-area | 2.57 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.61 | 46 | 47 | 1488365 | SPN-S000000392185 | 300 | 150 | 40-60% | SHEPWAY 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10095449550 | Storage or Distribution | 953 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2024-01-19 |  | 1 | FALSE | 51.2292 | 0.54356 | SPN-S000000008644 | 13345947000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1481 | 33.2 | BAYLEY WOOD | ASHFORD | TN26 1JJ | Ashford |  | Warehouse And Premises | industrial | 1 | 1495.7 | 16100 | GIA | 90000 | ASHFORD WEST 33/6.6KV | inside-area | 4.98 | Ashford Grid | Sellindge | East Kent Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.1 | Thermal | 0 | 0 | 0 | 0 | 2.4 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 6.3 | 4.8 | Winter | 36.5079 | 2.3 | Green (Over 5% headroom) | 17112 | 100 | 2.38 | 37 | 4 | 82432 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1288 | 0.80955 | SPN-S000000008502 | 219041148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1482 | 33.2 | UNIT 13, NEW LUCKHURST FARM, BETHERSDEN ROAD | ASHFORD | TN27 8QT | Ashford |  | Workshop And Premises | industrial | 1 | 1400.44 | 15074 | GIA | 64500 | ASHFORD WEST 33/6.6KV | inside-area | 4.12 | Ashford Grid | Sellindge | East Kent Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.1 | Thermal | 0 | 0 | 0 | 0 | 2.4 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 6.3 | 4.8 | Winter | 36.5079 | 2.3 | Green (Over 5% headroom) | 17112 | 100 | 2.23 | 63 | 4 | 83458 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012879582 | Storage or Distribution | 1431 | A | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-07-01 |  | 1 | FALSE | 51.1323 | 0.6908 | SPN-S000000008502 | 14078082000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1483 | 33.2 | UNITS 30 & 33, OLD SURRENDEN MANOR FARM | ASHFORD | TN26 3DL | Ashford |  | Workshop And Premises | industrial | 1 | 1298.05 | 13972 | GIA | 76000 | ASHFORD WEST 33/6.6KV | inside-area | 3.69 | Ashford Grid | Sellindge | East Kent Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.1 | Thermal | 0 | 0 | 0 | 0 | 2.4 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 6.3 | 4.8 | Winter | 36.5079 | 2.3 | Green (Over 5% headroom) | 17112 | 100 | 2.06 | 58 | 4 | 84560 | SPN-S000000371668 | 200 | 140 | 60-80% | ASHFORD WEST 33/6.6KV | 375 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012868759 | Offices and Workshop Businesses | 612 | E | Oil | 3 | 1 | Heating and Natural Ventilation | 2024-07-30 |  | 1 | FALSE | 51.1277 | 0.78702 | SPN-S000000008502 | 10414248000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1484 | 33.2 | BARN STORE SWATTENDEN GILL, SWATTENDEN LANE | CRANBROOK | TN17 3PR | Tunbridge Wells |  | Store And Premises | industrial | 1 | 1063.27 | 11445 | GIA | 31000 | CRANBROOK 33/11KV | inside-area | 1.42 | Hartley Grid | Ninfield | East Sussex Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.2 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 35.4839 | 2.2 | Green (Over 5% headroom) | 17112 | 100 | 1.69 | 27 | 3 | 58410 | SPN-R000000838105-000-007Z | 50 | 25 | 40-60% | CRANBROOK 33/11KV | 163 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.0824 | 0.53033 | SPN-S000000008381 | 10359580000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1485 | 33.2 | UNITS 4 & 5, THE OLD SAW MILL, PLUCKLEY ROAD | ASHFORD | TN26 3DD | Ashford |  | Factory And Premises | industrial | 1 | 1047 | 11270 | GIA | 31000 | ASHFORD WEST 33/6.6KV | inside-area | 1.7 | Ashford Grid | Sellindge | East Kent Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.1 | Thermal | 0 | 0 | 0 | 0 | 2.4 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 6.3 | 4.8 | Winter | 36.5079 | 2.3 | Green (Over 5% headroom) | 17112 | 100 | 1.66 | 63 | 4 | 87262 | SPN-S000000361082 | 315 | 220 | 60-80% | ASHFORD WEST 33/6.6KV | 35 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004392272 | Storage or Distribution | 1219 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-03-17 |  | 1 | FALSE | 51.1338 | 0.75523 | SPN-S000000008502 | 3160358000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1486 | 33.2 | UNITS 6-9 & OFFICES 1 & 3-6, COURTLANDS FARM, TURNDEN ROAD | CRANBROOK | TN17 2QL | Tunbridge Wells |  | Workshop And Premises | industrial | 1 | 1006.08 | 10829 | GIA | 101000 | CRANBROOK 33/11KV | inside-area | 1.25 | Hartley Grid | Ninfield | East Sussex Zone | 2.4 | primary | 2.4 | Green | 6.5 | 4.2 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 35.4839 | 2.2 | Green (Over 5% headroom) | 17112 | 100 | 1.6 | 45 | 3 | 59026 | SPN-S000000443009 | 500 | 350 | 60-80% | CRANBROOK 33/11KV | 204 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 10008671371 | B1 Offices and Workshop businesses | 76 | C | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2021-06-28 |  | 1 | FALSE | 51.0916 | 0.51631 | SPN-S000000008381 | 9223791000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1487 | 32.9 | DARENTH HOUSE 84-88, MAIN ROAD | SEVENOAKS | TN14 6ER | Sevenoaks |  | Offices And Premises | office | 1 | 1403.46 | 15107 | NIA | 305000 | SUNDRIDGE 33/11KV | inside-area | 0.12 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 2.23 | 98 | 9 | 289328 | SPN-S000000446942 | 800 | 560 | 60-80% |  | 99 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013770775 | Offices and Workshop Businesses | 2662 | C | Natural Gas | 4 |  | Mixed-mode with Mechanical Ventilation | 2026-07-15 |  | 0.75 | FALSE | 51.2795 | 0.13539 | SPN-S000000008496 | 11077157000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1488 | 32.9 | 101, LONDON ROAD | SEVENOAKS | TN13 1AX | Sevenoaks |  | Offices And Premises | office | 1 | 1324.1 | 14252 | NIA | 236000 | SUNDRIDGE 33/11KV | inside-area | 3.99 | Chelsfield Grid | Northfleet | West Kent Zone | 6.7 | primary | 6.7 | Green | 24 | 17.6 | Thermal | 2 | 0 | 0 | 2 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | Green (Over 5% headroom) | 47772 | 100 | 2.1 | 93 | 9 | 290183 | SPN-S000000446615 | 800 | 400 | 40-60% |  | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.2725 | 0.18991 | SPN-S000000008496 | 411632148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1489 | 32.9 | UNIT B STENMAR WORKS, COMMERCE WAY | EDENBRIDGE | TN8 6ED | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1740.7 | 18737 | GIA | 151000 | EDENBRIDGE 33/11KV | inside-area | 1.29 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 84 | 2.77 | 44 | 11 | 423236 | SPN-S000000442659 | 500 | 250 | 40-60% | EDENBRIDGE 33/11KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013771497 | B8 Storage or Distribution | 2698 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-28 |  | 1 | FALSE | 51.2054 | 0.06327 | SPN-S000000008614 | 7558487000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1490 | 32.9 | UNITS 3-7, BLIBY FARM | ASHFORD | TN25 7JB | Ashford |  | Workshop, Office And Premises | industrial | 1 | 1111.73 | 11967 | GIA | 57500 | SMEETH 33/11KV | inside-area | 4.09 | Sellindge Grid | Sellindge | East Kent Zone | 2.2 | primary | 2.2 | Green | 3.8 | 0.9 | Thermal | 0 | 0 | 0 | 0 | 2.9 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.7 | Winter | 76.3158 | 2.9 | Green (Over 5% headroom) | 15686 | 100 | 1.77 | 50 | 1 | 29811 | SPN-R000000848501-000-080Z | 200 | 180 | 80-100% | WAREHORNE 33/11KV | 284 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.101 | 0.89198 | SPN-S000000008485 | 10201117000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1491 | 32.9 | GND FLR REAR & 1ST FLR UNIT A STENMAR WORKS, COMMERCE WAY | EDENBRIDGE | TN8 6ED | Sevenoaks |  | Warehouse And Premises | industrial | 1 | 1024.04 | 11023 | GIA | 118000 | EDENBRIDGE 33/11KV | inside-area | 1.29 | Dormansland Grid | Northfleet | West Sussex Zone | 2.2 | primary | 2.2 | Green | 9.6 | 7.4 | Thermal | 0 | 0 | 1.7 | 0 | 2.3 | Dormansland Grid 33kV | 53.5 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | Green (Over 5% headroom) | 15686 | 100 | 1.63 | 26 | 11 | 430950 | SPN-S000000442659 | 500 | 250 | 40-60% | EDENBRIDGE 33/11KV | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10013771496 | B8 Storage or Distribution | 963 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2021-07-28 |  | 1 | FALSE | 51.2054 | 0.06327 | SPN-S000000008614 | 7997799000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1492 | 32.8 | CIVIC CENTRE, ST MARYS ROAD | SWANLEY | BR8 7BU | Sevenoaks | SWANLEY TOWN COUNCIL | Offices And Premises | office | 1 | 1318.05 | 14187 | NIA | 172000 | SWANLEY 33/11KV | inside-area | 1.29 | Chelsfield Grid | Northfleet | West Kent Zone | 6.6 | primary | 6.6 | Green | 22.8 | 16.3 | Thermal | 0 | 4.5 | 0 | 4.5 | 5.1 | Chelsfield Grid 33kV | 37.7 | GREEN | 45 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | Green (Over 5% headroom) | 47059 | 100 | 2.09 | 92 | 18 | 1058466 | SPN-S000000316143 | 500 | 250 | 40-60% | SWANLEY 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3942 | 0.16737 | SPN-S000000008528 | 413603148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1493 | 32.7 | UNIT B, RIVERSIDE BUSINESS PARK, NEW HYTHE LANE | AYLESFORD | ME20 6WT | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 22780.48 | 245207 | GIA | 2130000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.32 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 6 | 36.2 | 570 | 23 | 1573734 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 334 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10002917473 | Storage or Distribution | 22967 | A | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2026-04-13 |  | 1 | FALSE | 51.3156 | 0.45709 | SPN-S000000008653 | 4236785000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1494 | 32.7 | UNIT 1, INVICTA PARK, NEW HYTHE LANE | AYLESFORD | ME20 7FG | Tonbridge & Malling |  | Warehouse And Premises; Workshop And Premises | industrial | 3 | 18044.7 | 194231 | GIA | 1742500 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.87 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 7 | 28.67 | 812 | 23 | 1624710 | [9 empty] | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10013924496 | Storage or Distribution | 8901 | B | Natural Gas | 4 |  | Heating and Natural Ventilation | 2025-06-05 |  | 1 | FALSE | 51.3106 | 0.45799 | SPN-S000000008653 | 9733427000;9655931000;9655934000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1495 | 32.7 | SOUTH EAST WATER, ROCFORT ROAD | SNODLAND | ME6 5NQ | Tonbridge & Malling |  | Offices And Premises | office | 1 | 3739.49 | 40251 | NIA | 497500 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.4 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 35 | 5.94 | 262 | 23 | 1778690 | SPN-S000000391472 | 300 | 90 | 20-40% | TOWNSEND HOOK 33/6.6KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3294 | 0.44614 | SPN-S000000008653 | 6987649000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1496 | 32.7 | MEDWAY GAP POSTAL SORTING OFFICE, SORTMILL ROAD | SNODLAND | ME6 5GP | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1350.06 | 14532 | GIA | 142000 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.23 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 98 | 2.15 | 34 | 23 | 1804409 | SPN-S000000394290 | 800 | 560 | 60-80% | TOWNSEND HOOK 33/6.6KV | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3263 | 0.44667 | SPN-S000000008653 | 387934148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1497 | 32.7 | UNITS A3 & A4, LARKFIELD TRADING ESTATE, NEW HYTHE LANE | AYLESFORD | ME20 6SW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1303.59 | 14032 | GIA | 119000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.35 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 100 | 2.07 | 33 | 23 | 1804909 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 |  | Storage or Distribution | 1325 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2025-08-19 |  | 1 | FALSE | 51.3146 | 0.45191 | SPN-S000000008653 | 12932283000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1498 | 32.7 | UNIT 1 BLOCK E, LARKFIELD TRADING ESTATE, NEW HYTHE LANE | AYLESFORD | ME20 6SW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1039.37 | 11188 | GIA | 107000 | TOWNSEND HOOK 33/6.6KV | inside-area | 1.35 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 100 | 1.65 | 26 | 23 | 1807753 | SPN-S000000394238 | 1000 | 700 | 60-80% | TOWNSEND HOOK 33/6.6KV | 74 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10013918442 | Storage or Distribution | 776 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2022-11-16 |  | 0.8 | FALSE | 51.3146 | 0.45191 | SPN-S000000008653 | 14462944000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1499 | 32.7 | NORTHGATE VEHICLE HIRE, SORTMILL ROAD | SNODLAND | ME6 5UA | Tonbridge & Malling |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1000.3 | 10767 | GIA | 138000 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.29 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 100 | 1.59 | 45 | 23 | 1808174 | SPN-S000000394290 | 800 | 560 | 60-80% | TOWNSEND HOOK 33/6.6KV | 121 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3251 | 0.44663 | SPN-S000000008653 | 14293625000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1500 | 32.5 | UNIT 1 AND UNIT 2, BMS INDUSTRIAL PARK, DENGEMARSH ROAD | ROMNEY MARSH | TN29 9JH | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 1377.36 | 14826 | GIA | 76500 | RYE 33/11KV | inside-area | 12.77 | Rye Grid | Ninfield | East Sussex Zone | 1.9 | primary | 1.9 | Green | 12.6 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.9 | Rye Grid 33kV | 7 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 12.2 | 9.6 | Winter | 14.7541 | 1.8 | Green (Over 5% headroom) | 13547 | 91 | 2.19 | 62 | 2 | 70475 | SPN-R000000846906-000-105Z | 200 | 60 | 20-40% | ROMNEY WARREN 33/11KV | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | 50002310 | B1 Offices and Workshop businesses | 943 | C | Other | 3 |  | Unconditioned | 2019-05-20 |  | 1 | FALSE | 50.9321 | 0.9076 | SPN-S000000008476 | 15061657000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1501 | 32.3 | PLOT 6, MOUNTFIELD ROAD INDUSTRIAL ESTATE | NEW ROMNEY | TN28 8LH | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 1341 | 14434 | GIA | 76500 | ROMNEY WARREN 33/11KV | inside-area | 1.62 | Ruckinge Grid | Sellindge | East Kent Zone | 1.7 | primary | 1.7 | Green | 13 | 9.9 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | Green (Over 5% headroom) | 12121 | 84 | 2.13 | 60 | 5 | 106645 | SPN-S000000363452 | 500 | 250 | 40-60% | ROMNEY WARREN 33/11KV | 176 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 50.9838 | 0.95202 | SPN-S000000008469 | 3528896000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1502 | 32.3 | BYRNE GROUP AT, CRICKETTS FARM, BOROUGH GREEN ROAD | SEVENOAKS | TN15 9JB | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1327.87 | 14293 | GIA | 196000 | WROTHAM HEATH 33/11KV | inside-area | 2.91 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 85 | 2.11 | 33 | 8 | 280884 | SPN-S000000391248 | 500 | 250 | 40-60% | WROTHAM HEATH 33/11KV | 289 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.2954 | 0.29588 | SPN-S000000008519 | 14651491000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1503 | 32.3 | UNITS 1-4, HORNET BUSINESS ESTATE, QUARRY HILL ROAD | SEVENOAKS | TN15 8QW | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 1323.16 | 14242 | GIA | 90500 | WROTHAM HEATH 33/11KV | inside-area | 3.05 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 85 | 2.1 | 33 | 8 | 280935 | SPN-S000000400023 | 800 | 560 | 60-80% | WROTHAM HEATH 33/11KV | 106 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.2882 | 0.29901 | SPN-S000000008519 | 9564863000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1504 | 32.3 | HANCOCK INDUSTRIAL WORKSHOPS, KITEWELL LANE | ROMNEY MARSH | TN29 9LP | Folkestone & Hythe |  | Warehouse, Workshop And Premises | industrial | 1 | 1214 | 13067 | GIA | 52000 | ROMNEY WARREN 33/11KV | inside-area | 5.43 | Ruckinge Grid | Sellindge | East Kent Zone | 1.7 | primary | 1.7 | Green | 13 | 9.9 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | Green (Over 5% headroom) | 12121 | 93 | 1.93 | 55 | 5 | 108012 | SPN-R000000846908-000-244Z | 100 | 50 | 40-60% | ROMNEY WARREN 33/11KV | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 50.9571 | 0.91563 | SPN-S000000008469 | 886742000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1505 | 32.3 | UNIT 3, PLATT MILL INDUSTRIAL ESTATE, MILL PLACE, MAIDSTONE ROAD | SEVENOAKS | TN15 8FD | Tonbridge & Malling |  | Workshop And Premises | industrial | 1 | 1118.86 | 12043 | GIA | 77500 | WROTHAM HEATH 33/11KV | inside-area | 1.24 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 100 | 1.78 | 50 | 8 | 283134 | SPN-S000000393344 | 800 | 560 | 60-80% | WROTHAM HEATH 33/11KV | 40 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | 10013915734 | B1 Offices and Workshop businesses | 930 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-09-21 |  | 1 | FALSE | 51.2953 | 0.32312 | SPN-S000000008519 | 15118502000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1506 | 32.3 | UNIT 20, MOUNTFIELD ROAD INDUSTRIAL ESTATE | NEW ROMNEY | TN28 8LH | Folkestone & Hythe |  | Workshop And Premises | industrial | 1 | 1112.56 | 11975 | GIA | 70000 | ROMNEY WARREN 33/11KV | inside-area | 1.62 | Ruckinge Grid | Sellindge | East Kent Zone | 1.7 | primary | 1.7 | Green | 13 | 9.9 | Thermal | 0 | 0 | 0 | 0 | 1.6 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | Green (Over 5% headroom) | 12121 | 100 | 1.77 | 50 | 5 | 109104 | SPN-S000000363452 | 500 | 250 | 40-60% | ROMNEY WARREN 33/11KV | 176 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50116073 | A1/A2 Retail and Financial/Professional services | 1025 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-02-10 |  | 1 | FALSE | 50.9838 | 0.95202 | SPN-S000000008469 | 9374057000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1507 | 31.9 | UNIT 3, DACLIFFE INDUSTRIAL ESTATE, APPLEDORE ROAD | ASHFORD | TN26 3TG | Ashford |  | Warehouse And Premises | industrial | 1 | 1500.89 | 16155 | GIA | 79500 | KENARDINGTON 33/6.6KV | inside-area | 2.61 | Ruckinge Grid | Sellindge | East Kent Zone | 1.4 | primary | 1.4 | Green | 7.2 | 5.3 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 7.1 | 4 | Winter | 26.7606 | 1.9 | Green (Over 5% headroom) | 9982 | 62 | 2.38 | 38 | 1 | 13171 | SPN-R000000831901-000-123Z | 100 | 70 | 60-80% | KENARDINGTON 33/6.6KV | 73 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200004393647 | B8 Storage or Distribution | 549 | D | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2018-04-20 |  | 0.67 | FALSE | 51.0716 | 0.77866 | SPN-S000000008319 | 11117103000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1508 | 31.9 | THE COVERED YARDS AT PARK FARM BARN, SCHOOL ROAD | ASHFORD | TN26 2AR | Ashford |  | Store And Premises | industrial | 1 | 1223.6 | 13171 | GIA | 57000 | KENARDINGTON 33/6.6KV | inside-area | 3.17 | Ruckinge Grid | Sellindge | East Kent Zone | 1.4 | primary | 1.4 | Green | 7.2 | 5.3 | Thermal | 0 | 0 | 0 | 0 | 1.7 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 7.1 | 4 | Winter | 26.7606 | 1.9 | Green (Over 5% headroom) | 9982 | 76 | 1.94 | 31 | 1 | 16155 | SPN-R000000831903-000-085Z | 100 | 70 | 60-80% | KENARDINGTON 33/6.6KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.039 | 0.78093 | SPN-S000000008319 | 184892000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1509 | 31.8 | UNIT 2, NEWSPRINT AVENUE, PANATTONI PARK | AYLESFORD | ME20 7XH | Tonbridge & Malling | DME4 AMAZON | Warehouse And Premises | industrial | 2 | 75687.18 | 814689 | GIA | 7800000 | AYLESFORD 33/6.6KV | inside-area | 1.21 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 6 | 120.27 | 1892 | 85 | 4251005 | SPN-S000000400184 | 1000 | 900 | 80-100% | AYLESFORD 33/6.6KV | 327 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10094698371 | Storage or Distribution | 58782 | A+ | Grid Supplied Electricity | 4 |  | Air Conditioning | 2025-06-05 |  | 1 | FALSE | 51.3072 | 0.45342 | SPN-S000000008312 | 15029809000;14504777000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1510 | 31.8 | WAITROSE LTD, BEDDOW WAY | AYLESFORD | ME20 7BT | Tonbridge & Malling |  | Warehouse And Premises | industrial | 1 | 52708.81 | 567352 | GIA | 2670000 | AYLESFORD 33/6.6KV | inside-area | 1.78 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 9 | 83.76 | 1318 | 85 | 4498342 | SPN-S000000392305 | 500 | 250 | 40-60% | AYLESFORD 33/6.6KV | 51 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.303 | 0.49266 | SPN-S000000008312 | 5407401000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1511 | 31.8 | UNIT 1, CLICK AYLESFORD, FRANK SANDO WAY | AYLESFORD | ME20 7NY | Tonbridge & Malling |  | Warehouse And Premises | industrial | 6 | 32867.23 | 353780 | GIA | 3187500 | AYLESFORD 33/6.6KV | inside-area | 1.58 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 14 | 52.23 | 822 | 85 | 4711914 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.298 | 0.48968 | SPN-S000000008312 | 14861385000;15154857000;14940654000;14861405000;14987498000;14861450000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1512 | 31.8 | UNIT 3, LARKFIELD MILL, BELLINGHAM WAY | AYLESFORD | ME20 6SQ | Tonbridge & Malling |  | Warehouse And Premises; Workshop And Premises | industrial | 6 | 28500.55 | 306777 | GIA | 1891000 | AYLESFORD 33/6.6KV | inside-area | 1.25 | Burham Grid | Northfleet | Mid Kent Zone | 7 | primary | 7 | Green | 29 | 21.9 | Thermal | 2 | 4 | 1 | 6 | 1.4 | Burham Grid 33kV | 45.6 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | Green (Over 5% headroom) | 49911 | 16 | 45.29 | 1283 | 85 | 4758917 | SPN-S000000400184 | 1000 | 900 | 80-100% | AYLESFORD 33/6.6KV | 190 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.3061 | 0.45161 | SPN-S000000008312 | 14409794000;3493012000;14392161000;8077859000;3492242000;3492909000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1513 | 31.6 | MOUNTAIN FARM, MARSH ROAD | ASHFORD | TN26 2JD | Ashford |  | Warehouse And Premises | industrial | 1 | 1707.48 | 18379 | GIA | 63500 | WAREHORNE 33/11KV | inside-area | 1.61 | Ruckinge Grid | Sellindge | East Kent Zone | 1.2 | primary | 1.2 | Green | 5 | 3.7 | Thermal | 0 | 0 | 0 | 0 | 0.5 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 4.9 | 4.5 | Winter | 26.5306 | 1.3 | Green (Over 5% headroom) | 8556 | 47 | 2.71 | 43 | 3 | 107615 | SPN-S000000361228 | 500 | 350 | 60-80% | WAREHORNE 33/11KV | 185 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012860421 | B1 Offices and Workshop businesses | 207 | G | Oil | 3 |  | Heating and Natural Ventilation | 2019-01-22 |  | 1 | FALSE | 51.061 | 0.85915 | SPN-S000000008507 | 2264495000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1514 | 31.6 | NICKLEY WOOD, ORLESTONE MILL, CHURCH LANE | ASHFORD | TN26 1LZ | Ashford | ORLESTONE OAK | Workshop And Premises | industrial | 1 | 1702.49 | 18325 | GIA | 118000 | WAREHORNE 33/11KV | inside-area | 3.77 | Ruckinge Grid | Sellindge | East Kent Zone | 1.2 | primary | 1.2 | Green | 5 | 3.7 | Thermal | 0 | 0 | 0 | 0 | 0.5 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 4.9 | 4.5 | Winter | 26.5306 | 1.3 | Green (Over 5% headroom) | 8556 | 47 | 2.71 | 77 | 3 | 107669 | SPN-R000000831906-000-191Z | 200 | 140 | 60-80% | KENARDINGTON 33/6.6KV | 369 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0961 | 0.82798 | SPN-S000000008507 | 8093637000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1515 | 31.6 | GREEN OAK BARN, GOLDEN WOOD FARM, BRISLEY WOOD LANE | ASHFORD | TN26 2PW | Ashford |  | Warehouse And Premises | industrial | 1 | 1134 | 12206 | GIA | 12500 | WAREHORNE 33/11KV | inside-area | 4.73 | Ruckinge Grid | Sellindge | East Kent Zone | 1.2 | primary | 1.2 | Green | 5 | 3.7 | Thermal | 0 | 0 | 0 | 0 | 0.5 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 4.9 | 4.5 | Winter | 26.5306 | 1.3 | Green (Over 5% headroom) | 8556 | 70 | 1.8 | 28 | 3 | 113788 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0956 | 0.8789 | SPN-S000000008507 | 12335642000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1516 | 31.5 | R S SALES, HONEYCREST INDUSTRIAL PARK, LODGE ROAD | TONBRIDGE | TN12 0RX | Maidstone |  | Warehouse And Premises | industrial | 1 | 1484.08 | 15974 | GIA | 125000 | STAPLEHURST 33/6.6KV | inside-area | 0.48 | Hartley Grid | Ninfield | West Kent Zone | 1.1 | primary | 1.1 | Green | 6.5 | 5.4 | Thermal | 0 | 0 | 0 | 0 | 0.2 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 6.2 | 4.6 | Winter | 16.129 | 1 | Green (Over 5% headroom) | 7843 | 49 | 2.36 | 37 | 7 | 397928 | SPN-S000000394704 | 500 | 250 | 40-60% | STAPLEHURST 33/6.6KV | 77 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.1708 | 0.54795 | SPN-S000000008493 | 2565903000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1517 | 31.5 | LEIGH GREEN INDUSTRIAL ESTATE, APPLEDORE ROAD | TENTERDEN | TN30 7DF | Ashford | GEORGE J GOFF LTD | Storage Depot And Premises | industrial | 1 | 1046.6 | 11265 | OTH | 21750 | TENTERDEN 33/6.6KV | inside-area | 2.15 | Ruckinge Grid | Sellindge | East Sussex Zone | 1.1 | primary | 1.1 | Green | 11.9 | 10.7 | Thermal | 0 | 0 | 0 | 0 | 0.8 | Ruckinge Grid 33kV | 27.4 | GREEN | 9 | 99.9 | GREEN | 9 | 385.3 | 1 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | Green (Over 5% headroom) | 7843 | 70 | 1.66 | 26 | 5 | 157445 | SPN-R000000837608-000-138Z |  |  | 60-80% | TENTERDEN 33/6.6KV | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0608 | 0.71611 | SPN-S000000008376 | 8189096000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1518 | 31.3 | KENT COUNTY COUNCIL HIGHWAYS PEPPERHILL DEPOT, STATION ROAD | GRAVESEND | DA13 9PA | Dartford | KENT COUNTY COUNCIL HIGHWAYS | Storage Depot And Premises | industrial | 1 | 1936.14 | 20840 | OTH | 19750 | GRAVESEND SOUTH 33/11KV | inside-area | 3.29 | Northfleet East | Northfleet | West Kent Zone | 1 | primary | 1 | Amber | 22.8 | 21.8 | Thermal | 3.8 | 0 | 0 | 3.8 | -0.2 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.2 | Winter | 4.4248 | 1 | Yellow (Between 5% overloaded and 5% headroom) | 7130 | 34 | 3.08 | 48 | 4 | 427878 | SPN-S000000314180 | 200 | -20 | -20-0% | GRAVESEND SOUTH 33/11KV | 247 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4208 | 0.31154 | SPN-S000000008625 | 125549147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1519 | 31.1 | J SAINSBURY PLC, SIMONE WEIL AVENUE | ASHFORD | TN24 8YN | Ashford |  | Superstore And Premises | bigbox | 2 | 26883.47 | 289371 | GIA | 4640000 | ASHFORD EAST 33/11KV | inside-area | 2.15 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 8 | 42.72 | 2420 | 27 | 1675716 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1587 | 0.86728 | SPN-S000000008402 | 15143793000;14491544000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1520 | 30.8 | THE MILL, MAIDSTONE ROAD | ASHFORD | TN26 1AE | Ashford | WAREHOUSE | Warehouse And Premises | industrial | 1 | 1558.88 | 16780 | GIA | 81000 | LITTLE CHART 33/6.6KV | inside-area | 4.67 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 25 | 2.48 | 39 | 9 | 589558 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062562624 | B1 Offices and Workshop businesses | 7 | G | Oil | 3 |  | Heating and Natural Ventilation | 2013-02-12 |  | 1 | FALSE | 51.1697 | 0.84367 | SPN-S000000008428 | 2973970000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1521 | 30.8 | LITTLE HOOK FARM, HOOK LANE | ASHFORD | TN27 0AN | Ashford |  | Workshop And Premises | industrial | 1 | 1361.56 | 14656 | GIA | 119000 | LITTLE CHART 33/6.6KV | inside-area | 3.44 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 29 | 2.16 | 61 | 9 | 591682 | SPN-R000000842805-000-025Z | 100 | 70 | 60-80% | LITTLE CHART 33/6.6KV | 102 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062563243 | B1 Offices and Workshop businesses | 479 | C | Oil | 5 |  | Heating and Natural Ventilation | 2014-06-10 |  | 1 | FALSE | 51.2104 | 0.7788 | SPN-S000000008428 | 8900527000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1522 | 30.8 | UNITS 1 & 2 HUNGER HATCH BUILDING | ASHFORD | TN27 0QQ | Ashford |  | Workshop And Premises | industrial | 1 | 1119.83 | 12054 | GIA | 65500 | LITTLE CHART 33/6.6KV | inside-area | 1.81 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 35 | 1.78 | 50 | 9 | 594284 | SPN-R000000842805-000-010Z | 25 | 2 | 0-20% | LITTLE CHART 33/6.6KV | 205 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012848761 | B1 Offices and Workshop businesses | 383 | A | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2017-06-30 |  | 0.5 | FALSE | 51.195 | 0.77095 | SPN-S000000008428 | 14969946000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1523 | 30.8 | UNITS 1-4, PADDOCKS FARM, BETHERSDEN ROAD | ASHFORD | TN26 1EP | Ashford |  | Workshop And Premises | industrial | 1 | 1081.86 | 11645 | GIA | 39500 | LITTLE CHART 33/6.6KV | inside-area | 2.72 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 37 | 1.72 | 49 | 9 | 594693 | SPN-R000000842807-000-077Z | 100 | 50 | 40-60% | LITTLE CHART 33/6.6KV | 48 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062562611 | B2 to B7 General Industrial and Special Industrial Groups | 831 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2013-05-30 |  | 1 | FALSE | 51.1677 | 0.81264 | SPN-S000000008428 | 3734707000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1524 | 30.3 | NEWNHAM COURT GARDEN CENTRE, BEARSTED ROAD | MAIDSTONE | ME14 5LH | Maidstone |  | Garden Centre And Premises | bigbox | 1 | 14176.45 | 152594 | GIA | 370000 | MAIDSTONE GRID SOUTH | inside-area | 1.72 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 12 | 22.53 | 1276 | 19 | 656190 | SPN-S000000392586 | 1000 | 500 | 40-60% | MAIDSTONE GRID SOUTH | 16 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003690131 | Retail/Financial and Professional Services | 1685 | D | Natural Gas | 4 | 2 | Air Conditioning | 2024-11-12 |  | 1 | FALSE | 51.2846 | 0.55165 | SPN-S000000009533 | 12924768000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1525 | 30 | UNIT E, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Warehouse And Premises | industrial | 1 | 1625 | 17491 | GIA | 159000 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 2.58 | 41 | 28 | 1037934 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560421 | B2 to B7 General Industrial and Special Industrial Groups | 2293 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2016-12-02 |  | 0.5 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 329049148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1526 | 30 | UNIT 2D, ENTRALON GATE, ORBITAL PARK | ASHFORD | TN24 0LP | Ashford |  | Warehouse And Premises | industrial | 1 | 1585 | 17061 | GIA | 182000 | SEVINGTON 33/11KV | inside-area | 0.59 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 2.52 | 40 | 28 | 1038364 | SPN-S000000371288 | 500 | 350 | 60-80% | SEVINGTON 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.129 | 0.89914 | SPN-S000000008595 | 14563872000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1527 | 30 | HANOVER MILL, THE FORSTAL | ASHFORD | TN25 6NU | Ashford | T DENNE & SONS HOLDINGS LTD | Mill And Premises | industrial | 1 | 1555.2 | 16740 | GIA | 73000 | SEVINGTON 33/11KV | inside-area | 2.92 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 2.47 | 93 | 28 | 1038685 | SPN-S000000362184 | 500 | 350 | 60-80% | SEVINGTON 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012868094 | B1 Offices and Workshop businesses | 50 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2017-02-06 |  | 1 | FALSE | 51.1149 | 0.92675 | SPN-S000000008595 | 11125796000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1528 | 30 | UNITS 3&4 & 8-10, FOSTER ROAD, CONNECT 10, ASHFORD BUSINESS PARK | ASHFORD | TN24 0FE | Ashford |  | Warehouse And Premises | industrial | 1 | 1503.7 | 16186 | GIA | 108000 | SEVINGTON 33/11KV | inside-area | 0.84 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 2.39 | 38 | 28 | 1039239 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 64 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012868075 | B2 to B7 General Industrial and Special Industrial Groups | 1053 | C | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2016-12-07 |  | 0.86 | FALSE | 51.1315 | 0.90179 | SPN-S000000008595 | 8397263000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1529 | 30 | UNIT 1, ENTRALON GATE, ORBITAL PARK | ASHFORD | TN24 0LP | Ashford |  | Warehouse And Premises | industrial | 1 | 1452.9 | 15639 | GIA | 165000 | SEVINGTON 33/11KV | inside-area | 0.59 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 2.31 | 36 | 28 | 1039786 | SPN-S000000371288 | 500 | 350 | 60-80% | SEVINGTON 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.129 | 0.89914 | SPN-S000000008595 | 14563862000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1530 | 30 | 1, ST JOHNS COURT, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SJ | Ashford |  | Warehouse And Premises | industrial | 1 | 1217.87 | 13109 | GIA | 112000 | SEVINGTON 33/11KV | inside-area | 0.95 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 1.94 | 30 | 28 | 1042316 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560423 | A1/A2 Retail and Financial/Professional services | 803 | B | Natural Gas | 3 |  | Heating and Natural Ventilation | 2014-10-23 |  | 0.75 | FALSE | 51.1319 | 0.90313 | SPN-S000000008595 | 5534238000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1531 | 30 | D & D AUTOS, MOAT WAY, ORBITAL PARK | ASHFORD | TN24 0TT | Ashford |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1171.2 | 12607 | GIA | 136000 | SEVINGTON 33/11KV | inside-area | 0.59 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 1.86 | 53 | 28 | 1042818 | SPN-S000000371114 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 133 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012852358 | Offices and Workshop Businesses | 1119 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2023-10-11 |  | 0.67 | FALSE | 51.1315 | 0.89758 | SPN-S000000008595 | 6688002000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1532 | 30 | UNIT A, FOSTER ROAD, ASHFORD BUSINESS PARK | ASHFORD | TN24 0SH | Ashford |  | Warehouse And Premises | industrial | 1 | 1118.9 | 12044 | GIA | 99500 | SEVINGTON 33/11KV | inside-area | 0.89 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 1.78 | 28 | 28 | 1043381 | SPN-S000000371389 | 1000 | 900 | 80-100% | SEVINGTON 33/11KV | 123 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 100062560403 | Storage or Distribution | 1042 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2026-05-27 |  | 1 | FALSE | 51.1325 | 0.90173 | SPN-S000000008595 | 4483782000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1533 | 30 | WORKSHOP AT BARRETTS JAGUAR LAND ROVER UNITS 6-12, ARROWHEAD ROAD, WATERBROOK PARK | ASHFORD | TN24 0FL | Ashford |  | Workshop And Premises | industrial | 1 | 1043.52 | 11232 | GIA | 115000 | SEVINGTON 33/11KV | inside-area | 1.01 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 1.66 | 47 | 28 | 1044193 | SPN-S000000371598 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 191 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 |  | Offices and Workshop Businesses | 1097 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2024-11-07 |  | 1 | FALSE | 51.1263 | 0.90491 | SPN-S000000008595 | 14592806000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1534 | 29.9 | 144-145, MILTON ROAD | GRAVESEND | DA12 2AA | Gravesham |  | Post Office And Premises | office | 1 | 1420.63 | 15292 | NIA | 61500 | ROSHERVILLE 33/6.6KV | inside-area | 1.31 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 100 | 2.26 | 99 | 14 | 1975564 | SPN-S000000311237 | 800 | 400 | 40-60% | ROSHERVILLE 33/6.6KV | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4412 | 0.37333 | SPN-S000000008470 | 105354147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1535 | 29.6 | W.M.MORRISON, G-PARK, FLEET END | SITTINGBOURNE | ME10 2FD | Swale |  | Warehouse And Premises | industrial | 1 | 85907.43 | 924699 | GIA | 6890000 | GROVEHURST LOCAL | inside-area | 0.58 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 4 | 136.51 | 2148 | 31 | 2042910 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3711 | 0.75165 | SPN-S000000008585 | 11348964000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1536 | 29.6 | BUILDING S440, PANATTONI PARK, BARGE WAY | SITTINGBOURNE | ME10 2FD | Swale |  | Warehouse And Premises | industrial | 1 | 40868.8 | 439908 | GIA | 3760000 | GROVEHURST LOCAL | inside-area | 0.58 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 9 | 64.94 | 1022 | 31 | 2527701 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3711 | 0.75165 | SPN-S000000008585 | 15034414000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1537 | 29.6 | RIDHAM DOCK | SITTINGBOURNE | ME9 8SR | Swale | FLO GAS; KNAUF | Factory And Premises; Storage Depot And Premises | industrial | 2 | 31628 | 340441 | GIA | 1265500 | GROVEHURST LOCAL | inside-area | 1.65 | Grovehurst | Kemsley | Mid Kent Zone | 5.3 | primary | 5.3 | Green | 24 | 15.9 | Thermal | 0 | 1.2 | 0 | 1.2 | 2.8 |  |  |  | 0 | 94.3 | GREEN | 7 | 282.9 | 1 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | Green (Over 5% headroom) | 37790 | 11 | 50.26 | 1898 | 31 | 2627168 | SPN-S000000394887 | 315 | 32 | 0-20% | GROVEHURST LOCAL | 49 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10023196739 | Offices and Workshop Businesses | 398 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2023-05-18 |  | 1 | FALSE | 51.3805 | 0.75903 | SPN-S000000008585 | 335684147;6316532000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1538 | 29.3 | DICKLEY LANE | MAIDSTONE | ME17 2DD | Maidstone | MARLEY PLC | Factory And Premises | industrial | 1 | 50246.43 | 540848 | GIA | 1280000 | HARRIETSHAM 33/11KV | inside-area | 0.74 | Ashford Grid | Sellindge | Mid Kent Zone | 5.1 | primary | 5.1 | Green | 16 | 10.9 | Thermal | 13.5 | 0 | 5.4 | 13.5 | 3.5 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | Green (Over 5% headroom) | 36364 | 7 | 79.85 | 3015 | 5 | 582585 | SPN-S000000392002 | 300 | 210 | 60-80% | HARRIETSHAM 33/11KV | 32 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.2431 | 0.69877 | SPN-S000000008414 | 73733148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1539 | 29.3 | LENHAM STORAGE COMPANY LTD, HAM LANE | MAIDSTONE | ME17 2LH | Maidstone |  | Warehouse And Premises | industrial | 1 | 47956.65 | 516201 | GIA | 1350000 | HARRIETSHAM 33/11KV | inside-area | 0.32 | Ashford Grid | Sellindge | Mid Kent Zone | 5.1 | primary | 5.1 | Green | 16 | 10.9 | Thermal | 13.5 | 0 | 5.4 | 13.5 | 3.5 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | Green (Over 5% headroom) | 36364 | 7 | 76.21 | 1199 | 5 | 607232 | SPN-S000000394885 | 1000 | 700 | 60-80% | HARRIETSHAM 33/11KV | 69 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.237 | 0.70519 | SPN-S000000008414 | 1570361000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1540 | 28.4 | LIDL DISTRIBUTION CENTRE, CRETE HALL ROAD | GRAVESEND | DA11 9AA | Gravesham |  | Warehouse And Premises | industrial | 3 | 127195.8 | 1369123 | GIA | 16030000 | ROSHERVILLE 33/6.6KV | inside-area | 0.53 | Northfleet East | Northfleet | West Kent Zone | 4.4 | primary | 4.4 | Green | 19.5 | 15.1 | Thermal | 0 | 2.4 | 0 | 2.4 | 0.6 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | Green (Over 5% headroom) | 31373 | 2 | 202.13 | 3180 | 14 | 621733 | SPN-S000000311112 | 300 | 210 | 60-80% | ROSHERVILLE 33/6.6KV | 35 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4441 | 0.34759 | SPN-S000000008470 | 9325943000;9325943000;9325943000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1541 | 28.1 | KENT COUNTY COUNCIL, JAVELIN WAY | ASHFORD | TN24 8AD | Ashford |  | Offices And Premises | office | 1 | 1819.9 | 19589 | NIA | 297500 | ASHFORD EAST 33/11KV | inside-area | 0.87 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.89 | 127 | 27 | 1945498 | SPN-S000000364093 | 315 | 158 | 40-60% | ASHFORD EAST 33/11KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012881920 | Offices and Workshop Businesses | 2213 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2026-04-10 |  | 0.5 | FALSE | 51.1507 | 0.88813 | SPN-S000000008402 | 15116017000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1542 | 28.1 | INCA HOUSE, TRINITY ROAD | ASHFORD | TN25 4AB | Ashford |  | Offices And Premises | office | 1 | 1401.56 | 15086 | NIA | 340000 | ASHFORD EAST 33/11KV | inside-area | 2.47 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 100 | 2.23 | 98 | 27 | 1950001 | SPN-S000000371073 | 500 | 150 | 20-40% | ASHFORD EAST 33/11KV | 105 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012862681 | B1 Offices and Workshop businesses | 1616 | D | Grid Supplied Electricity | 3 | 1 | Air Conditioning | 2015-10-02 |  | 1 | FALSE | 51.1717 | 0.87315 | SPN-S000000008402 | 14760254000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1543 | 27.7 | RAIL SHED, THAMESPORT, GRAIN ROAD | ROCHESTER | ME3 0EP | Medway |  | Warehouse And Premises | industrial | 1 | 36805.43 | 396170 | GIA | 690000 | GRAIN 33/11KV | inside-area | 0.59 | Northfleet East | Northfleet | Mid Kent Zone | 3.9 | primary | 3.9 | Green | 7.3 | 3.4 | Voltage | 0 | 0 | 55 | 0 | 2.1 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 6.8 | 6.8 | Winter | 52.9412 | 3.6 | Green (Over 5% headroom) | 27807 | 7 | 58.49 | 920 | 2 | 85794 | [9 empty] | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4412 | 0.68581 | SPN-S000000008425 | 15150513000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1544 | 27.5 | 1ST-4TH FLRS BLOCK B, INTERNATIONAL HOUSE, DOVER PLACE | ASHFORD | TN23 1HU | Ashford |  | Offices And Premises | office | 1 | 1493.7 | 16078 | NIA | 190000 | ASHFORD CENTRAL | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.37 | 105 | 36 | 952160 | SPN-S000000361029 | 750 | 525 | 60-80% | ASHFORD CENTRAL | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012841872 | B1 Offices and Workshop businesses | 9691 | D | Natural Gas | 4 |  | Heating and Natural Ventilation | 2018-10-10 |  | 1 | FALSE | 51.1446 | 0.87623 | SPN-S000000008302 | 927941000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1545 | 27.5 | CUMMING HOUSE, WOTTON ROAD | ASHFORD | TN23 6LW | Ashford |  | Office And Premises | office | 1 | 1416.89 | 15251 | NIA | 137000 | ASHFORD CENTRAL | inside-area | 1.4 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 2.25 | 99 | 36 | 952987 | SPN-S000000362128 | 500 | 250 | 40-60% | SINGLETON 33/6.6KV | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012872774 | B1 Offices and Workshop businesses | 1167 | C | Grid Supplied Electricity | 3 | 3 | Air Conditioning | 2014-06-01 |  | 0.5 | FALSE | 51.1327 | 0.86671 | SPN-S000000008302 | 331192148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1546 | 27.5 | 3RD & 4TH FLRS BLOCK A, INTERNATIONAL HOUSE, DOVER PLACE | ASHFORD | TN23 1HU | Ashford |  | Offices And Premises | office | 1 | 1074.6 | 11567 | NIA | 181000 | ASHFORD CENTRAL | inside-area | 0.57 | Ashford Grid | Sellindge | East Kent Zone | 2.6 | primary | 2.6 | Green | 22.9 | 18 | Thermal | 2 | 9.7 | 0 | 11.7 | -4.3 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | Green (Over 5% headroom) | 18538 | 100 | 1.71 | 75 | 36 | 956671 | SPN-S000000361029 | 750 | 525 | 60-80% | ASHFORD CENTRAL | 26 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 10012841872 | B1 Offices and Workshop businesses | 9691 | D | Natural Gas | 4 |  | Heating and Natural Ventilation | 2018-10-10 |  | 1 | FALSE | 51.1446 | 0.87623 | SPN-S000000008302 | 15070456000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1547 | 27.3 | 39-40, ST MARGARETS STREET | CANTERBURY | CT1 2TY | Canterbury |  | Offices And Premises | office | 1 | 1713.96 | 18449 | NIA | 155000 | CANTERBURY TOWN 33/11KV | inside-area | 0.93 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 97 | 2.72 | 120 | 27 | 1040327 | SPN-S000000341676 | 500 | 150 | 20-40% | CANTERBURY TOWN 33/11KV | 56 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2777 | 1.0787 | SPN-S000000008410 | 4532549000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1548 | 27.3 | HALL PLACE, CHURCH HILL | CANTERBURY | CT2 9AG | Canterbury |  | Offices And Premises | office | 1 | 1671.6 | 17993 | NIA | 182000 | CANTERBURY TOWN 33/11KV | inside-area | 2.49 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 99 | 2.66 | 117 | 27 | 1040783 | SPN-R000000841006-000-020Z | 100 | 10 | 0-20% | CANTERBURY TOWN 33/11KV | 231 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062618672 | C2 Residential Institutions - Universities and colleges | 2362 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-10-02 |  | 0.75 | FALSE | 51.284 | 1.0496 | SPN-S000000008410 | 519082145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1549 | 27.3 | 1 COUNTY GATE LOWER GND GROUND & 1ST FLRS, STACEYS STREET | MAIDSTONE | ME14 1ST | Maidstone |  | Offices And Premises | office | 1 | 1511.89 | 16274 | NIA | 360000 | WATERSIDE 33/11KV | inside-area | 0.24 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 2.4 | 106 | 44 | 1710352 | SPN-S000000394007 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 81 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003654884 | B1 Offices and Workshop businesses | 2520 | B | Grid Supplied Electricity | 4 |  | Mixed-mode with Mechanical Ventilation | 2018-11-13 |  | 1 | FALSE | 51.2791 | 0.5187 | SPN-S000000008529 | 12963043000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1550 | 27.3 | 423, SUTTON ROAD | MAIDSTONE | ME15 8RA | Maidstone |  | Office And Premises | office | 1 | 1491.23 | 16051 | OTH | 56500 | SHEPWAY 33/11KV | inside-area | 1.02 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.37 | 104 | 47 | 1483218 | SPN-S000000392378 | 500 | 150 | 20-40% | SHEPWAY 33/11KV | 120 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.244 | 0.55732 | SPN-S000000008644 | 15017327000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1551 | 27.3 | NORTHGATE HOUSE 115-124, NORTHGATE | CANTERBURY | CT1 1BH | Canterbury |  | Offices And Premises | office | 1 | 1421.4 | 15300 | NIA | 184000 | CANTERBURY TOWN 33/11KV | inside-area | 0.17 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 100 | 2.26 | 99 | 27 | 1043476 | SPN-S000000341812 | 800 | 240 | 20-40% | CANTERBURY TOWN 33/11KV | 106 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2836 | 1.0861 | SPN-S000000008410 | 926332000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1552 | 27.3 | OFFICES AT HOMESTEAD FARM, STONE STREET | CANTERBURY | CT4 5PP | Canterbury |  | Offices And Premises | office | 1 | 1380.78 | 14863 | NIA | 126000 | CHARTHAM 33/11KV | inside-area | 5.62 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 5.2 | Green | 15 | 9.4 | Thermal | 0 | 5.7 | 0 | 5.7 | 5.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 14.4 | 10.6 | Winter | 37.5 | 5.4 | Green (Over 5% headroom) | 17825 | 100 | 2.19 | 97 | 4 | 132616 | SPN-R000000856006-000-267Z | 100 | 50 | 40-60% | CHARTHAM 33/11KV | 217 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033173404 | Offices and Workshop Businesses | 1301 | D | Oil | 3 |  | Heating and Natural Ventilation | 2024-04-12 |  | 0.75 | FALSE | 51.2109 | 1.059 | SPN-S000000008560 | 4820807000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1553 | 27.3 | TERRADACE HOLDINGS LIMITED, CORBIN BUSINESS PARK, CARING LANE | MAIDSTONE | ME14 4NJ | Maidstone |  | Offices And Premises | office | 1 | 1374.31 | 14793 | NIA | 179000 | SHEPWAY 33/11KV | inside-area | 3.43 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 2.18 | 96 | 47 | 1484476 | SPN-S000000393478 | 315 | 220 | 60-80% | MAIDSTONE GRID SOUTH | 39 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014311803 | B1 Offices and Workshop businesses | 495 | C | Natural Gas | 3 | 2 | Air Conditioning | 2018-10-30 |  | 0.5 | FALSE | 51.2628 | 0.59602 | SPN-S000000008644 | 15022016000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1554 | 27.3 | SECOND-FOURTH FLOOR, MEDWAY BRIDGE HOUSE 1-8, FAIRMEADOW | MAIDSTONE | ME14 1JP | Maidstone |  | Offices And Premises | office | 1 | 1286.46 | 13847 | NIA | 287500 | WATERSIDE 33/11KV | inside-area | 0.41 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 2.04 | 90 | 44 | 1712779 | SPN-S000000392349 | 800 | 560 | 60-80% | WATERSIDE 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003717373 | B1 Offices and Workshop businesses | 2382 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2018-02-12 |  | 1 | FALSE | 51.2733 | 0.51948 | SPN-S000000008529 | 15049322000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1555 | 27.3 | MEDWAY HOUSE 81, LONDON ROAD | MAIDSTONE | ME16 0DU | Maidstone |  | Offices And Premises | office | 1 | 1253.7 | 13495 | NIA | 159000 | WATERSIDE 33/11KV | inside-area | 0.82 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.99 | 88 | 44 | 1713131 | SPN-S000000394844 | 315 | 220 | 60-80% | FAIRMEADOW 11KV | 76 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003670435 | B1 Offices and Workshop businesses | 1257 | D | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-05-01 |  | 1 | FALSE | 51.2777 | 0.50743 | SPN-S000000008529 | 181160148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1556 | 27.3 | RIDING GATE HOUSE 37, OLD DOVER ROAD | CANTERBURY | CT1 3JB | Canterbury |  | Offices And Premises | office | 1 | 1252.4 | 13481 | NIA | 163000 | CANTERBURY TOWN 33/11KV | inside-area | 1.15 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 6.9 | Green | 45.7 | 38.8 | Thermal | 0 | 0 | 1 | 0 | 2.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | Green (Over 5% headroom) | 17825 | 100 | 1.99 | 88 | 27 | 1045295 | SPN-S000000341817 | 1000 | 700 | 60-80% | CANTERBURY TOWN 33/11KV | 34 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10033173055 | Offices and Workshop Businesses | 625 | C | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2022-11-18 |  | 0.6 | FALSE | 51.2747 | 1.0833 | SPN-S000000008410 | 926215000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1557 | 27.3 | UNIT 2, LOWER BOXLEY ROAD | MAIDSTONE | ME14 2UU | Maidstone |  | Offices And Premises | office | 1 | 1240.3 | 13350 | NIA | 238000 | WATERSIDE 33/11KV | inside-area | 0.41 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.97 | 87 | 44 | 1713276 | SPN-S000000392490 | 500 | 150 | 20-40% | MAIDSTONE GRID SOUTH | 184 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003669902 | B1 Offices and Workshop businesses | 1593 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2021-09-17 |  | 0.67 | FALSE | 51.2802 | 0.52209 | SPN-S000000008529 | 15165061000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1558 | 27.3 | JOB CENTRE PLUS, BOXLEY ROAD | MAIDSTONE | ME14 2UU | Maidstone |  | Offices And Premises | office | 1 | 1240.3 | 13350 | NIA | 238000 | WATERSIDE 33/11KV | inside-area | 0.41 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.97 | 87 | 44 | 1713276 | SPN-S000000392490 | 500 | 150 | 20-40% | MAIDSTONE GRID SOUTH | 184 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2802 | 0.52209 | SPN-S000000008529 | 13542247000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1559 | 27.3 | GND PT 1ST AND 2ND FLRS TOWERGATE HOUSE 5 ECLIPSE PARK, SITTINGBOURNE ROAD | MAIDSTONE | ME14 3EN | Maidstone |  | Offices And Premises | office | 1 | 1210.78 | 13033 | NIA | 267500 | MAIDSTONE GRID SOUTH | inside-area | 1.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 100 | 1.92 | 85 | 19 | 795751 | SPN-S000000394805 | 800 | 560 | 60-80% | MAIDSTONE GRID SOUTH | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10094442385 | B1 Offices and Workshop businesses | 2631 | C | Natural Gas | 4 | 2 | Air Conditioning | 2020-08-21 |  | 1 | FALSE | 51.2856 | 0.5466 | SPN-S000000009533 | 12586269000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1560 | 27.3 | GLOBE HOUSE UNIT 2, ECLIPSE PARK, SITTINGBOURNE ROAD | MAIDSTONE | ME14 3EN | Maidstone |  | Offices And Premises | office | 1 | 1169.85 | 12592 | NIA | 255000 | MAIDSTONE GRID SOUTH | inside-area | 1.56 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 12.1 | Green | 38.1 | 23.6 | Thermal | 1 | 5.1 | 6 | 6.1 | 12.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 37 | 29.1 | Winter | 38.1081 | 14.1 | Green (Over 5% headroom) | 17825 | 100 | 1.86 | 82 | 19 | 796192 | SPN-S000000394805 | 800 | 560 | 60-80% | MAIDSTONE GRID SOUTH | 101 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10022897419 | B2 to B7 General Industrial and Special Industrial Groups | 1847 | D | Grid Supplied Electricity | 4 | 2 | Air Conditioning | 2018-09-28 |  | 1 | FALSE | 51.2856 | 0.5466 | SPN-S000000009533 | 5307223000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1561 | 27.3 | MAIDSTONE TELEPHONE EXCHANGE 2, WYKE MANOR ROAD | MAIDSTONE | ME14 1BZ | Maidstone | BRITISH TELECOMMUNICATIONS PLC | Offices And Premises | office | 1 | 1143 | 12303 | NIA | 86500 | WATERSIDE 33/11KV | inside-area | 0.43 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.82 | 80 | 44 | 1714323 | SPN-S000000392484 | 1000 | 700 | 60-80% | MAIDSTONE NORTH 132/11KV | 45 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2747 | 0.52396 | SPN-S000000008529 | 37754148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1562 | 27.3 | 59, LONDON ROAD | MAIDSTONE | ME16 8JH | Maidstone |  | Offices And Premises | office | 1 | 1135.57 | 12223 | NIA | 140000 | WATERSIDE 33/11KV | inside-area | 0.72 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.8 | 79 | 44 | 1714403 | SPN-S000000392330 | 500 | 350 | 60-80% | WATERSIDE 33/11KV | 55 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 200003674606 | Offices and Workshop Businesses | 1442 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2026-02-25 |  | 1 | FALSE | 51.2754 | 0.50903 | SPN-S000000008529 | 38931148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1563 | 27.3 | 5TH FLR, MAIDSTONE HOUSE, KING STREET | MAIDSTONE | ME15 6JQ | Maidstone |  | Offices And Premises | office | 1 | 1100.56 | 11846 | NIA | 177000 | WATERSIDE 33/11KV | inside-area | 0.71 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 13.4 | Green | 38.1 | 22 | Thermal | 2.5 | 6.3 | 1.4 | 8.8 | 8.5 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | Green (Over 5% headroom) | 17825 | 100 | 1.75 | 77 | 44 | 1714780 | SPN-S000000394382 | 800 | 400 | 40-60% | MAIDSTONE NORTH 132/11KV | 58 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10014306994 | B1 Offices and Workshop businesses | 8451 | D | Natural Gas | 3 | 2 | Air Conditioning | 2021-10-12 |  | 1 | FALSE | 51.2726 | 0.52655 | SPN-S000000008529 | 11036650000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1564 | 27.3 | AYLESHAM AND DISTRICT COMMUNITY CENTRE, ACKHOLT ROAD | CANTERBURY | CT3 3AJ | Dover | AYLESHAM AND DISTRICT COMMUNITY WORKSHOP | Offices And Premises | office | 1 | 1069.4 | 11511 | NIA | 74500 | WINGHAM 33/11KV | inside-area | 2.92 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 7.1 | Green | 22 | 14.7 | Thermal | 0 | 0 | 1.9 | 0 | 2.6 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 21.1 | 16.2 | Winter | 33.1754 | 7 | Green (Over 5% headroom) | 17825 | 100 | 1.7 | 75 | 18 | 823362 | SPN-S000000371221 | 500 | 350 | 60-80% | WINGHAM 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10034883202 | D1 Non-residential Institutions - Community/Day Centre | 298 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2013-06-19 |  | 0.5 | FALSE | 51.2257 | 1.2094 | SPN-S000000008517 | 1749829000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1565 | 27.3 | LINTON PARK PLC, LINTON PARK | MAIDSTONE | ME17 4AB | Maidstone |  | Offices And Premises | office | 1 | 1040.05 | 11195 | NIA | 63000 | SHEPWAY 33/11KV | inside-area | 4.1 | Maidstone Group | Canterbury | Mid Kent Zone | 2.5 | gsp | 10.6 | Green | 36.7 | 25.8 | Thermal | 1.2 | 5.5 | 1.2 | 6.7 | 5.9 | Maidstone Grid 33kV | 40.7 | GREEN | 0 | 2.5 | GREEN | 7 | 303.9 | 4 | 36 | 28.8 | Winter | 29.7222 | 10.7 | Green (Over 5% headroom) | 17825 | 100 | 1.65 | 73 | 47 | 1488074 | SPN-S000000392062 | 200 | 60 | 20-40% | SHEPWAY 33/11KV | 67 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2217 | 0.51611 | SPN-S000000008644 | 3495034000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1566 | 26.6 | PREMIER GROCERY PRODUCTS, KENNINGTON ROAD | ASHFORD | TN24 0LU | Ashford |  | Factory And Premises | industrial | 1 | 28358.38 | 305247 | GIA | 655000 | ASHFORD EAST 33/11KV | inside-area | 0.1 | Sellindge Grid | Sellindge | East Kent Zone | 3.1 | primary | 3.1 | Green | 22.9 | 19.8 | Thermal | 3.5 | 4 | 3 | 7.5 | -0.8 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.2 | 15.9 | Winter | 13.5135 | 3 | Green (Over 5% headroom) | 22103 | 7 | 45.06 | 1702 | 27 | 1659840 | [9 empty] | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.1548 | 0.8982 | SPN-S000000008402 | 6868249000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1567 | 26.3 | ORCHARD HOUSE, ENDEAVOUR PARK, LONDON ROAD | WEST MALLING | ME19 5SH | Tonbridge & Malling |  | Offices And Premises | office | 1 | 1811.42 | 19498 | NIA | 226000 | WROTHAM HEATH 33/11KV | inside-area | 1.45 | Medway Grid | Kingsnorth | West Kent Zone | 1.7 | primary | 1.7 | Green | 16.9 | 14.7 | Thermal | 1.2 | 0 | 1.5 | 1.2 | -1.7 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 16.6 | 13 | Winter | 13.253 | 2.2 | Green (Over 5% headroom) | 12121 | 62 | 2.88 | 127 | 8 | 275679 | SPN-S000000394220 | 315 | 158 | 40-60% | WROTHAM HEATH 33/11KV | 33 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.2982 | 0.35517 | SPN-S000000008519 | 409818148 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1568 | 26.3 | MORRISONS SUPERMARKET, COLDHARBOUR ROAD | GRAVESEND | DA11 8AE | Gravesham |  | Superstore And Premises | bigbox | 2 | 12762.7 | 137376 | GIA | 3200000 | GRAVESEND SOUTH 33/11KV | inside-area | 1.6 | Northfleet East | Northfleet | West Kent Zone | 1 | primary | 1 | Amber | 22.8 | 21.8 | Thermal | 3.8 | 0 | 0 | 3.8 | -0.2 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.2 | Winter | 4.4248 | 1 | Yellow (Between 5% overloaded and 5% headroom) | 7130 | 5 | 20.28 | 1149 | 4 | 311342 | SPN-S000000316978 | 315 | 220 | 60-80% | GRAVESEND SOUTH 33/11KV | 125 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.431 | 0.34791 | SPN-S000000008625 | 15149426000;14788314000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1569 | 26.3 | J SAINSBURY PLC, WINGFIELD BANK, SPRINGHEAD ROAD | GRAVESEND | DA11 8JH | Gravesham |  | Superstore And Premises | bigbox | 1 | 11929.53 | 128408 | GIA | 1990000 | GRAVESEND SOUTH 33/11KV | inside-area | 2.25 | Northfleet East | Northfleet | West Kent Zone | 1 | primary | 1 | Amber | 22.8 | 21.8 | Thermal | 3.8 | 0 | 0 | 3.8 | -0.2 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.2 | Winter | 4.4248 | 1 | Yellow (Between 5% overloaded and 5% headroom) | 7130 | 6 | 18.96 | 1074 | 4 | 320310 | SPN-S000000311478 | 500 | 150 | 20-40% | EBBSFLEET 33/11KV | 118 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4303 | 0.33265 | SPN-S000000008625 | 11267160000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1570 | 25.8 | VAUXHALL INDUSTRIAL ROAD | CANTERBURY | CT1 1HD | Canterbury | PARKER STEEL | Factory And Premises | industrial | 1 | 28709.84 | 309030 | GIA | 815000 | CANTERBURY LOCAL 33/11KV | inside-area | 1.34 | Canterbury South | Canterbury | East Kent Zone | 2.5 | gsp | 3.5 | Green | 23.8 | 20.3 | Thermal | 0 | 8.7 | 24.3 | 8.7 | 3.1 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | Green (Over 5% headroom) | 17825 | 6 | 45.62 | 1723 | 28 | 923095 | SPN-S000000342344 | 800 | 560 | 60-80% | CANTERBURY LOCAL 33/11KV | 139 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 100062279031 | B1 Offices and Workshop businesses | 5033 | C | Natural Gas | 3 | 2 | Air Conditioning | 2019-04-08 |  | 1 | FALSE | 51.2959 | 1.1051 | SPN-S000000008597 | 7683262000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1571 | 25.2 | SNODLAND PAPER MILL, MILL STREET | SNODLAND | ME6 5AT | Tonbridge & Malling |  | Mill And Premises | industrial | 1 | 30765.56 | 331157 | GIA | 895000 | TOWNSEND HOOK 33/6.6KV | inside-area | 0.37 | Medway Grid | Kingsnorth | Mid Kent Zone | 2 | primary | 2 | Green | 13.8 | 10.6 | Thermal | 0 | 0 | 0 | 0 | 2.2 | Medway Grid 33kV | 34.8 | GREEN | 0 |  | RED | 3 | 60.6 | 0 | 13.2 | 12.6 | Winter | 22.7273 | 3 | Green (Over 5% headroom) | 14260 | 4 | 48.89 | 1846 | 23 | 1487784 | SPN-S000000392727 | 500 | 250 | 40-60% | TOWNSEND HOOK 33/6.6KV | 175 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 500 | 0 | 812 | 2023-05 | [12 empty] | 51.3299 | 0.44888 | SPN-S000000008653 | 872520000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1572 | 25 | UNIT H, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Warehouse And Premises | industrial | 2 | 12457.24 | 134088 | GIA | 552500 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 19.8 | 311 | 14 | 416911 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0787 | 1.0127 | SPN-S000000008393 | 10434314000;10434314000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1573 | 25 | OTTERPOOL LANE | HYTHE | CT21 4LP | Folkestone & Hythe | NU-STEEL STRUCTURES | Factory And Premises | industrial | 1 | 7791.34 | 83865 | GIA | 390000 | DYMCHURCH 33/11KV | inside-area | 4.7 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 12.38 | 467 | 14 | 467134 | SPN-S000000361598 | 500 | 350 | 60-80% | HYTHE MAIN 33/11KV | 84 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0777 | 1.0106 | SPN-S000000008393 | 125888145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1574 | 25 | SICO EUROPE LTD LINK PARK, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 4059.27 | 43694 | GIA | 310000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 6.45 | 244 | 14 | 507305 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0787 | 1.0127 | SPN-S000000008393 | 3528440000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1575 | 25 | ALCALINE HOUSE UNITS S-V, LYMPNE INDUSTRIAL ESTATE | HYTHE | CT21 4LR | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 3814.03 | 41054 | GIA | 168000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 6.06 | 95 | 14 | 509945 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0787 | 1.0127 | SPN-S000000008393 | 9683138000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1576 | 25 | UNITS R1-R8, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Cold Store And Premises | industrial | 1 | 3712.91 | 39965 | GIA | 185000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 5.9 | 446 | 14 | 511034 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50011164 | B8 Storage or Distribution | 2080 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2021-09-20 |  | 0.67 | FALSE | 51.0787 | 1.0127 | SPN-S000000008393 | 462386145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1577 | 25 | ASHBY HOUSE & COLD STORE, LINK PARK, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Cold Store And Premises | industrial | 1 | 3506.53 | 37744 | GIA | 275000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 5.57 | 421 | 14 | 513255 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50122044 | B1 Offices and Workshop businesses | 578 | C | LPG | 3 |  | Heating and Natural Ventilation | 2013-05-10 |  | 1 | FALSE | 51.0787 | 1.0127 | SPN-S000000008393 | 14850398000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1578 | 25 | GRD & 1ST FLR DYNA HOUSE EAST, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 2980.85 | 32086 | GIA | 177000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 4.74 | 75 | 14 | 518913 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0787 | 1.0127 | SPN-S000000008393 | 12531028000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1579 | 25 | M C TRUCK & BUS, THE LINK PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Vehicle Repair Workshop And Premises | industrial | 1 | 2880.36 | 31004 | GIA | 242000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 4.58 | 130 | 14 | 519995 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0787 | 1.0127 | SPN-S000000008393 | 2647906000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1580 | 25 | HUSK (UK) LTD THE FREIGHT TERMINAL, LYDDEN HILL | DOVER | CT15 7JW | Dover |  | Storage Depot And Premises | industrial | 1 | 4358.46 | 46914 | GIA | 153000 | LIGHTWEIGHT AGGREGATES | inside-area | 3.95 | Canterbury South | Canterbury | East Kent Zone | -0.6 | primary | -0.6 | Red | 4.4 | 5 | Thermal | 0 | 0 | 0 | 0 | 4.2 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 4.2 | 4.1 | Winter | -14.2857 | -0.6 | Red (More than 5% overloaded) | 0 | 0 | 6.93 | 109 | 4 | 94834 | SPN-S000000363016 | 500 | 250 | 40-60% | LIGHTWEIGHT AGGREGATES | 372 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.1735 | 1.2158 | SPN-S000000008658 | 14289244000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1581 | 25 | ENVIROGRAF HOUSE | DOVER | CT15 7JG | Dover |  | Factory And Premises | industrial | 1 | 2868.41 | 30875 | GIA | 78500 | LIGHTWEIGHT AGGREGATES | inside-area | 1.26 | Canterbury South | Canterbury | East Kent Zone | -0.6 | primary | -0.6 | Red | 4.4 | 5 | Thermal | 0 | 0 | 0 | 0 | 4.2 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 4.2 | 4.1 | Winter | -14.2857 | -0.6 | Red (More than 5% overloaded) | 0 | 0 | 4.56 | 172 | 4 | 110873 | SPN-R000000865801-000-446Z | 315 | 284 | 80-100% | LIGHTWEIGHT AGGREGATES | 88 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | 10034873898 | B2 to B7 General Industrial and Special Industrial Groups | 27 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2014-05-29 |  | 1 | FALSE | 51.2074 | 1.2371 | SPN-S000000008658 | 520789145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1582 | 25 | BEECH GROVE, FOREST DRIVE | DOVER | CT15 4FB | Dover |  | Workshops Nursery School And Premises | industrial | 1 | 2394.5 | 25774 | GIA | 82500 | LIGHTWEIGHT AGGREGATES | inside-area | 2.6 | Canterbury South | Canterbury | East Kent Zone | -0.6 | primary | -0.6 | Red | 4.4 | 5 | Thermal | 0 | 0 | 0 | 0 | 4.2 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 4.2 | 4.1 | Winter | -14.2857 | -0.6 | Red (More than 5% overloaded) | 0 | 0 | 3.81 | 108 | 4 | 115974 | SPN-S000000371076 | 100 | 10 | 0-20% | LIGHTWEIGHT AGGREGATES | 267 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.2281 | 1.2408 | SPN-S000000008658 | 9633208000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1583 | 25 | AB CRUSH PANEL CRAFT LTD FIVE OAKS BUSINESS PARK, GEDDINGE LANE | CANTERBURY | CT4 6RY | Dover |  | Vehicle Repair Workshop And Premises | industrial | 1 | 2068.4 | 22264 | GIA | 130000 | LIGHTWEIGHT AGGREGATES | inside-area | 3.85 | Canterbury South | Canterbury | East Kent Zone | -0.6 | primary | -0.6 | Red | 4.4 | 5 | Thermal | 0 | 0 | 0 | 0 | 4.2 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 4.2 | 4.1 | Winter | -14.2857 | -0.6 | Red (More than 5% overloaded) | 0 | 0 | 3.29 | 93 | 4 | 119484 | SPN-S000000363016 | 500 | 250 | 40-60% | LIGHTWEIGHT AGGREGATES | 60 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.1748 | 1.2108 | SPN-S000000008658 | 14519047000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1584 | 25 | PHASE 20, AMBLEY ROAD, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0NG | Medway |  | Warehouse And Premises | industrial | 1 | 7601.61 | 81823 | GIA | 540000 | RAINHAM 33/11KV | inside-area | 1 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 12.08 | 190 | 9 | 612480 | SPN-S000000312011 | 500 | 350 | 60-80% | RAINHAM 33/11KV | 285 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3536 | 0.58772 | SPN-S000000008462 | 4863379000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1585 | 25 | KENT COUNTY COUNCIL STORAGE & LAND, ASH ROAD | SANDWICH | CT13 9XX | Dover |  | Storage Depot And Premises | industrial | 1 | 6768.5 | 72855 | OTH | 117000 |  | no-geocode | [33 empty] | 10.76 | 169 | [35 empty] | 6357545000
1586 | 25 | BPDM LTD - FORMER BP TRAVEL, ORBITAL PARK | ASHFORD | TN24 1EL | Ashford |  | Warehouse And Premises | industrial | 1 | 5726.7 | 61642 | GIA | 402500 |  | no-geocode | [33 empty] | 9.1 | 143 | [35 empty] | 10521611000
1587 | 25 | ORBITAL MARKETING SERVICES GROUP LIMITED, ORBITAL PARK | ASHFORD | TN24 1EL | Ashford |  | Warehouse And Premises | industrial | 1 | 4818.9 | 51870 | GIA | 390000 |  | no-geocode | [33 empty] | 7.66 | 120 | [35 empty] | 10521583000
1588 | 25 | UNIT 3B, GALLEON BOULEVARD, NEWTONS COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA1 6QL | Dartford |  | Warehouse And Premises | industrial | 1 | 1911.18 | 20572 | GIA | 212000 |  | no-geocode | [33 empty] | 3.04 | 48 | [35 empty] | 867126000
1589 | 25 | CROSSWAYS BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 0QA | Dartford | MICRON | Works And Premises | industrial | 1 | 1874.61 | 20178 | GIA | 275000 |  | no-geocode | [33 empty] | 2.98 | 112 | [35 empty] | 1473949000
1590 | 24 | JOSHNA HOUSE, CROWBRIDGE ROAD, ORBITAL PARK | ASHFORD | TN24 0GR | Ashford |  | Offices And Premises | office | 1 | 1224.45 | 13180 | NIA | 257500 | SEVINGTON 33/11KV | inside-area | 0.42 | Ashford Grid | Sellindge | East Kent Zone | -5.2 | primary | -5.2 | Green | 18 | 15 | Thermal | 1 | 21 | 0 | 22 | 2.9 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | Green (Over 5% headroom) | 0 | 0 | 1.95 | 86 | 28 | 1042245 | SPN-S000000371114 | 1000 | 700 | 60-80% | SEVINGTON 33/11KV | 71 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200001886673 | Offices and Workshop Businesses | 1333 | B | Grid Supplied Electricity | 3 | 2 | Air Conditioning | 2023-01-03 |  | 0.67 | FALSE | 51.1313 | 0.89467 | SPN-S000000008595 | 14251244000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1591 | 23.3 | ASHFORD ROAD | ASHFORD | TN27 0DF | Ashford | ARDO UK LTD | Cold Store And Premises | industrial | 2 | 32028.53 | 344752 | GIA | 2030000 | LITTLE CHART 33/6.6KV | inside-area | 2.62 | Ashford Grid | Sellindge | East Kent Zone | 0.6 | primary | 0.6 | Green | 7 | 6.4 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Ashford Grid 33kV | 33.9 | GREEN | 10 | 99.9 | GREEN | 9 | 385.3 | 1 | 7 | 6.9 | Winter | 8.5714 | 0.6 | Green (Over 5% headroom) | 4278 | 1 | 50.9 | 3843 | 9 | 261586 | SPN-S000000361101 | 315 | 158 | 40-60% | LITTLE CHART 33/6.6KV | 47 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 200001900468 | General Industrial and Special Industrial Groups | 15118 | C | Natural Gas | 4 |  | Heating and Natural Ventilation | 2024-11-25 |  | 1 | FALSE | 51.1945 | 0.80744 | SPN-S000000008428 | 1913114000;1913114000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1592 | 20 | TENTERDEN GARDEN CENTRE, READING STREET | TENTERDEN | TN30 7HT | Ashford |  | Garden Centre And Premises | bigbox | 1 | 4897.4 | 52715 | NIA | 108000 | WITTERSHAM 33/6.6KV | inside-area | 2.85 | Hartley Grid | Ninfield | East Kent Zone | -0.5 | primary | -0.5 | Red | 1.4 | 1.9 | Thermal | 0 | 0 | 0 | 0 | -0.6 | Hartley Grid 33kV | 22.2 | GREEN | 0 | 102.9 | GREEN | 13 | 540.2 | 3 | 1.3 | 1.8 | Winter | -38.4615 | -0.5 | Red (More than 5% overloaded) | 0 | 0 | 7.78 | 441 | 0 | 0 | SPN-S000000362615 | 100 | 10 | 0-20% | WITTERSHAM 33/6.6KV | 135 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 600 | 0 | 0 | 2027-04 | [12 empty] | 51.0418 | 0.74109 | SPN-S000000008531 | 4863612000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1593 | 20 | THE RANGE, FIRS LANE | FOLKESTONE | CT17 4QE | Folkestone & Hythe |  | Retail Warehouse And Premises | bigbox | 1 | 4141.9 | 44583 | GIA | 360000 |  | no-geocode | [33 empty] | 6.58 | 373 | [35 empty] | 9535435000
1594 | 18.3 | MILLBROOK GARDEN CENTRE, STATION ROAD | GRAVESEND | DA13 9PA | Dartford |  | Garden Centre And Premises | bigbox | 1 | 14019.47 | 150904 | NIA | 217000 | GRAVESEND SOUTH 33/11KV | inside-area | 3.29 | Northfleet East | Northfleet | West Kent Zone | 1 | primary | 1 | Amber | 22.8 | 21.8 | Thermal | 3.8 | 0 | 0 | 3.8 | -0.2 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.2 | Winter | 4.4248 | 1 | Yellow (Between 5% overloaded and 5% headroom) | 7130 | 5 | 22.28 | 1262 | 4 | 297814 | SPN-S000000314180 | 200 | -20 | -20-0% | GRAVESEND SOUTH 33/11KV | 247 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | 10023442408 | Retail/Financial and Professional Services | 525 | B | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2026-02-03 |  | 1 | FALSE | 51.4208 | 0.31154 | SPN-S000000008625 | 398331147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1595 | 15.3 | TOLLGATE, WATLING STREET | GRAVESEND | DA13 9RA | Gravesham |  | Offices And Premises | office | 1 | 1039.59 | 11190 | NIA | 71500 | GRAVESEND SOUTH 33/11KV | inside-area | 0.23 | Northfleet East | Northfleet | West Kent Zone | 1 | primary | 1 | Amber | 22.8 | 21.8 | Thermal | 3.8 | 0 | 0 | 3.8 | -0.2 | Northfleet East 33kV | 95.2 | GREEN | 0 | 97 | GREEN | 13 | 552.7 | 3 | 22.6 | 19.2 | Winter | 4.4248 | 1 | Yellow (Between 5% overloaded and 5% headroom) | 7130 | 64 | 1.65 | 73 | 4 | 437528 | SPN-S000000311177 | 500 | 350 | 60-80% | GRAVESEND SOUTH 33/11KV | 90 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 0 | 11.6 | 2028-06 | [12 empty] | 51.4165 | 0.36046 | SPN-S000000008625 | 5408029000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1596 | 15 | UNIT O, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Cold Store And Premises | industrial | 1 | 1783.29 | 19195 | GIA | 108000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 2.83 | 214 | 14 | 531804 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50103511 | B8 Storage or Distribution | 1484 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-03-11 |  | 1 | FALSE | 51.0787 | 1.0127 | SPN-S000000008393 | 126374145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1597 | 15 | UNIT 5 WESTGATE GROUP LTD | ROMNEY MARSH | TN29 0DZ | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1570.43 | 16904 | GIA | 78500 | DYMCHURCH 33/11KV | inside-area | 5.22 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 2.5 | 39 | 14 | 534095 | SPN-R000000839305-000-162Z | 100 | 50 | 40-60% | DYMCHURCH 33/11KV | 93 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.0454 | 0.93102 | SPN-S000000008393 | 12698635000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1598 | 15 | UNIT W, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Factory And Premises | industrial | 1 | 1521.31 | 16375 | GIA | 94000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 2.42 | 91 | 14 | 534624 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50011185 | B1 Offices and Workshop businesses | 1397 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2020-05-18 |  | 1 | FALSE | 51.0787 | 1.0127 | SPN-S000000008393 | 461339145 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1599 | 15 | DAVID IAN FURNITURE BUILDING REAR KENGATE INDUSTRIAL ESTATE 142, DYMCHURCH ROAD | HYTHE | CT21 4LU | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1417.13 | 15254 | GIA | 75500 | DYMCHURCH 33/11KV | inside-area | 4.96 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 2.25 | 35 | 14 | 535745 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 132 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | [12 empty] | 51.08 | 1.0125 | SPN-S000000008393 | 12421704000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1600 | 15 | UNIT 1, IVYCHURCH BUSINESS PARK | ROMNEY MARSH | TN29 0AL | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1321.12 | 14220 | GIA | 71500 | DYMCHURCH 33/11KV | inside-area | 8.43 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 2.1 | 33 | 14 | 536779 | SPN-S000000361795 | 315 | 158 | 40-60% | ROMNEY WARREN 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50100526 | B1 Offices and Workshop businesses | 648 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-10-20 |  | 0.5 | FALSE | 51.0118 | 0.88979 | SPN-S000000008393 | 12341239000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1601 | 15 | UNITS 2&3, IVYCHURCH BUSSINESS PARK, ASHFORD ROAD | ROMNEY MARSH | TN29 0AL | Folkestone & Hythe |  | Warehouse And Premises | industrial | 1 | 1296.44 | 13955 | GIA | 53500 | DYMCHURCH 33/11KV | inside-area | 8.43 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 2.06 | 32 | 14 | 537044 | SPN-S000000361795 | 315 | 158 | 40-60% | ROMNEY WARREN 33/11KV | 107 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50100526 | B1 Offices and Workshop businesses | 648 | D | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2014-10-20 |  | 0.5 | FALSE | 51.0118 | 0.88979 | SPN-S000000008393 | 10368854000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1602 | 15 | UNITS P P1 & P2, LYMPNE INDUSTRIAL PARK | HYTHE | CT21 4LR | Folkestone & Hythe |  | Warehouse, Offices And Premises | industrial | 1 | 1077.3 | 11596 | GIA | 92000 | DYMCHURCH 33/11KV | inside-area | 4.82 | Sellindge Grid | Sellindge | East Kent Zone | -0.2 | primary | -0.2 | Red | 3.8 | 4 | Thermal | 0 | 0 | 0 | 0 | -0.3 | Sellindge Local 33kV | 25.9 | GREEN | 0 | 99.9 | GREEN | 9 | 385.3 | 1 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | Red (More than 5% overloaded) | 0 | 0 | 1.71 | 75 | 14 | 539403 | SPN-S000000371370 | 1000 | 700 | 60-80% | HYTHE MAIN 33/11KV | 72 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 0 | 10 | 2026-08 | 50100777 | Storage or Distribution | 1070 | C | Natural Gas | 3 | 1 | Air Conditioning | 2026-01-12 |  | 0.67 | FALSE | 51.0787 | 1.0127 | SPN-S000000008393 | 1983799000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1603 | 15 | SHELVIN MANOR, SHELVIN FARM ROAD | CANTERBURY | CT4 6RL | Dover |  | Factory And Premises | industrial | 1 | 1479.1 | 15921 | GIA | 60000 | LIGHTWEIGHT AGGREGATES | inside-area | 4 | Canterbury South | Canterbury | East Kent Zone | -0.6 | primary | -0.6 | Red | 4.4 | 5 | Thermal | 0 | 0 | 0 | 0 | 4.2 | Canterbury South 33kV | 66.6 | GREEN | 3 | 2.5 | GREEN | 7 | 303.9 | 4 | 4.2 | 4.1 | Winter | -14.2857 | -0.6 | Red (More than 5% overloaded) | 0 | 0 | 2.35 | 89 | 4 | 125827 | SPN-R000000865801-000-159Z | 200 | 100 | 40-60% | LIGHTWEIGHT AGGREGATES | 323 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 0 | 2031-10 | [12 empty] | 51.1817 | 1.1818 | SPN-S000000008658 | 14986489000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1604 | 15 | IRON MOUNTAIN, OTTERHAM QUAY LANE | GILLINGHAM | ME8 8LL | Medway |  | Storage Depot And Premises | industrial | 1 | 15757.3 | 169610 | GIA | 860000 | RAINHAM 33/11KV | inside-area | 1.64 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 25.04 | 394 | 9 | 524693 | SPN-S000000312103 | 500 | 350 | 60-80% | RAINHAM 33/11KV | 70 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3617 | 0.62094 | SPN-S000000008462 | 10904196000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1605 | 15 | M2 DEPOT FARTHING CORNER, MATTS HILL ROAD | SITTINGBOURNE | ME9 7XA | Medway |  | Storage Depot And Premises | industrial | 1 | 1817.8 | 19567 | GIA | 111000 | RAINHAM 33/11KV | inside-area | 2.69 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 2.89 | 45 | 9 | 674736 | SPN-R000000846208-000-002Z | 100 | 70 | 60-80% | RAINHAM 33/11KV | 82 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.336 | 0.59959 | SPN-S000000008462 | 888746000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1606 | 15 | BEELINE SAME DAY DELIVERY LTD, SEYMOUR ROAD | GILLINGHAM | ME8 8PY | Medway |  | Warehouse And Premises | industrial | 1 | 1595.81 | 17177 | GIA | 88500 | RAINHAM 33/11KV | inside-area | 2.12 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 2.54 | 40 | 9 | 677126 | SPN-S000000316892 | 500 | 350 | 60-80% | RAINHAM 33/11KV | 127 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3603 | 0.62797 | SPN-S000000008462 | 10403695000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1607 | 15 | BREACH LANE | SITTINGBOURNE | ME9 7PE | Swale | BROOKERPAKS | Warehouse And Premises | industrial | 1 | 1326.3 | 14276 | GIA | 46250 | RAINHAM 33/11KV | inside-area | 3.85 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 2.11 | 33 | 9 | 680027 | SPN-R000000846209-000-115Z | 200 | 140 | 60-80% |  | 220 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10093083408 | B2 to B7 General Industrial and Special Industrial Groups | 732 | D | Oil | 3 |  | Heating and Natural Ventilation | 2020-03-01 |  | 1 | FALSE | 51.3602 | 0.65287 | SPN-S000000008462 | 402277147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1608 | 15 | UNITS 17 & 18 MATTS HILL FARM, MATTS HILL ROAD | SITTINGBOURNE | ME9 7UY | Medway |  | Warehouse And Premises | industrial | 1 | 1122.7 | 12085 | GIA | 163000 | RAINHAM 33/11KV | inside-area | 2.85 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 1.78 | 28 | 9 | 682218 | [9 empty] | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3357 | 0.60963 | SPN-S000000008462 | 14814567000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1609 | 15 | WOODGERS WHARF, HORSHAM LANE | SITTINGBOURNE | ME9 7AP | Swale |  | Land, Warehouse And Premises | industrial | 1 | 1084.33 | 11672 | GIA | 31250 | RAINHAM 33/11KV | inside-area | 3.46 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 1.72 | 27 | 9 | 682631 | SPN-S000000393434 | 200 | 100 | 40-60% | RAINHAM 33/11KV | 288 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3769 | 0.63953 | SPN-S000000008462 | 11780649000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1610 | 15 | 194-196, HIGH STREET | GILLINGHAM | ME8 8AX | Medway |  | Vehicle Repair Workshop And Premises | industrial | 1 | 1024.8 | 11031 | GIA | 126000 | RAINHAM 33/11KV | inside-area | 1.33 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 1.63 | 46 | 9 | 683272 | SPN-S000000312094 | 500 | 350 | 60-80% | RAINHAM 33/11KV | 219 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 44105293 | B1 Offices and Workshop businesses | 1006 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-01-15 |  | 1 | FALSE | 51.3615 | 0.61654 | SPN-S000000008462 | 89518147 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1611 | 15 | 11, GALLEON BOULEVARD, NEWTONS COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 0QA | Dartford |  | Computer Centre And Premises | office | 1 | 2578 | 27749 | GIA | 184000 |  | no-geocode | [33 empty] | 4.1 | 180 | [35 empty] | 13478248000
1612 | 15 | MARINER HOUSE, GALLEON BOULEVARD, CROSSWAYS BUSINESS PARK | DARTFORD | DA2 0QA | Dartford | MOAT HOMES LTD | Offices And Premises | office | 1 | 2511.5 | 27034 | NIA | 525000 |  | no-geocode | [33 empty] | 3.99 | 176 | [35 empty] | 10304765000
1613 | 15 | UNIT 3A, GALLEON BOULEVARD, NEWTONS COURT, CROSSWAYS BUSINESS PARK | DARTFORD | DA1 6QL | Dartford |  | Warehouse And Premises | industrial | 1 | 1786.96 | 19235 | GIA | 244000 |  | no-geocode | [33 empty] | 2.84 | 45 | [35 empty] | 867122000
1614 | 9 | CHAMBROS, BAILEY DRIVE, GILLINGHAM BUSINESS PARK | GILLINGHAM | ME8 0BZ | Medway |  | Offices And Premises | office | 1 | 1349.24 | 14523 | NIA | 198000 | RAINHAM 33/11KV | inside-area | 0.32 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 2.14 | 94 | 9 | 679780 | SPN-S000000312048 | 500 | 350 | 60-80% | RAINHAM 33/11KV | 137 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | [12 empty] | 51.3627 | 0.5952 | SPN-S000000008462 | 7716518000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS
1615 | 7.5 | SPADE LANE | SITTINGBOURNE | ME9 7TT | Swale | INTERNATIONAL PROCUREMENT & LOGISTICS | Cold Store And Premises | industrial | 1 | 31822.91 | 342539 | GIA | 2430000 | RAINHAM 33/11KV | inside-area | 2.57 | Sittingbourne Grid | Kemsley | Mid Kent Zone | -1.4 | primary | -1.4 | Red | 22 | 23.4 | Thermal | 0 | 0 | 0 | 0 | -2 | Sittingbourne Grid 33kV | 8.2 | GREEN | 20 | 94.3 | GREEN | 7 | 282.9 | 1 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | Red (More than 5% overloaded) | 0 | 0 | 50.57 | 3819 | 9 | 351764 | SPN-S000000312121 | 500 | 350 | 60-80% |  | 78 |  |  | UKPN secondary sites (modelled headroom band x ONAN rating) | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 0 | 85.7 | 2027-10 | 10035063584 | B1 Offices and Workshop businesses | 65 | G | Grid Supplied Electricity | 3 |  | Heating and Natural Ventilation | 2012-03-29 |  | 1 | FALSE | 51.355 | 0.63353 | SPN-S000000008462 | 15053999000 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS

## Primary substations
primary_floc | primary | hm_name | grid_site | bsp_name | gsp | zone | local_authority | demand_firm_mw | demand_max_mw | headroom_mw | rag_short | limiting_factor | offers_accepted_mw | offers_accepted_n | offers_made_mw | offers_made_n | budget_est_mw | budget_est_n | t6_accepted_mw | t6_pending_mw | t6_budget_mw | ltds_max_24_25_mw | ltds_forecast_29_30_mw | headroom_2030_mw | bsp_firm_mw | bsp_max_mw | bsp_headroom_mw | bsp_constraint | bsp_offers_made_mw | gsp_import_limit_mw | gsp_max_observed_mw | gsp_headroom_mw | gsp_rag | gsp_queue_apps | gsp_queue_mva | gsp_queue_large_demand_mva | gsp_queue_apps_since_2024 | effective_headroom_mw | binding_tier | pipeline_pressure_mw | tx_gsp_region | tx_tec_key | tx_tec_projects | tx_tec_pipeline_mw | tx_tec_storage_mw | tx_tec_gate2_mw | tx_tec_connected_mw | tx_tec_next_date | firm_mva_winter | firm_mva_summer | season | unutilised_pct | headroom_polygon_mw | site_postcode | transformers | trans_rating_winter | source | dno | lat | lon | candidate_sites | candidate_sqft | edge_sqft_supportable
SPN-S000000009377 | LITTLEBROOK PARK 132/11KV | Littlebrook Park 11kV | Littlebrook Park 132/11 |  | Littlebrook | West Kent Zone | Dartford | 60 | 12.2 | 47.8 | Green | Thermal | 10 | 1 | 9.5 | 3 | 0 | 0 | 1.5 | 0 | 0 | 11.3 | 16.1 | 53 |  |  |  |  | 0 |  | 9.84 |  | RED | 2 | 21.5 | 0 | 0 | 47.8 | primary | 19.5 | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 2027-10 | 69.1 | 57.6 | Summer | 79.6875 | 45.9 | DA1 5PT | 0 |  | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4626 | 0.23915 | 8 | 1162279 | 340819
SPN-S000000008508 | CHATHAM WEST 33/11KV (NEW) | Chatham West 11kV | Medway Grid | Medway Grid 33kV | Kingsnorth | Mid Kent Zone | Medway | 72 | 20 | 41.7 | Green | Thermal | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 19.6 | 22.7 | 47.9 | 117 | 74 | 34.8 | GREEN | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 34.8 | bsp | 0 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 70.6 | 58.8 | Summer | 70.068 | 41.2 | ME4 6UQ | 4 | 70.60, 70.60, 70.60, 70.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3775 | 0.51454 | 30 | 1814108 | 248128
SPN-S000000008682 | NEW HYTHE 33/11kV |  | Burham Grid |  | Northfleet | Mid Kent Zone | Tonbridge and Malling | 37.3 |  | 34.5 | Green |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 5.3 | 32 |  |  |  |  | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 34.5 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 37.3 | 29.4 | Winter | 92.4933 | 34.5 | ME20 6TF | 2 | 37.30, 37.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3038 | 0.46124 | 3 | 670043 | 245989
SPN-S000000009320 | MOREHALL 132/11KV | Morehall 132/11kV | Folkestone Total | Folkestone Grid 33kV | Sellindge | East Kent Zone | Folkestone and Hythe | 76.2 | 22 | 40.7 | Green | Thermal | 0 | 0 | 1.6 | 1 | 0 | 0 | 4.5 | 4.5 | 0 | 21.6 | 24.7 | 50 | 78 | 42.7 | 30.2 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 30.2 | bsp | 1.6 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 74.7 | 58.8 | Summer | 67.8571 | 39.9 | CT19 4AY | 0 |  | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0857 | 1.1506 | 35 | 1568738 | 215329
SPN-S000000008616 | MANSTON 33/11KV | Manston 11kV | Richborough Grid | Richborough Grid 33kV | Richborough | East Kent Zone | Thanet | 38.1 | 2.4 | 25.6 | Green | Thermal | 9 | 3 | 41 | 6 | 0 | 0 | 11.5 | 11.5 | 0 | 2.3 | 5.5 | 31.1 | 114.3 | 16.9 | 72.9 | GREEN | 144.9 | 134 | 84.06 | 49.9 | GREEN | 7 | 286.7 | 0 | 3 | 25.6 | primary | 50 | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 100 | 2025-04 | 36.6 | 28.8 | Summer | 92.3611 | 26.6 | CT12 5AU | 2 | 36.60, 36.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.353 | 1.3648 | 5 | 371517 | 182531
SPN-S000000008447 | NORTH SEVENOAKS 33/11KV | North Sevenoaks 11kV | Chelsfield Grid | Chelsfield Grid 33kV | Northfleet | West Kent Zone | Sevenoaks | 45.8 | 20.4 | 25.1 | Green | Thermal | 0 | 0 | 9.2 | 3 | 1.5 | 1 | 9.6 | 5.6 | 1.5 | 20 | 23.8 | 21.1 | 130.3 | 92.3 | 37.7 | GREEN | 45 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 25.1 | primary | 9.2 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 44.9 | 37.6 | Winter | 55.4566 | 24.9 | TN13 3LE | 3 | 44.90, 44.90, 44.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.287 | 0.18641 | 20 | 843047 | 178966
LPN-S000000000715 | CRAYFORD | Crayford 11kV | Dartford Grid 33kV | Dartford Grid A 33kV | Littlebrook | SOUTH EAST | Bexley | 58.5 | 30.7 | 23.1 | Green | Thermal | 3.8 | 1 | 11 | 3 | 0 | 0 | 2 | 2 | 6.5 | 29.8 | 42.5 | 14.2 | 175.5 | 102.9 | 64.9 | GREEN | 139 |  | 9.84 |  | RED | 2 | 21.5 | 0 | 0 | 23.1 | primary | 14.8 | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 2027-10 | 56.7 | 42.8 | Winter | 47.4427 | 26.9 | DA1 4HS | 4 | 56.70, 56.70, 56.70, 56.70 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | LPN | 51.4524 | 0.18051 | 1 | 13300 | 164705
SPN-S000000009525 | KINGSNORTH GRID 11KV | Kingsnorth Grid 11kV | KINGSNORTH GRID 11KV |  | Kingsnorth | Mid Kent Zone | Medway | 38.1 | 9.3 | 22 | Green | Thermal | 0 | 0 | 14.2 | 6 | 5.9 | 3 | 7.5 | 7.5 | 5.9 | 9.1 | 14.9 | 22.4 |  |  |  |  | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 22 | primary | 14.2 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 37.3 | 29.1 | Summer | 74.5704 | 21.7 | ME3 9NQ | 0 |  | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4218 | 0.59532 | 13 | 1333668 | 156862
SPN-S000000008627 | EBBSFLEET 33/11KV | Ebbsfleet 11KV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Dartford | 34 | 11.7 | 20.8 | Green | Thermal | 0 | 0 | 16.1 | 4 | 0 | 0 | 1.2 | 1.2 | 0 | 11.1 | 24.7 | 7.6 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 20.8 | primary | 16.1 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 32.3 | 28.8 | Winter | 65.6347 | 21.2 | DA11 9DT | 2 | 32.30, 32.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4473 | 0.31916 | 8 | 462400 | 148306
SPN-S000000008391 | DOVER 33/11KV | Dover 11kV | Folkestone Total | Folkestone Grid 33kV | Sellindge | East Kent Zone | Dover | 51.8 | 32.5 | 19.3 | Green | Thermal | 0 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 1.2 | 31.2 | 39.5 | 10.2 | 78 | 42.7 | 30.2 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 19.3 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 49.7 | 40.5 | Winter | 37.2233 | 18.5 | CT16 1RH | 4 | 49.70, 49.70, 49.70, 49.70 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1292 | 1.3111 | 40 | 1384421 | 137611
SPN-S000000008525 | RAINHAM MARK 33/11KV | Rainham Mark 11kV | Chatham Grid | Chatham Grid 33kV | Kingsnorth | Mid Kent Zone | Medway | 48 | 20.6 | 19.3 | Green | Thermal | 0 | 0 | 4.3 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 26.2 | 20.4 | 114.3 | 64.7 | 43.2 | GREEN | 17.6 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 19.3 | primary | 4.3 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 46.6 | 34.9 | Summer | 53.8682 | 18.8 | ME8 0PR | 3 | 46.60, 46.60, 46.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3629 | 0.57839 | 38 | 2388245 | 137611
SPN-S000000008367 | ORPINGTON 33/11KV | Orpington 11kV | Bromley Grid 33kV | Bromley Grid 33kV | Hurst | West Kent Zone | Bromley | 45.8 | 27.6 | 18 | Green | Thermal | 1.2 | 1 | 5.4 | 2 | 0 | 0 | 0 | 0 | 0 | 27.3 | 29.9 | 15.4 | 205.7 | 118.5 | 87.2 | GREEN | 0 |  |  |  | RED | 1 | 23 | 23 | 0 | 18 | primary | 6.6 | Northfleet East | HURST | 1 | 228 | 228 | 0 | 0 | 2037-10 | 45.3 | 35.6 | Winter | 39.7351 | 18 | BR5 4AA | 3 | 45.30, 45.30, 45.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3864 | 0.10778 | 0 | 0 | 128342
SPN-S000000009251 | TUNBRIDGE WELLS TOWN 132/6.6kV | Tunbridge Wells Town 6.6kV | Tunbridge Wells Total | Tunbridge Wells Grid 33kV | Northfleet | West Kent Zone | Tunbridge Wells | 39 | 20.3 | 17 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5 | 19.8 | 15.7 | 78 | 34.1 | 36.7 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 17 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 35.5 | 27.3 | Winter | 47.8873 | 17 | TN1 2RL | 0 |  | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1393 | 0.26967 | 14 | 414056 | 121212
SPN-S000000009948 | STROOD 132/11KV | Strood 11kV | STROOD 132/11KV |  | Kingsnorth | Mid Kent Zone | Medway | 60 | 43.9 | 16 | Green | Thermal | 3 | 1 | 5.4 | 3 | 3.8 | 2 | 7 | 3.9 | 0 | 41.7 | 48.7 | 8.3 |  |  |  |  | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 16 | primary | 8.4 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 57 | 57 | Winter | 26.8421 | 15.3 | ME2 4EA | 2 | 57.00, 57.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4001 | 0.49973 | 63 | 3341458 | 114081
SPN-S000000008655 | MARGATE 33/11KV | Margate 11kV | Thanet Grid | Thanet Grid 33kV | Richborough | East Kent Zone | Thanet | 37.1 | 18.8 | 14.8 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 20.6 | 15.8 | 117 | 85.9 | 25.8 | GREEN | 0 | 134 | 84.06 | 49.9 | GREEN | 7 | 286.7 | 0 | 3 | 14.8 | primary | 0 | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 100 | 2025-04 | 36.4 | 27.6 | Winter | 49.4505 | 18 | CT9 5TA | 2 | 36.40, 36.40 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3808 | 1.3795 | 25 | 564611 | 105525
LPN-S000000000716 | DARTFORD GRID B 11KV | Dartford Grid B 11kV | DARTFORD GRID B 11KV |  | Littlebrook | SOUTH EAST | Dartford | 58.5 | 39.3 | 14.5 | Green | Thermal | 16 | 3 | 28.1 | 8 | 0 | 0 | 9.2 | 5.2 | 0 | 37.7 | 46.2 | 10 |  |  |  |  | 0 |  | 9.84 |  | RED | 2 | 21.5 | 0 | 0 | 14.5 | primary | 44.1 | Littlebrook (_C) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 2027-10 | 56.2 | 42.3 | Summer | 32.3877 | 13.7 | UNKNOWN | 0 |  | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | LPN | 51.4498 | 0.21256 | 55 | 2772749 | 103386
SPN-S000000008646 | LORDSWOOD 33/11KV | Lordswood 11KV | Chatham Grid | Chatham Grid 33kV | Kingsnorth | Mid Kent Zone | Medway | 23.9 | 9.8 | 14.1 | Green | Thermal | 0 | 0 | 4.8 | 3 | 0 | 0 | 3.9 | 3.9 | 0 | 9.4 | 9.4 | 13.5 | 114.3 | 64.7 | 43.2 | GREEN | 17.6 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 14.1 | primary | 4.8 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 22.9 | 22.9 | Winter | 58.952 | 13.5 | ME7 3JL | 2 | 22.90, 22.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3478 | 0.54417 | 7 | 457686 | 100534
SPN-S000000008626 | CROSSWAYS | Crossways 11KV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Dartford | 24 | 7.2 | 13.1 | Green | Thermal | 1 | 1 | 8.2 | 2 | 0 | 0 | 0 | 0 | 0 | 7.1 | 10.1 | 13.4 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 13.1 | primary | 9.2 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 23.5 | 17.6 | Winter | 69.7872 | 16.4 | DA9 9BB | 2 | 23.50, 23.50 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4513 | 0.24988 | 36 | 5919301 | 93404
SPN-S000000008368 | QUEENBOROUGH 33/6.6KV | Queenborough 6.6kV | Sheerness Grid | Sheerness Grid 33kV | Kemsley | Mid Kent Zone | Swale | 22.9 | 5.9 | 13 | Green | Thermal | 0 | 0 | 1.5 | 1 | 7.8 | 3 | 0 | 0 | 0 | 5.3 | 8.8 | 11.8 | 58.5 | 21.2 | 29.6 | GREEN | 0 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 13 | primary | 1.5 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 20.6 | 15.5 | Winter | 74.2718 | 15.3 | ME11 5HL | 2 | 20.60, 20.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4138 | 0.74738 | 16 | 1140052 | 92691
SPN-S000000008421 | HYTHE MAIN 33/11KV | Hythe Main 11kV | Folkestone Total | Folkestone Grid 33kV | Sellindge | East Kent Zone | Folkestone and Hythe | 24 | 11.5 | 12.8 | Green | Thermal | 0 | 0 | 10 | 2 | 7.7 | 2 | 0 | 0 | 2.7 | 11.4 | 14.2 | 9.6 | 78 | 42.7 | 30.2 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 12.8 | primary | 10 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 23.8 | 18.8 | Winter | 52.1008 | 12.4 | CT21 5NA | 2 | 23.80, 23.80 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0729 | 1.0929 | 8 | 207355 | 91265
SPN-S000000008458 | PETTS WOOD 33/11KV | Petts Wood 11kV | Bromley Grid 33kV | Bromley Grid 33kV | Hurst | West Kent Zone | Bromley | 22.8 | 10.2 | 12.6 | Green | Thermal | 0 | 0 | 3.7 | 1 | 0 | 0 | 0 | 0 | 0 | 9.8 | 9.4 | 12.5 | 205.7 | 118.5 | 87.2 | GREEN | 0 |  |  |  | RED | 1 | 23 | 23 | 0 | 12.6 | primary | 3.7 | Beddington (_J) | HURST | 1 | 228 | 228 | 0 | 0 | 2037-10 | 21.9 | 19.2 | Winter | 55.2511 | 12.1 | BR5 1DP | 2 | 21.90, 21.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.383 | 0.07437 | 0 | 0 | 89839
SPN-S000000008389 | DEAL 33/11KV | Deal 11kV | Betteshanger Grid | Betteshanger Grid 33kV | Sellindge | East Kent Zone | Dover | 24 | 11.7 | 12.3 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9 | 12.6 | 9.7 | 68.6 | 43.1 | 23.9 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 12.3 | primary | 0 | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 22.3 | 18.6 | Winter | 51.1211 | 11.4 | CT14 9LX | 2 | 22.30, 22.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2262 | 1.3897 | 5 | 126879 | 87700
SPN-S000000008342 | RICHBOROUGH 33/11KV | Richborough 11kV | Richborough Grid | Richborough Grid 33kV | Richborough | East Kent Zone |  | 23.8 | 9.9 | 12.2 | Green | Thermal | 0 | 0 | 0 | 0 | 1.9 | 1 | 0 | 0 | 0 | 9.8 | 14 | 9.6 | 114.3 | 16.9 | 72.9 | GREEN | 144.9 | 134 | 84.06 | 49.9 | GREEN | 7 | 286.7 | 0 | 3 | 12.2 | primary | 0 | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 100 | 2025-04 | 23.6 | 18.9 | Winter | 58.4746 | 13.8 | CT13 9ND | 2 | 23.60, 23.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2923 | 1.3469 | 30 | 1343018 | 86987
SPN-S000000008615 | HALLING 33/11KV | Halling 11kV | Medway Grid | Medway Grid 33kV | Kingsnorth | Mid Kent Zone | Medway | 24 | 8.5 | 12.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 9.9 | 13.1 | 117 | 74 | 34.8 | GREEN | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 12.2 | primary | 0 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 23 | 17.3 | Winter | 64.3478 | 14.8 | ME2 1BA | 2 | 23.00, 23.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3601 | 0.44583 | 4 | 471250 | 86987
SPN-S000000008610 | SINGLETON 33/6.6KV | Singleton 6.6kV | Ashford Grid | Ashford Grid 33kV | Sellindge | East Kent Zone | Ashford | 22.9 | 11 | 11 | Green | Thermal | 0 | 0 | 6.9 | 3 | 0 | 0 | 1.9 | 1.9 | 0 | 10.2 | 15 | 6.3 | 117 | 74.1 | 33.9 | GREEN | 10 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 11 | primary | 6.9 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 21.3 | 16.7 | Winter | 52.1127 | 11.1 | TN23 3AE | 2 | 21.30, 21.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1463 | 0.84718 | 25 | 748114 | 78431
SPN-S000000008322 | BIGGIN HILL 33/11KV | Biggin Hill 11kV | Addington Grid | Addington Grid 33kV | Beddington | Croydon Zone | Bromley | 22.3 | 12 | 10.3 | Green | Thermal | 0 | 0 | 0 | 0 | 5.5 | 2 | 0 | 0 | 0 | 11.4 | 13.7 | 7.5 | 86.9 | 73 | 13.9 | GREEN | 0 |  | 137.05 |  | RED | 7 | 94.8 | 78.8 | 1 | 10.3 | primary | 0 | Beddington (_J) | [7 empty] | 21.2 | 19.6 | Winter | 46.2264 | 9.8 | TN16 3EA | 2 | 21.20, 21.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3179 | 0.032483 | 1 | 48285 | 73440
SPN-S000000009351 | TUNBRIDGE WELLS GRID 132/11 | Tunbridge Wells Grid 11kV | Tunbridge Wells Total | Tunbridge Wells Grid 33kV | Northfleet | West Kent Zone | Tunbridge Wells | 38.1 | 26.5 | 10 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.2 | 34.5 | 1.7 | 78 | 34.1 | 36.7 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 10 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 36.2 | 28.5 | Winter | 30.3867 | 11 | TN2 3GG | 1 | 36.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1448 | 0.27362 | 2 | 56980 | 71301
SPN-S000000008349 | THANET 33/11KV | Thanet 11kV | Thanet Grid | Thanet Grid 33kV | Richborough | East Kent Zone | Thanet | 26 | 12.9 | 9.7 | Green | Thermal | 1 | 1 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 12.5 | 16.5 | 8.7 | 117 | 85.9 | 25.8 | GREEN | 0 | 134 | 84.06 | 49.9 | GREEN | 7 | 286.7 | 0 | 3 | 9.7 | primary | 3.1 | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 100 | 2025-04 | 25.2 | 19.4 | Winter | 50.3968 | 12.7 | CT9 4JA | 3 | 25.20, 25.20, 25.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3679 | 1.3897 | 6 | 230280 | 69162
SPN-S000000008656 | LONGFIELD 33/11KV | Longfield 11kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Dartford | 23 | 10 | 9.3 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.7 | 13.3 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 9.3 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 23 | 17.1 | Summer | 56.1404 | 9.6 | DA3 7QT | 2 | 23.00, 23.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3988 | 0.30349 | 2 | 86664 | 66310
SPN-S000000008511 | GRAVESEND WEST 33/11KV | Gravesend West 11kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Gravesham | 19 | 9.6 | 9.3 | Green | Thermal | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 9.2 | 10.6 | 7.6 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 9.3 | primary | 2 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 18.2 | 16.6 | Winter | 49.4505 | 9 | DA11 9BL | 2 | 18.20, 18.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4505 | 0.32086 | 20 | 477641 | 66310
SPN-S000000008304 | BETTESHANGER LOCAL 33/11KV | Betteshanger Local 11kV | Betteshanger Grid | Betteshanger Grid 33kV | Sellindge | East Kent Zone | Dover | 24 | 14.4 | 8.8 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1 | 15.3 | 8.2 | 68.6 | 43.1 | 23.9 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 8.8 | primary | 0 | Canterbury / RICH_J / Richborough | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 23.5 | 17.1 | Winter | 40 | 9.4 | CT14 0LT | 2 | 23.50, 23.50 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2283 | 1.3437 | 6 | 276735 | 62745
SPN-S000000008544 | STONE MARSHES 33/11KV | Stonemarshes 11kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Dartford | 27.8 | 13.8 | 8.8 | Green | Thermal | 1.5 | 1 | 1 | 1 | 0 | 0 | 2.5 | 2.5 | 0 | 13.2 | 19 | 7.7 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 8.8 | primary | 2.5 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 26.7 | 20.5 | Summer | 40 | 8.2 | DA9 9ED | 2 | 26.70, 26.70 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4439 | 0.25465 | 3 | 206516 | 62745
SPN-S000000008457 | PENSHURST 33/11KV | Penshurst 11kV | Tunbridge Wells Total | Tunbridge Wells Grid 33kV | Northfleet | West Kent Zone | Sevenoaks | 14.9 | 5.9 | 8.8 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 5.3 | 8.9 | 78 | 34.1 | 36.7 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 8.8 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 14.2 | 10.6 | Winter | 60.5634 | 8.6 | TN11 8EN | 2 | 14.20, 14.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1529 | 0.17637 | 2 | 31730 | 62745
SPN-S000000008645 | CHATHAM HILL 33/11KV | Chatham Hill 11kV | Chatham Grid | Chatham Grid 33kV | Kingsnorth | Mid Kent Zone | Medway | 47 | 35.6 | 8.6 | Green | Thermal | 8.2 | 3 | 7 | 2 | 2.8 | 2 | 9.4 | 7 | 2.8 | 34.2 | 39 | 6.1 | 114.3 | 64.7 | 43.2 | GREEN | 17.6 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 8.6 | primary | 15.2 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 45.1 | 32.4 | Winter | 24.1685 | 10.9 | ME5 7AR | 3 | 45.10, 45.10, 45.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3776 | 0.54054 | 26 | 1115742 | 61319
SPN-S000000008504 | TONBRIDGE TOWN 33/6.6KV | Tonbridge Town 6.6kV | Tunbridge Wells Total | Tunbridge Wells Grid 33kV | Northfleet | West Kent Zone | Tonbridge and Malling | 22.8 | 14.2 | 8.6 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6 | 16.6 | 5.3 | 78 | 34.1 | 36.7 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 8.6 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 21.9 | 17.3 | Winter | 37.8995 | 8.3 | TN9 1HS | 2 | 21.90, 21.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1973 | 0.27189 | 51 | 1822916 | 61319
SPN-S000000008494 | STONE 33/11KV | Stone 11kV | Dartford Grid 33kV | Dartford Grid A 33kV | Littlebrook | West Kent Zone | Dartford | 10.2 | 1.9 | 8.3 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 3.1 | 7.1 | 175.5 | 102.9 | 64.9 | GREEN | 139 |  | 9.84 |  | RED | 2 | 21.5 | 0 | 0 | 8.3 | primary | 0 | Northfleet East | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 2027-10 | 10.2 | 10.2 | Winter | 81.3725 | 8.3 | DA2 6AS | 1 | 10.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4425 | 0.24437 | 0 | 0 | 59180
SPN-S000000008444 | SITTINGBOURNE WEST 33/11KV | Sittingbourne West 11kV | Sittingbourne Grid | Sittingbourne Grid 33kV | Kemsley | Mid Kent Zone | Swale | 45.8 | 24.1 | 17.6 | Green | Thermal | 25.8 | 5 | 4.3 | 3 | 0 | 0 | 22.9 | 3 | 0 | 23.4 | 28.1 | 16.3 | 100.6 | 83.9 | 8.2 | GREEN | 20 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 8.2 | bsp | 30.1 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 44.4 | 32.4 | Winter | 47.2973 | 21 | ME10 1JU | 3 | 44.40, 44.40, 44.40 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3413 | 0.71527 | 26 | 1215377 | 58467
SPN-S000000008405 | FAVERSHAM 33/11KV | Faversham 11kV | Sittingbourne Grid | Sittingbourne Grid 33kV | Kemsley | Mid Kent Zone | Swale | 41.3 | 19.4 | 15.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2 | 27.8 | 13.1 | 100.6 | 83.9 | 8.2 | GREEN | 20 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 8.2 | bsp | 0 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 40.9 | 31.7 | Summer | 45.1104 | 14.3 | ME13 8UP | 3 | 40.90, 40.90, 40.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3126 | 0.91158 | 22 | 1094035 | 58467
EPN-S0000000H7013 | PURFLEET PRIMARY | Purfleet Primary 11kV T1 & T2 | Purfleet Grid 33 | Purfleet Grid 33kV | Warley | HAROLD HILL | Thurrock | 21.2 | 11.9 | 7.7 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4 | 12.3 | 8.1 | 114.3 | 75.4 | 23.5 | GREEN | 36.6 | 212.4 | 192.65 | 19.8 | GREEN | 10 | 1007.5 | 609.7 | 2 | 7.7 | primary | 0 | Warley | WARLEY | 8 | 1710.9 | 1710.9 | 0 | 205.9 | 2027-08 | 20.4 | 17 | Summer | 43.5294 | 7.4 | RM19 1SA | 4 | 21.10, 21.10, 21.10, 21.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | EPN | 51.4778 | 0.25729 | 2 | 347507 | 54901
SPN-S000000008483 | SHEERNESS 33/6.6KV | Sheerness 6.6kV | Sheerness Grid | Sheerness Grid 33kV | Kemsley | Mid Kent Zone | Swale | 16 | 8.9 | 7.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 13.7 | 1.7 | 58.5 | 21.2 | 29.6 | GREEN | 0 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 7.2 | primary | 0 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 15.4 | 13.4 | Winter | 44.8052 | 6.9 | ME12 1DB | 2 | 15.40, 15.40 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4372 | 0.74913 | 20 | 829144 | 51336
SPN-S000000008643 | MEREWORTH 33/11KV | Mereworth 11kV | Pembury Grid | Pembury Grid 33kV | Northfleet | Mid Kent Zone | Tonbridge and Malling | 21.2 | 13.6 | 7.1 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9 | 14.3 | 5.8 | 113.1 | 46 | 57 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 7.1 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 20.1 | 17.1 | Winter | 35.8209 | 7.2 | ME18 5JG | 2 | 20.10, 20.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2553 | 0.37069 | 31 | 1004346 | 50623
SPN-S000000008312 | AYLESFORD 33/6.6KV | Aylesford 6.6kV | Burham Grid | Burham Grid 33kV | Northfleet | Mid Kent Zone | Tonbridge and Malling | 29 | 21.9 | 7 | Green | Thermal | 2 | 1 | 4 | 2 | 1 | 0 | 6.1 | 4.1 | 1 | 21.5 | 27 | 1.4 | 90 | 43.6 | 45.6 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 7 | primary | 6 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 28.4 | 28.4 | Winter | 24.2958 | 6.9 | ME20 7JH | 3 | 28.40, 28.40, 28.40 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3007 | 0.46734 | 86 | 5065694 | 49910
SPN-S000000008403 | FARNINGHAM 33/11KV | Farningham 11kV | Chelsfield Grid | Chelsfield Grid 33kV | Northfleet | West Kent Zone | Sevenoaks | 22.9 | 15 | 6.9 | Green | Thermal | 1.1 | 1 | 2.4 | 2 | 0 | 0 | 1.2 | 1.2 | 0 | 15 | 16.5 | 6.4 | 130.3 | 92.3 | 37.7 | GREEN | 45 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.9 | primary | 3.5 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 22.9 | 17.2 | Winter | 34.4978 | 7.9 | DA4 0LD | 2 | 22.90, 22.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3799 | 0.23413 | 8 | 272008 | 49197
SPN-S000000008660 | FOLKESTONE EAST 33/11KV | Folkestone East 11kV | Folkestone Total | Folkestone Grid 33kV | Sellindge | East Kent Zone | Folkestone and Hythe | 22.9 | 16.2 | 6.8 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16.6 | 6.1 | 78 | 42.7 | 30.2 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 6.8 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 22.7 | 17.6 | Winter | 29.5154 | 6.7 | CT19 5NQ | 2 | 22.70, 22.70 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0867 | 1.1849 | 8 | 351210 | 48484
SPN-S000000008496 | SUNDRIDGE 33/11KV | Sundridge 11kV | Chelsfield Grid | Chelsfield Grid 33kV | Northfleet | West Kent Zone | Sevenoaks | 24 | 17.6 | 6.7 | Green | Thermal | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4 | 18.7 | 5.1 | 130.3 | 92.3 | 37.7 | GREEN | 45 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.7 | primary | 2 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 23.8 | 16.9 | Winter | 26.8908 | 6.4 | TN14 6ER | 2 | 23.80, 23.80 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.28 | 0.13385 | 10 | 304435 | 47771
SPN-S000000008454 | PADDOCK WOOD 33/11KV | Paddock Wood 11kV | Pembury Grid | Pembury Grid 33kV | Northfleet | West Kent Zone | Tunbridge Wells | 23 | 16.3 | 6.6 | Green | Thermal | 0 | 0 | 3.7 | 2 | 0 | 0 | 3.7 | 3.7 | 0 | 15.8 | 18.8 | 3.5 | 113.1 | 46 | 57 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.6 | primary | 3.7 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 22.3 | 16.7 | Winter | 29.148 | 6.5 | TN12 6HT | 2 | 22.30, 22.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1774 | 0.39265 | 39 | 1931116 | 47058
SPN-S000000008510 | WESTGATE 33/11KV | Westgate 11kV | Thanet Grid | Thanet Grid 33kV | Richborough | East Kent Zone | Thanet | 22.9 | 16.3 | 6.6 | Green | Thermal | 0 | 0 | 4.6 | 1 | 13 | 3 | 4.6 | 4.6 | 0 | 15.8 | 18.2 | 4 | 117 | 85.9 | 25.8 | GREEN | 0 | 134 | 84.06 | 49.9 | GREEN | 7 | 286.7 | 0 | 3 | 6.6 | primary | 4.6 | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 100 | 2025-04 | 22.2 | 19.4 | Winter | 28.8288 | 6.4 | CT7 9BP | 2 | 22.20, 22.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3751 | 1.3241 | 17 | 815280 | 47058
SPN-S000000008528 | SWANLEY 33/11KV | Swanley 11kV | Chelsfield Grid | Chelsfield Grid 33kV | Northfleet | West Kent Zone | Sevenoaks | 22.8 | 16.3 | 6.6 | Green | Thermal | 0 | 0 | 4.5 | 2 | 0 | 0 | 0 | 0 | 0 | 16.1 | 17.5 | 5.1 | 130.3 | 92.3 | 37.7 | GREEN | 45 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.6 | primary | 4.5 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 22.6 | 17.1 | Winter | 28.7611 | 6.5 | BR8 7QD | 2 | 22.60, 22.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4046 | 0.15891 | 19 | 1072653 | 47058
SPN-S000000008474 | RUSTHALL 33/11KV | Rusthall 11kV | Tunbridge Wells Total | Tunbridge Wells Grid 33kV | Northfleet | West Kent Zone | Tunbridge Wells | 13 | 5.9 | 6.5 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 5.6 | 7.1 | 78 | 34.1 | 36.7 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.5 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 12.7 | 9.2 | Winter | 54.3307 | 6.9 | TN4 8UU | 2 | 12.70, 12.70 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.141 | 0.22914 | 0 | 0 | 46345
SPN-S000000008333 | MEDWAY 33/11KV | Medway 11kV | Medway Grid | Medway Grid 33kV | Kingsnorth | Mid Kent Zone | Tonbridge and Malling | 22.8 | 16.5 | 6.4 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8 | 24.3 | -2.4 | 117 | 74 | 34.8 | GREEN | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 6.4 | primary | 0 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 21.9 | 16.6 | Winter | 27.8539 | 6.1 | ME1 3TS | 2 | 21.90, 21.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3524 | 0.46044 | 5 | 306160 | 45632
SPN-S000000008503 | TONBRIDGE EAST 33/6.6KV | Tonbridge East 6.6kV | Pembury Grid | Pembury Grid 33kV | Northfleet | West Kent Zone | Tonbridge and Malling | 22.9 | 16.6 | 6.3 | Green | Thermal | 0 | 0 | 3.1 | 1 | 2.9 | 1 | 0 | 0 | 0 | 16.1 | 17.4 | 4.8 | 113.1 | 46 | 57 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.3 | primary | 3.1 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 22.2 | 15.7 | Winter | 27.4775 | 6.1 | TN10 4EZ | 2 | 22.20, 22.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2057 | 0.29418 | 24 | 942744 | 44919
SPN-S000000008301 | ADDINGTON LOCAL 33/11KV | Addington Local 11kV | Addington Grid | Addington Grid 33kV | Beddington | West Kent Zone | Croydon | 23 | 16.6 | 6.3 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3 | 22.5 | 0 | 86.9 | 73 | 13.9 | GREEN | 0 |  | 137.05 |  | RED | 7 | 94.8 | 78.8 | 1 | 6.3 | primary | 0 | Beddington (_J) | [7 empty] | 22.5 | 19.4 | Winter | 27.5556 | 6.2 | CR0 5AR | 2 | 22.50, 22.50 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3573 | -0.032551 | 0 | 0 | 44919
SPN-S000000008326 | OXTED 33/11KV | Oxted 11kV | Chelsfield Grid | Chelsfield Grid 33kV | Northfleet | West Kent Zone | Tandridge | 18 | 11.8 | 6.2 | Green | Thermal | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 11.6 | 12 | 5.6 | 130.3 | 92.3 | 37.7 | GREEN | 45 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6.2 | primary | 4 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 17.6 | 16.7 | Winter | 34.0909 | 6 | RH8 0ER | 2 | 17.60, 17.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2553 | 0.004023 | 0 | 0 | 44206
SPN-S000000008492 | STANFORD 33/11KV | Stanford 11kV | Sellindge Grid | Sellindge Local 33kV | Sellindge | East Kent Zone | Folkestone and Hythe | 15.1 | 8.8 | 6.2 | Green | Thermal | 5 | 2 | 7 | 2 | 5 | 1 | 2 | 2 | 0 | 8.5 | 14.9 | -0.3 | 58.5 | 31.2 | 25.9 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 6.2 | primary | 12 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 14.6 | 11.2 | Winter | 41.7808 | 6.1 | TN25 6DW | 2 | 14.60, 14.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1082 | 1.0423 | 5 | 150890 | 44206
SPN-S000000008360 | GOUDHURST 33/11KV | Goudhurst 11kV | Hartley Grid | Hartley Grid 33kV | Ninfield | West Kent Zone | Tunbridge Wells | 13 | 7 | 6 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6.8 | 6.2 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 6 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 13 | 9.7 | Winter | 46.1538 | 6 | TN17 1DP | 2 | 13.00, 13.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1135 | 0.47032 | 7 | 192000 | 42780
SPN-S000000008489 | SOUTH ORPINGTON 33/11KV | South Orpington 11kV | Chelsfield Grid | Chelsfield Grid 33kV | Northfleet | West Kent Zone | Bromley | 22.8 | 16.9 | 6 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7 | 22 | 0.6 | 130.3 | 92.3 | 37.7 | GREEN | 45 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 6 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 22.6 | 19.8 | Winter | 26.1062 | 5.9 | BR6 7EU | 2 | 22.60, 22.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3563 | 0.083431 | 2 | 245930 | 42780
SPN-S000000008522 | SWANSCOMBE 33/11KV | Swanscombe 11kV | Dartford Grid 33kV | Dartford Grid A 33kV | Littlebrook | West Kent Zone | Dartford | 13 | 6.4 | 5.6 | Green | Thermal | 0 | 0 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 6.4 | 4.2 | 8.8 | 175.5 | 102.9 | 64.9 | GREEN | 139 |  | 9.84 |  | RED | 2 | 21.5 | 0 | 0 | 5.6 | primary | 2.5 | Northfleet East | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 2027-10 | 13 | 9.9 | Winter | 50.7692 | 6.6 | DA10 0LL | 3 | 13.00, 13.00, 13.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4525 | 0.30304 | 3 | 247557 | 39928
SPN-S000000008585 | GROVEHURST LOCAL | Grovehurst Local 11kV | Grovehurst |  | Kemsley | Mid Kent Zone | Swale | 24 | 15.9 | 5.3 | Green | Thermal | 0 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 15.6 | 20.7 | 2.8 |  |  |  |  | 0 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 5.3 | primary | 1.2 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 23.5 | 17.5 | Summer | 29.7143 | 5.2 | ME10 2GT | 2 | 23.50, 23.50 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.366 | 0.75379 | 32 | 2967609 | 37789
SPN-S000000008414 | HARRIETSHAM 33/11KV | Harrietsham 11kV | Ashford Grid | Ashford Grid 33kV | Sellindge | Mid Kent Zone | Maidstone | 16 | 10.9 | 5.1 | Green | Thermal | 13.5 | 3 | 0 | 0 | 5.4 | 0 | 0 | 0 | 0 | 10.1 | 11.4 | 3.5 | 117 | 74.1 | 33.9 | GREEN | 10 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 5.1 | primary | 13.5 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 14.9 | 14.9 | Winter | 32.2148 | 4.8 | ME17 2PZ | 2 | 14.90, 14.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2395 | 0.70771 | 6 | 1123433 | 36363
SPN-S000000008478 | ST PETERS 33/11KV | St Peters 11kV | Thanet Grid | Thanet Grid 33kV | Richborough | East Kent Zone | Thanet | 22.8 | 18 | 4.8 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8 | 18.1 | 4.5 | 117 | 85.9 | 25.8 | GREEN | 0 | 134 | 84.06 | 49.9 | GREEN | 7 | 286.7 | 0 | 3 | 4.8 | primary | 0 | Canterbury / RICH_J / Richborough | RICHBOROUGH | 2 | 299 | 299 | 0 | 100 | 2025-04 | 22.6 | 19.4 | Winter | 21.2389 | 4.8 | CT10 3JJ | 2 | 22.60, 22.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3719 | 1.4169 | 32 | 1493813 | 34224
SPN-S000000008433 | MARDEN 33/11KV | Marden 11kV | Hartley Grid | Hartley Grid 33kV | Ninfield | West Kent Zone | Maidstone | 12 | 6.9 | 4.8 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 7.2 | 4.6 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 4.8 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 11.8 | 9 | Winter | 42.3729 | 5 | TN12 9QS | 2 | 11.80, 11.80 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1757 | 0.49056 | 25 | 919268 | 34224
SPN-S000000008365 | HEADCORN 33/6.6KV | Headcorn 6.6kV | Hartley Grid | Hartley Grid 33kV | Ninfield | West Kent Zone | Maidstone | 13 | 8.3 | 4.7 | Green | Thermal | 0 | 0 | 4 | 2 | 2 | 1 | 0 | 0 | 0 | 8.1 | 9.6 | 3.1 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 4.7 | primary | 4 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 12.7 | 9.8 | Winter | 36.2205 | 4.6 | TN27 9QY | 2 | 12.70, 12.70 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1693 | 0.6138 | 7 | 167709 | 33511
SPN-S000000008344 | SITTINGBOURNE TOWN 33/11KV | Sittingbourne Town 11kV | Sittingbourne Grid | Sittingbourne Grid 33kV | Kemsley | Mid Kent Zone | Swale | 26.8 | 16.5 | 4.6 | Green | Thermal | 1.1 | 1 | 7.3 | 5 | 1.2 | 1 | 6.6 | 6.6 | 1.2 | 16.2 | 16.9 | 9.4 | 100.6 | 83.9 | 8.2 | GREEN | 20 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 4.6 | primary | 8.4 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 26.3 | 19.6 | Summer | 34.6939 | 6.8 | ME10 3NN | 2 | 26.30, 26.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3417 | 0.75315 | 59 | 2524025 | 32798
SPN-S000000008470 | ROSHERVILLE 33/6.6KV | Rosherville 6.6kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Gravesham | 19.5 | 15.1 | 4.4 | Green | Thermal | 0 | 0 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 14.6 | 18.3 | 0.6 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 4.4 | primary | 2.4 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 18.9 | 13.6 | Winter | 22.7513 | 4.3 | DA11 9LN | 2 | 18.90, 18.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4421 | 0.35446 | 15 | 1990856 | 31372
SPN-S000000008436 | MINSTER 33/6.6KV | Minster 6.6kV | Sheerness Grid | Sittingbourne Grid 33kV | Kemsley | Mid Kent Zone | Swale | 13.8 | 9 | 4.4 | Green | Thermal | 0 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 8.6 | 8.8 | 4.4 | 100.6 | 83.9 | 8.2 | GREEN | 20 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 4.4 | primary | 2.3 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 13.2 | 10.5 | Winter | 34.8485 | 4.6 | ME12 3PG | 2 | 13.20, 13.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4182 | 0.80228 | 2 | 64703 | 31372
SPN-S000000007371 | TUNBRIDGE WELLS TOWN 11KV | Tunbridge Wells Town 11kV | Tunbridge Wells Total | Tunbridge Wells Grid 33kV | Northfleet | West Kent Zone | Tunbridge Wells | 7.4 | 2.8 | 4.4 | Green | Thermal | 0 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 2.7 | 3.1 | 4.1 | 78 | 34.1 | 36.7 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 4.4 | primary | 5.6 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 7.2 | 6.5 | Winter | 62.5 | 4.5 | TN1 2EZ | 2 | 7.20, 7.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1399 | 0.27071 | 3 | 178054 | 31372
SPN-S000000008408 | FOUR ELMS 33/11KV | Four Elms 11kV | Dormansland Grid | Dormansland Grid 33kV | Northfleet | West Kent Zone | Sevenoaks | 12 | 7.7 | 4.3 | Green | Thermal | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7.5 | 7.1 | 4.5 | 117 | 55.8 | 53.5 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 4.3 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 11.6 | 10.6 | Winter | 35.3448 | 4.1 | TN8 6PA | 2 | 11.60, 11.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.225 | 0.11167 | 10 | 252286 | 30659
SPN-S000000008409 | GRAVESEND TOWN 33/6.6KV | Gravesend Town 6.6kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Gravesham | 18.3 | 14 | 4.3 | Green | Thermal | 3.5 | 2 | 6 | 3 | 1.2 | 0 | 2 | 2 | 1.2 | 13.7 | 16.2 | 1.7 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 4.3 | primary | 9.5 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 17.9 | 16.8 | Winter | 23.4637 | 4.2 | DA12 2SW | 2 | 17.90, 17.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4415 | 0.38395 | 11 | 417926 | 30659
SPN-S000000008513 | WEST WICKHAM 33/11KV | West Wickham 11kV | Addington Grid | Addington Grid 33kV | Beddington | West Kent Zone | Bromley | 23 | 18.8 | 4.2 | Green | Thermal | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 18.2 | 19.6 | 2.7 | 86.9 | 73 | 13.9 | GREEN | 0 |  | 137.05 |  | RED | 7 | 94.8 | 78.8 | 1 | 4.2 | primary | 1 | Beddington (_J) | [7 empty] | 22.3 | 19.4 | Winter | 18.3857 | 4.1 | BR4 9HJ | 2 | 22.30, 22.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3674 | -0.005223 | 0 | 0 | 29946
SPN-S000000008475 | RUXLEY 33/11KV | Ruxley 11kV | Dartford Grid 33kV | Dartford Grid A 33kV | Littlebrook | West Kent Zone | Bromley | 15.2 | 10.9 | 4.2 | Green | Thermal | 0 | 0 | 3 | 1 | 5.6 | 4 | 0 | 0 | 3.2 | 10.8 | 11.4 | 3.6 | 175.5 | 102.9 | 64.9 | GREEN | 139 |  | 9.84 |  | RED | 2 | 21.5 | 0 | 0 | 4.2 | primary | 3 | Littlebrook (_J) | LITTLEBROOK | 3 | 607 | 607 | 0 | 0 | 2027-10 | 15 | 14.6 | Winter | 28 | 4.2 | DA14 5AJ | 2 | 15.00, 15.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4128 | 0.1253 | 0 | 0 | 29946
SPN-S000000008425 | GRAIN 33/11KV | Grain 11kV | Northfleet East | Northfleet East 33kV | Northfleet | Mid Kent Zone | Medway | 7.3 | 3.4 | 3.9 | Green | Voltage | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 3.2 | 4.7 | 2.1 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 3.9 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 6.8 | 6.8 | Winter | 52.9412 | 3.6 | ME3 0AD | 2 | 6.80, 6.80 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4455 | 0.69078 | 3 | 481964 | 27807
SPN-S000000008402 | ASHFORD EAST 33/11KV | Ashford East 11kV | Sellindge Grid | Sellindge Local 33kV | Sellindge | East Kent Zone | Ashford | 22.9 | 19.8 | 3.1 | Green | Thermal | 3.5 | 1 | 4 | 2 | 3 | 0 | 3.5 | 0 | 3 | 19.2 | 23 | -0.8 | 58.5 | 31.2 | 25.9 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 3.1 | primary | 7.5 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 22.2 | 15.9 | Winter | 13.5135 | 3 | TN24 9RD | 2 | 22.20, 22.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1557 | 0.89771 | 28 | 1965087 | 22103
SPN-S000000008587 | EASTCHURCH PRISON 33/6.6KV | Eastchurch Prison 6.6kV | Sheerness Grid | Sheerness Grid 33kV | Kemsley | Mid Kent Zone | Swale | 10 | 5.7 | 3 | Green | Thermal | 0 | 0 | 0 | 0 | 12 | 2 | 0 | 0 | 0 | 5.3 | 7.1 | 2.2 | 58.5 | 21.2 | 29.6 | GREEN | 0 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 3 | primary | 0 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 9.3 | 7 | Winter | 43.0108 | 4 | ME12 4DH | 2 | 9.30, 9.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.398 | 0.85228 | 2 | 63766 | 21390
SPN-S000000008498 | COBHAM 33/11KV | Cobham Kent 11kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Gravesham | 13 | 10 | 3 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 3 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 3 | primary | 0 | Kingsnorth | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 13 | 9.7 | Winter | 23.0769 | 3 | DA12 3BP | 2 | 13.00, 13.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3909 | 0.40476 | 1 | 11849 | 21390
SPN-S000000008363 | HAWKHURST 33/11KV | Hawkhurst 11kV | Hartley Grid | Hartley Grid 33kV | Ninfield | East Sussex Zone | Tunbridge Wells | 15 | 10 | 3 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4 | 10.3 | 3.8 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 3 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 14.1 | 10.6 | Summer | 31.1321 | 3.3 | TN18 5EE | 2 | 14.10, 14.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0518 | 0.50728 | 4 | 114551 | 21390
SPN-S000000008302 | ASHFORD CENTRAL | Ashford Central 6.6kV | Ashford Grid | Ashford Grid 33kV | Sellindge | East Kent Zone | Ashford | 22.9 | 18 | 2.6 | Green | Thermal | 2 | 1 | 9.7 | 5 | 0 | 0 | 5 | 5 | 0 | 18 | 27.2 | -4.3 | 117 | 74.1 | 33.9 | GREEN | 10 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 2.6 | primary | 11.7 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 22.9 | 19.4 | Winter | 21.3974 | 4.9 | TN23 7HQ | 2 | 22.90, 22.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1453 | 0.86816 | 37 | 968238 | 18538
SPN-S000000008517 | WINGHAM 33/11KV | Wingham 11kV | Canterbury South | Canterbury South 33kV | Canterbury | East Kent Zone | Dover | 22 | 14.7 | 7.1 | Green | Thermal | 0 | 0 | 0 | 0 | 1.9 | 1 | 0 | 0 | 0 | 14.1 | 18.5 | 2.6 | 156 | 79.1 | 66.6 | GREEN | 3 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 0 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 21.1 | 16.2 | Winter | 33.1754 | 7 | CT3 3JD | 2 | 21.10, 21.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2518 | 1.2141 | 19 | 834873 | 17825
SPN-S000000008529 | WATERSIDE 33/11KV | Waterside 11kV | Maidstone Group | Maidstone Grid 33kV | Canterbury | Mid Kent Zone | Maidstone | 38.1 | 22 | 13.4 | Green | Thermal | 2.5 | 1 | 6.3 | 3 | 1.4 | 1 | 1.3 | 1.3 | 1.4 | 21.1 | 28.1 | 8.5 | 114.3 | 69 | 40.7 | GREEN | 0 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 8.8 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 36.6 | 28.8 | Winter | 42.3497 | 15.5 | ME14 1JU | 2 | 36.60, 36.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.277 | 0.51911 | 45 | 1726626 | 17825
SPN-S000000008597 | CANTERBURY LOCAL 33/11KV | Canterbury Local 11kV | Canterbury South | Canterbury South 33kV | Canterbury | East Kent Zone | Canterbury | 23.8 | 20.3 | 3.5 | Green | Thermal | 0 | 0 | 8.7 | 4 | 24.3 | 4 | 0 | 0 | 24.3 | 19.7 | 20 | 3.1 | 156 | 79.1 | 66.6 | GREEN | 3 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 8.7 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 23.1 | 17.6 | Winter | 14.7186 | 3.4 | CT2 7RA | 2 | 23.10, 23.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.291 | 1.0874 | 29 | 1232125 | 17825
SPN-S000000008560 | CHARTHAM 33/11KV | Chartham 11kV | Canterbury South | Canterbury South 33kV | Canterbury | East Kent Zone | Canterbury | 15 | 9.4 | 5.2 | Green | Thermal | 0 | 0 | 5.7 | 2 | 0 | 0 | 0 | 0 | 0 | 9 | 8.8 | 5.6 | 156 | 79.1 | 66.6 | GREEN | 3 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 5.7 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 14.4 | 10.6 | Winter | 37.5 | 5.4 | CT4 7JE | 2 | 14.40, 14.40 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2563 | 1.0237 | 5 | 147479 | 17825
SPN-S000000008527 | BARMING 33/11KV | Barming 11kV | Maidstone Group | Maidstone Grid 33kV | Canterbury | Mid Kent Zone | Maidstone | 22.8 | 18.7 | 4.1 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 19.4 | 1.6 | 114.3 | 69 | 40.7 | GREEN | 0 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 0 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 21 | 15.9 | Winter | 18.0952 | 3.8 | ME16 9BX | 2 | 21.00, 21.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2651 | 0.48792 | 4 | 172451 | 17825
SPN-S000000009533 | MAIDSTONE GRID SOUTH | Maidstone Grid South 11kV | Maidstone Group | Maidstone Grid 33kV | Canterbury | Mid Kent Zone | Maidstone | 38.1 | 23.6 | 12.1 | Green | Thermal | 1 | 1 | 5.1 | 3 | 6 | 1 | 3.3 | 3.3 | 0 | 22.9 | 24.5 | 12.5 | 114.3 | 69 | 40.7 | GREEN | 0 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 6.1 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 37 | 29.1 | Winter | 38.1081 | 14.1 | ME14 5DU | 0 |  | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2744 | 0.53299 | 20 | 808784 | 17825
SPN-S000000008644 | SHEPWAY 33/11KV | Shepway 11kV | Maidstone Group | Maidstone Grid 33kV | Canterbury | Mid Kent Zone | Maidstone | 36.7 | 25.8 | 10.6 | Green | Thermal | 1.2 | 1 | 5.5 | 5 | 1.2 | 1 | 2 | 2 | 1.2 | 25.3 | 30.1 | 5.9 | 114.3 | 69 | 40.7 | GREEN | 0 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 6.7 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 36 | 28.8 | Winter | 29.7222 | 10.7 | ME15 8AJ | 2 | 36.00, 36.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2519 | 0.5499 | 48 | 1499269 | 17825
SPN-S000000008516 | WHITSTABLE 33/11KV | Whitstable 11kV | Herne Bay Grid | Herne Bay Grid 33kV | Canterbury | East Kent Zone | Canterbury | 32.9 | 18.4 | 11.8 | Green | Thermal | 8 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 18.2 | 19.4 | 13.2 | 114.3 | 38.4 | 60.5 | GREEN | 0 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 9 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 32.6 | 28.2 | Winter | 44.1718 | 14.4 | CT5 1QF | 2 | 32.60, 32.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3509 | 1.0334 | 12 | 630151 | 17825
SPN-S000000008417 | HERNE BAY 33/11KV | Herne Bay 11kV | Herne Bay Grid | Herne Bay Grid 33kV | Canterbury | East Kent Zone | Canterbury | 46.8 | 17.6 | 24.6 | Green | Thermal | 0 | 0 | 1.5 | 1 | 2.2 | 1 | 1.5 | 1.5 | 2.2 | 17.4 | 22.8 | 23.5 | 114.3 | 38.4 | 60.5 | GREEN | 0 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 1.5 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 46.3 | 34.6 | Winter | 62.419 | 28.9 | CT6 7RY | 3 | 46.30, 46.30, 46.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.354 | 1.0953 | 17 | 777827 | 17825
SPN-S000000008410 | CANTERBURY TOWN 33/11KV | Canterbury Town 11kV | Canterbury South | Canterbury South 33kV | Canterbury | East Kent Zone | Canterbury | 45.7 | 38.8 | 6.9 | Green | Thermal | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 37.2 | 41.8 | 2.1 | 156 | 79.1 | 66.6 | GREEN | 3 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | 2.5 | gsp | 0 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 43.9 | 31.7 | Winter | 15.262 | 6.7 | CT1 1BW | 3 | 43.90, 43.90, 43.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.285 | 1.0853 | 28 | 1058776 | 17825
SPN-S000000008381 | CRANBROOK 33/11KV | Cranbrook 11kV | Hartley Grid | Hartley Grid 33kV | Ninfield | East Sussex Zone | Tunbridge Wells | 6.5 | 4.2 | 2.4 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4.6 | 1.6 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 2.4 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 6.2 | 4.6 | Winter | 35.4839 | 2.2 | TN17 3DQ | 2 | 6.20, 6.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0951 | 0.53325 | 4 | 69855 | 17112
SPN-S000000008502 | ASHFORD WEST 33/6.6KV | Ashford West 6.6kV | Ashford Grid | Ashford Grid 33kV | Sellindge | East Kent Zone | Ashford | 6.5 | 4.1 | 2.4 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3.9 | 2.4 | 117 | 74.1 | 33.9 | GREEN | 10 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 2.4 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 6.3 | 4.8 | Winter | 36.5079 | 2.3 | TN26 3EF | 2 | 6.30, 6.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1475 | 0.74468 | 5 | 98532 | 17112
SPN-S000000008614 | EDENBRIDGE 33/11KV | Edenbridge 11kV | Dormansland Grid | Dormansland Grid 33kV | Northfleet | West Sussex Zone | Sevenoaks | 9.6 | 7.4 | 2.2 | Green | Thermal | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 7.1 | 6.9 | 2.3 | 117 | 55.8 | 53.5 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 2.2 | primary | 0 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 9.2 | 7.1 | Winter | 22.8261 | 2.1 | TN8 6SL | 1 | 9.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.2153 | 0.053633 | 12 | 441973 | 15686
SPN-S000000008485 | SMEETH 33/11KV | Smeeth 11kV | Sellindge Grid | Sellindge Local 33kV | Sellindge | East Kent Zone | Ashford | 3.8 | 0.9 | 2.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 2.9 | 58.5 | 31.2 | 25.9 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 2.2 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 3.8 | 2.7 | Winter | 76.3158 | 2.9 | TN25 6SY | 1 | 3.80 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1062 | 0.94992 | 2 | 41778 | 15686
SPN-S000000008653 | TOWNSEND HOOK 33/6.6KV | Townsend Hook 6.6kV | Medway Grid | Medway Grid 33kV | Kingsnorth | Mid Kent Zone | Tonbridge and Malling | 13.8 | 10.6 | 2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 11 | 2.2 | 117 | 74 | 34.8 | GREEN | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 2 | primary | 0 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 13.2 | 12.6 | Winter | 22.7273 | 3 | ME6 5AT | 2 | 13.20, 13.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3267 | 0.44998 | 24 | 1818941 | 14260
SPN-S000000008476 | RYE 33/11KV | Rye 11kV | Rye Grid | Rye Grid 33kV | Ninfield | East Sussex Zone | Rother | 12.6 | 10.7 | 1.9 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 11.3 | 0.9 | 17.7 | 10.7 | 7 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 1.9 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 12.2 | 9.6 | Winter | 14.7541 | 1.8 | TN31 7HT | 2 | 12.20, 12.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 50.9613 | 0.73132 | 3 | 85301 | 13547
SPN-S000000008469 | ROMNEY WARREN 33/11KV | Romney Warren 11kV | Ruckinge Grid | Ruckinge Grid 33kV | Sellindge | East Kent Zone | Folkestone and Hythe | 13 | 9.9 | 1.7 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 11.3 | 1.6 | 58.5 | 27.9 | 27.4 | GREEN | 9 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 1.7 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 12.9 | 9.9 | Winter | 24.031 | 3.1 | TN28 8BF | 2 | 12.90, 12.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 50.9978 | 0.95856 | 6 | 121079 | 12121
SPN-S000000008519 | WROTHAM HEATH 33/11KV | Wrotham Heath 11kV | Medway Grid | Medway Grid 33kV | Kingsnorth | West Kent Zone | Tonbridge and Malling | 16.9 | 14.7 | 1.7 | Green | Thermal | 1.2 | 1 | 0 | 0 | 1.5 | 1 | 1.2 | 0 | 0 | 14.4 | 18.3 | -1.7 | 117 | 74 | 34.8 | GREEN | 0 |  | 196.35 |  | RED | 3 | 60.6 | 6 | 0 | 1.7 | primary | 1.2 | Kingsnorth | KINGSNORTH | 6 | 3029.5 | 3029.5 | 0 | 812 | 2023-05 | 16.6 | 13 | Winter | 13.253 | 2.2 | TN15 7RR | 2 | 16.60, 16.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3032 | 0.33582 | 9 | 295177 | 12121
SPN-S000000008319 | KENARDINGTON 33/6.6KV | Kenardington 6.6kV | Ruckinge Grid | Ruckinge Grid 33kV | Sellindge | East Kent Zone | Ashford | 7.2 | 5.3 | 1.4 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 5.4 | 1.7 | 58.5 | 27.9 | 27.4 | GREEN | 9 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 1.4 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 7.1 | 4 | Winter | 26.7606 | 1.9 | TN26 2LZ | 2 | 7.10, 7.10 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0602 | 0.81123 | 2 | 29326 | 9982
SPN-S000000008387 | STEEL CROSS 33/6.6KV | Steel Cross 6.6kV | Hartley Grid | Hartley Grid 33kV | Ninfield | West Kent Zone | Wealden | 5.6 | 3.9 | 1.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 4.5 | 1.1 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 1.2 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 5.6 | 3.8 | Winter | 30.3571 | 1.7 | TN6 2XA | 1 | 5.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0665 | 0.18498 | 0 | 0 | 8556
SPN-S000000008507 | WAREHORNE 33/11KV | Warehorne 11kV | Ruckinge Grid | Ruckinge Grid 33kV | Sellindge | East Kent Zone | Ashford | 5 | 3.7 | 1.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 4.4 | 0.5 | 58.5 | 27.9 | 27.4 | GREEN | 9 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 1.2 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 4.9 | 4.5 | Winter | 26.5306 | 1.3 | TN26 2JX | 1 | 4.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0626 | 0.83628 | 4 | 125994 | 8556
SPN-S000000008493 | STAPLEHURST 33/6.6KV | Staplehurst 6.6kV | Hartley Grid | Hartley Grid 33kV | Ninfield | West Kent Zone | Maidstone | 6.5 | 5.4 | 1.1 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 6 | 0.2 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | 1.1 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 6.2 | 4.6 | Winter | 16.129 | 1 | TN12 0SU | 2 | 6.20, 6.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1669 | 0.54478 | 8 | 413902 | 7843
SPN-S000000008376 | TENTERDEN 33/6.6KV | Tenterden 6.6kV | Ruckinge Grid | Ruckinge Grid 33kV | Sellindge | East Sussex Zone | Ashford | 11.9 | 10.7 | 1.1 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3 | 10.6 | 0.8 | 58.5 | 27.9 | 27.4 | GREEN | 9 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 1.1 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 11.4 | 8.7 | Winter | 9.6491 | 1.1 | TN30 6EY | 2 | 11.40, 11.40 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0664 | 0.68666 | 6 | 168710 | 7843
SPN-S000000008625 | GRAVESEND SOUTH 33/11KV | Gravesend South 11kV | Northfleet East | Northfleet East 33kV | Northfleet | West Kent Zone | Gravesham | 22.8 | 21.8 | 1 | Amber | Thermal | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6 | 22.8 | -0.2 | 228.6 | 110.8 | 95.2 | GREEN | 0 | 460 | 363.01 | 97 | GREEN | 13 | 552.7 | 91 | 3 | 1 | primary | 3.8 | Northfleet East | NORTHFLEET EAST | 1 | 49.9 | 49.9 | 0 | 11.6 | 2028-06 | 22.6 | 19.2 | Winter | 4.4248 | 1 | DA11 8NZ | 2 | 22.60, 22.60 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.4183 | 0.35877 | 5 | 448718 | 7130
SPN-S000000008428 | LITTLE CHART 33/6.6KV | Little Chart 6.6kV | Ashford Grid | Ashford Grid 33kV | Sellindge | East Kent Zone | Ashford | 7 | 6.4 | 0.6 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 7.6 | -0.6 | 117 | 74.1 | 33.9 | GREEN | 10 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | 0.6 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 7 | 6.9 | Winter | 8.5714 | 0.6 | TN27 0PS | 2 | 7.00, 7.00 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1795 | 0.77853 | 10 | 606338 | 4278
SPN-S000000008427 | LEYSDOWN 33/6.6KV | Leysdown 6.6kV | Sittingbourne Grid | Sittingbourne Grid 33kV | Kemsley | Mid Kent Zone | Swale | 2.3 | 2.1 | 0.2 | Green | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0.2 | 100.6 | 83.9 | 8.2 | GREEN | 20 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | 0.2 | primary | 0 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 2.2 | 2 | Winter | 9.0909 | 0.2 | ME12 4NA | 1 | 2.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.398 | 0.91014 | 0 | 0 | 1426
SPN-S000000008393 | DYMCHURCH 33/11KV | Dymchurch 11kV | Sellindge Grid | Sellindge Local 33kV | Sellindge | East Kent Zone | Folkestone and Hythe | 3.8 | 4 | -0.2 | Red | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4.1 | -0.3 | 58.5 | 31.2 | 25.9 | GREEN | 0 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | -0.2 | primary | 0 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 3.8 | 2.8 | Summer | -7.1429 | -0.2 | TN29 0NA | 1 | 3.80 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0357 | 1.0041 | 15 | 550999 | 0
SPN-S000000008531 | WITTERSHAM 33/6.6KV | Wittersham 6.6kV | Hartley Grid | Hartley Grid 33kV | Ninfield | East Kent Zone | Ashford | 1.4 | 1.9 | -0.5 | Red | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1.9 | -0.6 | 78 | 55.2 | 22.2 | GREEN | 0 | 490.7 | 387.81 | 102.9 | GREEN | 13 | 540.2 | 11.6 | 3 | -0.5 | primary | 0 | Ninfield | NINFIELD | 6 | 1419.9 | 1419.9 | 0 | 0 | 2027-04 | 1.3 | 1.8 | Winter | -38.4615 | -0.5 | TN30 7HG | 1 | 1.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.0176 | 0.72779 | 1 | 52715 | 0
SPN-S000000008658 | LIGHTWEIGHT AGGREGATES | Lightweight Aggregates 11kV | Canterbury South | Canterbury South 33kV | Canterbury | East Kent Zone | Canterbury | 4.4 | 5 | -0.6 | Red | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 | 4.2 | 156 | 79.1 | 66.6 | GREEN | 3 | 200.9 | 198.38 | 2.5 | GREEN | 7 | 303.9 | 48 | 4 | -0.6 | primary | 0 | Canterbury / RICH_J / Richborough | CANTERBURY NORTH | 1 | 57 | 57 | 0 | 0 | 2031-10 | 4.2 | 4.1 | Winter | -14.2857 | -0.6 | CT15 7JE | 1 | 4.20 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.209 | 1.2192 | 5 | 141748 | 0
SPN-S000000008462 | RAINHAM 33/11KV | Rainham 11kV | Sittingbourne Grid | Sittingbourne Grid 33kV | Kemsley | Mid Kent Zone | Medway | 22 | 23.4 | -1.4 | Red | Thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.7 | 23.3 | -2 | 100.6 | 83.9 | 8.2 | GREEN | 20 | 188.7 | 94.39 | 94.3 | GREEN | 7 | 282.9 | 9.9 | 1 | -1.4 | primary | 0 | Kemsley | KEMSLEY | 2 | 348.9 | 348.9 | 0 | 85.7 | 2027-10 | 21.3 | 17.1 | Winter | -6.5728 | -1.4 | ME8 0DT | 2 | 21.30, 21.30 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.3602 | 0.59746 | 10 | 694303 | 0
SPN-S000000008595 | SEVINGTON 33/11KV | Sevington 11kV | Ashford Grid | Ashford Grid 33kV | Sellindge | East Kent Zone | Ashford | 18 | 15 | -5.2 | Green | Thermal | 1 | 1 | 21 | 3 | 0 | 0 | 0 | 0 | 0 | 18.8 | 20 | 2.9 | 117 | 74.1 | 33.9 | GREEN | 10 | 275.8 | 175.86 | 99.9 | GREEN | 9 | 385.3 | 86 | 1 | -5.2 | primary | 22 | Sellindge | SELLINDGE | 4 | 576 | 576 | 0 | 10 | 2026-08 | 22.9 | 16.9 | Summer | 16.568 | 2.8 | TN24 0HT | 2 | 22.90, 22.90 | UKPN Open Data (live, API key): primary supply areas + capacity heat map + LTDS | SPN | 51.1284 | 0.89077 | 29 | 1055425 | 0

## Method & sources
item | detail
Built | 2026-10-01
Building source | VOA 2026 compiled rating list (epoch 3, 1 Apr 2026), summary valuations record 01: Kent billing authorities; industrial/office >= 1,000 m2, big-box retail/leisure >= 2,000 m2; hereditaments merged where postcode + address match
Power source | UKPN Open Data Portal, live via API key (pulled 2026-10-01): ukpn_primary_postcode_area (supply-area polygons), ukpn-capacity-heatmap (firm, max demand, available capacity, connection offers, budget estimates), LTDS table 3a (observed + forecast demand to 2029/30), LTDS table 6 (connection interest by substation), ukpn-grid-supply-points-overview (GSP import limits), ukpn-large-demand-list (>=5 MVA demand applications by GSP). Kent CC mirror kept only as fallback.
Site points | UKPN primary supply-area layer carries the substation coordinates; Knight Frank mirror used only where missing
Join | Nearest distribution substation within 400 m: UKPN secondary sites (ONAN rating x modelled demand-headroom band), ENWL distribution transformers (published demand headroom kVA) plus nearest 11kV section headroom within 300 m, Northern Powergrid substation sites (rating minus maximum demand). Not available for NGED (coordinates login-only), SSEN or SPEN. This is the test for a 0.3-2 MVA edge node connecting at LV/HV without reinforcement.
lm_* (last-mile tier) | England & Wales non-domestic EPC register (MHCLG 'Get energy performance of buildings data', Sep 2026 bulk extract; latest certificate per UPRN) matched to the VOA row by postcode + address tokens (epc_match_score; floor areas more than 4x apart rejected). Adds UPRN, EPC property type, EPC floor area, rating band, main heating fuel, building level, air-con kW, building environment, lodgement date and a data-centre/server-room flag. Address fields are not republished (OS/Royal Mail licence); UPRN and the rest are OGL.
tx_* (transmission tier) | NESO TEC register (28 Sep 2026): every transmission-contracted generation/storage/hybrid project not yet built, aggregated by connection site and matched to the primary's GSP name — projects, MW pipeline, storage MW, Gate 2 MW, earliest effective date, plus MW already connected. tx_gsp_region = NESO GSP region polygon the primary sits in. NESO publishes no demand-only register; transmission data-centre demand (c.140 projects, ~50 GW) is only in NESO's summary documents.
epc_* (EPC layer) | Building postcode centroid (postcodes.io) located inside the primary supply-area polygon; 'nearest-area' where the centroid fell outside every polygon
headroom_mw | UKPN heat map 'demand available capacity' (MW) at the primary = firm capacity minus maximum demand. headroom_polygon_mw is the older polygon-layer figure (firm x unutilised %) kept for comparison
bsp_headroom_mw / gsp_headroom_mw | same measure at the 33kV bulk supply point feeding the primary, and at the grid supply point (technical import limit winter minus maximum observed flow). Not every GSP publishes a limit (RED = no technical limit available)
effective_headroom_mw | min(primary, BSP, GSP) headroom — the tightest tier UKPN publishes; binding_tier names it. Still excludes transmission (NESO) constraints and connection offers already made
offers_* / budget_est_* / t6_* | demand connection offers accepted / made and budget estimates at the primary (heat map) and the LTDS table-6 breakdown by status: capacity already promised to others but not yet connected. pipeline_pressure_mw = accepted + made
gsp_queue_* | UKPN large-demand list aggregated by GSP: every live demand or storage-import application of 5 MVA and above (count, MVA, how many since 2024)
headroom_2030_mw | LTDS firm capacity minus UKPN's 2029/30 winter demand forecast for the primary — where headroom is heading before any new connections
edge_sqft_supportable_at_headroom | headroom_mw x 7,130 sq ft/MW (edge node: 55% white space, 150 W/sq ft IT, PUE 1.7) — gross floor an edge fit-out could power from local headroom
edge_fitout_whole_building_mva | area_sqft x 147.6 VA/gross sq ft / 1e6 (same edge-node spec, pf 0.95) — what a whole-building edge conversion would need
indicative_existing_kva | area_m2 x benchmark VA/m2 by use (warehouse 25, workshop 45, factory 60, office 70, big-box 90, lab 100, cold store 120) — a proxy for today's agreed supply capacity, which is private to the occupier/UKPN
score | headroom (0-60: min(headroom,20)/20 x 60) + size fit (25 if 20-150k sq ft, 15 if 10-20k or 150-300k, else 7.5) + RAG (Green 15 / Yellow 5 / Red 0)
Caveat 1 | Primary headroom is the binding limit only up to ~10-20 MVA; anything larger is a Grid/BSP or transmission question (NESO queue) and is NOT captured here
Caveat 2 | Supply-area polygons are indicative (built from MPAN postcodes); a building on a boundary may be fed from the neighbouring primary — confirm with a UKPN budget estimate
Caveat 3 | Floor areas are VOA valuation areas (GIA/NIA/other as flagged in 'unit'), not measured surveys