4266 | 12 | ASDA SUPERSTORE, HUYTON LANE | LIVERPOOL | L36 7XF | Knowsley |  | Superstore And Premises | bigbox | 1 | 15586.44 | 167771 | GIA | 1630000 | Bedburn Dv T1 / Bluebell La T1 / Brookbridge T1 / Eccleston T1 | inside-area | 1.67 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 24.77 | 1403 | 7 | 403871 | [9 empty] | Kirkby (_D) | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | [12 empty] | 53.417 | -2.8342 | SPM-BEDBURN_DV_T1_BLUEBELL_LA_T1_BROOKBRIDGE_T1_ECCLESTON_T1 | 12304539000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4267 | 12 | TESCO, THE MEADOW | SANDHURST | GU15 8DX | Bracknell Forest |  | Superstore And Premises | bigbox | 1 | 14144.98 | 152255 | GIA | 2200000 |  | no-geocode | [33 empty] | 22.48 | 1273 | [35 empty] | 12669916000
4268 | 9 | 1, CAMPION PARK, LONDON ROAD | HOLMES CHAPEL | CW4 8AX | Cheshire East |  | Offices And Premises | office | 1 | 1463.91 | 15757 | NIA | 190000 | Sandbach T1 | inside-area | 4.24 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM | -3.2 | bsp | -0.086 | Red | 7.5 | 7.586 | thermal | 0 | 1.6 | 0 | 1.6 | -1.5 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | -3.1663 | RED | 0 |  |  | 0 | 0 | 0 | 7.5 |  |  |  |  | Red (More than 5% overloaded) | 0 | 0 | 2.33 | 102 | 5 | 484611 | [9 empty] | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 0 | 20 | 2027-07 | 10094890085 | B1 Offices and Workshop businesses | 1907 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2019-12-04 |  | 1 | FALSE | 53.1912 | -2.3509 | SPM-SANDBACH_T1 | 12588868000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4269 | 9 | GND FLR NORTHBANK HOUSE, NORTHBANK INDUSTRIAL ESTATE, SIEMENS ROAD | MANCHESTER | M44 5AH | Salford |  | Offices And Premises | office | 1 | 1456.2 | 15674 | NIA | 219000 | Lymm T1 / Whiteleggs La T1 | nearest-substation | 6.6 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM | -3.6 | primary | -3.623 | Red | 10 | 8.623 | thermal | 10 | 3 | 0 | 13 | -0.4 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 2.392 | AMBER | 0 |  |  | 0 | 0 | 0 | 10 |  |  |  |  | Red (More than 5% overloaded) | 0 | 0 | 2.31 | 102 | 68 | 4318221 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 |  | B1 Offices and Workshop businesses | 3229 | C | Natural Gas | 3 |  | Air Conditioning | 2021-07-06 |  | 1 | FALSE | 53.4282 | -2.4339 | SPM-LYMM_T1_WHITELEGGS_LA_T1 | 13544040000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4270 | 9 | (INC 2ND-4TH FLRS 10 EXCHANGE SQUARE) LEVELS 1-6 EXCHANGE HOUSE 12, PRIMROSE STREET | LONDON | EC2R 2BQ | City Of London |  | Offices And Premises | office | 1 | 24860.96 | 267601 | NIA | 11530000 |  | no-geocode | [33 empty] | 39.51 | 1740 | [35 empty] | 13786974000
4271 | 9 | NTT COMMUNICATIONS BUILDING 1 DIGITAL DAGENHAM, YEWTREE AVENUE, RAINHAM ROAD SOUTH | DAGENHAM | RM10 7FU | Barking & Dagenham |  | Computer Centre And Premises | office | 1 | 20475 | 220391 | GIA | 3020000 |  | no-geocode | [33 empty] | 32.54 | 1433 | [35 empty] | 13084624000
4272 | 9 | PT 2ND & 3RD FLRS, THE CAPITAL BUILDING 39, OLD HALL STREET | LIVERPOOL | L3 9PP | Liverpool |  | Offices And Premises | office | 2 | 16628.95 | 178992 | NIA | 2280000 | Ex Bixteth St T1 / Littlewoods T1 / Pall Mall T1 | inside-area | 0.2 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 26.42 | 1164 | 9 | 493303 | [9 empty] | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 0 | 57 | 20 | 2026-09 | 38251179 | B1 Offices and Workshop businesses | 66079 | C | Natural Gas | 5 |  | Air Conditioning | 2022-01-17 |  | 1 | FALSE | 53.4093 | -2.995 | SPM-EX_BIXTETH_ST_T1_LITTLEWOODS_T1_PALL_MALL_T1 | 13467026000;12212094000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4273 | 9 | LEVEL 6 AT 6, GOODS YARD BUILDING, GOODS YARD STREET | MANCHESTER | M3 3PG | Manchester |  | Offices And Premises | office | 2 | 16544.2 | 178080 | NIA | 5350000 |  | no-geocode | [33 empty] | 26.29 | 1158 | [35 empty] | 15088879000;14978560000
4274 | 9 | UNIT 100, CASTLEGATE BUSINESS PARK | CALDICOT | NP26 6TH | Monmouthshire |  | Offices And Premises | office | 3 | 15026.88 | 161748 | GIA | 878500 |  | no-geocode | [33 empty] | 23.88 | 1052 | [35 empty] | 14987347000;10625655000;6639766000
4275 | 9 | 1ST FLR 25, CANNON STREET | LONDON | EC4N 6XD | City Of London |  | Offices And Premises | office | 1 | 1844 | 19849 | NIA | 1190000 |  | no-geocode | [33 empty] | 2.93 | 129 | [35 empty] | 14998474000
4276 | 9 | VIOLET 1 SCI-TECH DARESBURY, KECKWICK LANE | WARRINGTON | WA4 4AB | Halton |  | Offices And Premises | office | 1 | 1815.99 | 19547 | NIA | 322500 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 4.08 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.89 | 127 | 15 | 769034 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | 10093158446 | B1 Offices and Workshop businesses | 2100 | A | Natural Gas | 5 | 2 | Air Conditioning | 2022-01-26 |  | 0.5 | FALSE | 53.3441 | -2.6371 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 13851081000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4277 | 9 | UNIT 2, OVERBROOK LANE, KNOWSLEY INDUSTRIAL PARK SOUTH | PRESCOT | L34 9JA | Knowsley | GOODWIN ASSOCIATES | Offices And Premises | office | 1 | 1809.92 | 19482 | NIA | 99500 | Kelco T1 / News International T1 / News International T2 / Palco T1 / Southdene T1 | inside-area | 1.03 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.88 | 127 | 67 | 4676710 | [9 empty] | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 400 | 0 | 0 | 2027-08 | [12 empty] | 53.461 | -2.8564 | SPM-KELCO_T1_NEWS_INTERNATIONAL_T1_NEWS_INTERNATIONAL_T2_PALCO_T | 526575134 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4278 | 9 | GND & 1ST FLRS TRIDENT 1, STYAL ROAD | MANCHESTER | M22 5WN | Manchester |  | Offices And Premises | office | 1 | 1763.93 | 18987 | NIA | 305000 | Ringway T1 | nearest-substation | 4.34 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.8 | 123 | 120 | 5442602 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3648 | -2.2404 | SPM-RINGWAY_T1 | 13983657000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4279 | 9 | THE LANGLEY BUILDING OFF, SOUTHMOOR ROAD | MANCHESTER | M23 9QZ | Manchester |  | Offices And Premises | office | 1 | 1763.11 | 18978 | NIA | 255000 | Ringway T1 | nearest-substation | 3.59 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.8 | 123 | 120 | 5442611 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3907 | -2.2907 | SPM-RINGWAY_T1 | 5177713000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4280 | 9 | CLAVERTON COURT, CLAVERTON ROAD | MANCHESTER | M23 9NE | Manchester |  | Offices And Premises | office | 1 | 1751.42 | 18852 | NIA | 231000 | Ringway T1 | nearest-substation | 3.29 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.78 | 123 | 120 | 5442737 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 77045756 | B2 to B7 General Industrial and Special Industrial Groups | 1960 | C | Natural Gas | 3 | 1 | Heating and Natural Ventilation | 2019-08-07 |  | 1 | FALSE | 53.3888 | -2.297 | SPM-RINGWAY_T1 | 222277113 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4281 | 9 | THE LANDING, STYAL ROAD | MANCHESTER | M22 5WZ | Manchester |  | Offices And Premises | office | 1 | 1726.56 | 18585 | NIA | 340000 | Ringway T1 | nearest-substation | 4.38 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.74 | 121 | 120 | 5443004 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.365 | -2.2398 | SPM-RINGWAY_T1 | 14990558000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4282 | 9 | PRESTBURY HOUSE 339, STYAL ROAD | MANCHESTER | M22 5LG | Manchester |  | Offices And Premises | office | 1 | 1696.84 | 18265 | NIA | 262500 | Ringway T1 | nearest-substation | 4.47 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.7 | 119 | 120 | 5443324 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 77253287 | B1 Offices and Workshop businesses | 2149 | E | Natural Gas | 4 |  | Air Conditioning | 2014-05-05 |  | 0.5 | FALSE | 53.3663 | -2.2388 | SPM-RINGWAY_T1 | 9985116000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4283 | 9 | GND & 1ST FLRS, WELLINGTON HOUSE AT 38, DELAMERE STREET | CREWE | CW1 2LQ | Cheshire East |  | Offices And Premises | office | 1 | 1677.54 | 18057 | NIA | 129000 | Civic Centre T1 / Claughton Ave T1 / Electricity St T1 | inside-area | 0.62 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.67 | 117 | 15 | 511232 | [9 empty] | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 0 | 20 | 2027-07 | [12 empty] | 53.0979 | -2.4451 | SPM-CIVIC_CENTRE_T1_CLAUGHTON_AVE_T1_ELECTRICITY_ST_T1 | 13518070000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4284 | 9 | PRT 4TH FLR ASHDOWN HSE 123, VICTORIA STREET | LONDON | SW1E 6DB | Westminster City |  | Offices And Premises | office | 1 | 1674 | 18019 | NIA | 1210000 |  | no-geocode | [33 empty] | 2.66 | 117 | [35 empty] | 9071480000
4285 | 9 | 5 MANCHESTER GREEN 333, STYAL ROAD | MANCHESTER | M22 5LG | Manchester |  | Offices And Premises | office | 1 | 1673.5 | 18013 | NIA | 257500 | Ringway T1 | nearest-substation | 4.47 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.66 | 117 | 120 | 5443576 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 77253287 | B1 Offices and Workshop businesses | 2149 | E | Natural Gas | 4 |  | Air Conditioning | 2014-05-05 |  | 0.5 | FALSE | 53.3663 | -2.2388 | SPM-RINGWAY_T1 | 10241454000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4286 | 9 | PT L7 S EXCHANGE HOUSE 12, PRIMROSE STREET | LONDON | EC2R 2BQ | City Of London |  | Offices And Premises | office | 1 | 1648.58 | 17745 | NIA | 945000 |  | no-geocode | [33 empty] | 2.62 | 115 | [35 empty] | 8335763000
4287 | 9 | D C LAW, SOUTHPORT BUSINESS PARK, WIGHT MOSS WAY | SOUTHPORT | PR8 4HQ | Sefton |  | Call Centre And Premises | office | 1 | 1623.1 | 17471 | NIA | 155000 | Ivy St (Southport) T1 / Kensington Rd T1 / Market St T1 / Southport T1 | inside-area | 0.94 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.58 | 114 | 28 | 1138416 | [9 empty] | Lister Drive | KIRKBY | 4 | 514 | 514 | 400 | 0 | 0 | 2027-08 | 41129771 | A1/A2 Retail and Financial/Professional services | 1871 | C | Natural Gas | 3 |  | Air Conditioning | 2015-01-05 |  | 1 | FALSE | 53.6288 | -2.9879 | SPM-IVY_ST_SOUTHPORT_T1_KENSINGTON_RD_T1_MARKET_ST_T1_SOUTHPORT_ | 9404673000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4288 | 9 | 13TH FLR 70, ST MARY AXE | LONDON | EC3A 3BE | City Of London |  | Offices And Premises | office | 1 | 1603 | 17255 | NIA | 1080000 |  | no-geocode | [33 empty] | 2.55 | 112 | [35 empty] | 15100917000
4289 | 9 | THE WHITE HOUSE, WILDERSPOOL BUSINESS PARK, GREENALLS AVENUE | WARRINGTON | WA4 6HL | Warrington |  | Offices And Premises | office | 1 | 1594.88 | 17167 | NIA | 110000 | British Aluminium Latchford T1 / Greenhall Whitley T1 / Latchford T1 / Latchford T2 / Thames Board Mill T1 | inside-area | 1.11 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | SANKEY BRIDGES GT3 / WARRINGTON GT5 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.53 | 112 | 25 | 1054750 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 |  | B1 Offices and Workshop businesses | 2160 | B | Natural Gas | 3 | 2 | Heating and Natural Ventilation | 2021-06-09 |  | 1 | FALSE | 53.3748 | -2.5844 | SPM-BRITISH_ALUMINIUM_LATCHFORD_T1_GREENHALL_WHITLEY_T1_LATCHFOR | 2807701000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4290 | 9 | PT LGND & PT GND FLRS AREA B THE CAPITAL BUILDING 39, OLD HALL STREET | LIVERPOOL | L3 9PP | Liverpool |  | Offices And Premises | office | 1 | 1555.7 | 16745 | NIA | 180000 | Ex Bixteth St T1 / Littlewoods T1 / Pall Mall T1 | inside-area | 0.2 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.47 | 109 | 9 | 655550 | [9 empty] | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 0 | 57 | 20 | 2026-09 | 38251179 | B1 Offices and Workshop businesses | 66079 | C | Natural Gas | 5 |  | Air Conditioning | 2022-01-17 |  | 1 | FALSE | 53.4093 | -2.995 | SPM-EX_BIXTETH_ST_T1_LITTLEWOODS_T1_PALL_MALL_T1 | 15116145000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4291 | 9 | 2ND FLR ATLANTIC HOUSE, ATLAS BUSINESS PARK, SIMONSWAY | MANCHESTER | M22 5PR | Manchester |  | Offices And Premises | office | 1 | 1554.6 | 16734 | NIA | 270000 | Ringway T1 | nearest-substation | 4.11 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.47 | 109 | 120 | 5444855 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 10090665030 | B1 Offices and Workshop businesses | 5371 | D | Natural Gas | 5 | 2 | Air Conditioning | 2018-05-11 |  | 1 | FALSE | 53.3719 | -2.2468 | SPM-RINGWAY_T1 | 8759521000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4292 | 9 | 3, PENMAN WAY | LEICESTER | LE19 1FA | Blaby |  | Offices And Premises | office | 1 | 1540.16 | 16578 | NIA | 215000 |  | no-geocode | [33 empty] | 2.45 | 108 | [35 empty] | 6117520000
4293 | 9 | LAKE VIEW, KINGS BUSINESS PARK, LIVERPOOL ROAD | PRESCOT | L34 1PJ | Knowsley | KNOWSLEY HOUSING TRUST | Offices And Premises | office | 1 | 1533.32 | 16505 | NIA | 215000 | Bedburn Dv T1 / Bluebell La T1 / Brookbridge T1 / Eccleston T1 | inside-area | 0.73 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.44 | 107 | 7 | 555137 | [9 empty] | Kirkby (_D) | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | [12 empty] | 53.4241 | -2.8264 | SPM-BEDBURN_DV_T1_BLUEBELL_LA_T1_BROOKBRIDGE_T1_ECCLESTON_T1 | 4839717000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4294 | 9 | PT GND 1ST & 2ND FLRS BUILDING ONE AT 341, STYAL ROAD | MANCHESTER | M22 5LG | Manchester |  | Offices And Premises | office | 1 | 1520.24 | 16364 | NIA | 237000 | Ringway T1 | nearest-substation | 4.47 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.42 | 106 | 120 | 5445225 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 77253287 | B1 Offices and Workshop businesses | 2149 | E | Natural Gas | 4 |  | Air Conditioning | 2014-05-05 |  | 0.5 | FALSE | 53.3663 | -2.2388 | SPM-RINGWAY_T1 | 15053438000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4295 | 9 | AT SARN Y MYNACH | COLWYN BAY | LL28 5EL | Conwy |  | Car Sales Land Office And Premises | office | 1 | 1490 | 16038 | OTH | 18750 |  | no-geocode | [33 empty] | 2.37 | 104 | [35 empty] | 6625519000
4296 | 9 | PT L7 N EXCHANGE HOUSE 12, PRIMROSE STREET | LONDON | EC2R 2BQ | City Of London |  | Offices And Premises | office | 1 | 1453.87 | 15649 | NIA | 835000 |  | no-geocode | [33 empty] | 2.31 | 102 | [35 empty] | 8335767000
4297 | 9 | DANIELLE HOUSE, LEDSON ROAD | MANCHESTER | M23 9GP | Manchester |  | Offices And Premises | office | 1 | 1381.81 | 14874 | NIA | 139000 | Ringway T1 | nearest-substation | 3.81 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.2 | 97 | 120 | 5446715 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 77240973 | Offices and Workshop Businesses | 1789 | C | Natural Gas | 3 |  | Heating and Natural Ventilation | 2024-07-26 |  | 1 | FALSE | 53.3931 | -2.293 | SPM-RINGWAY_T1 | 8340173000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4298 | 9 | MENTAL HEALTH RESOURCE CENTRE, SEASIDERS WAY | BLACKPOOL | FY1 6TX | Blackpool |  | Offices And Premises | office | 1 | 1370.3 | 14750 | NIA | 150000 |  | no-geocode | [33 empty] | 2.18 | 96 | [35 empty] | 8538148000
4299 | 9 | 8TH FL 10, BLOOMSBURY WAY | LONDON | WC2A 2SL | Camden |  | Offices And Premises | office | 1 | 1366 | 14703 | NIA | 955000 |  | no-geocode | [33 empty] | 2.17 | 96 | [35 empty] | 12606369000
4300 | 9 | CAPITAL HOUSE 335, STYAL ROAD | MANCHESTER | M22 5LG | Manchester |  | Offices And Premises | office | 1 | 1357.56 | 14613 | NIA | 210000 | Ringway T1 | nearest-substation | 4.47 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.16 | 95 | 120 | 5446976 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 77253287 | B1 Offices and Workshop businesses | 2149 | E | Natural Gas | 4 |  | Air Conditioning | 2014-05-05 |  | 0.5 | FALSE | 53.3663 | -2.2388 | SPM-RINGWAY_T1 | 9985104000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4301 | 9 | UNITS 1 2 & 3, GALWAY CRESCENT | ST HELENS | WA11 0GR | St Helens |  | Offices And Premises | office | 1 | 1326.8 | 14282 | NIA | 159000 | Almatex T1 / St Helens Wwtw T1 / Watery La T2 / Ex Delta Metals T1 | nearest-substation | 3.2 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.11 | 93 | 70 | 5822426 | [9 empty] | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | 39084212 | Offices and Workshop Businesses | 466 | B | Natural Gas | 3 | 1 | Air Conditioning | 2024-09-05 |  | 0.75 | FALSE | 53.4723 | -2.6652 | SPM-ALMATEX_T1_ST_HELENS_WWTW_T1_WATERY_LA_T2_EX_DELTA_METALS_T1 | 9018004000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4302 | 9 | FIRST FLOOR, THE ALDERMANBURY, GODWIN STREET | BRADFORD | BD1 2SE | Bradford |  | Offices And Premises | office | 1 | 1311.56 | 14118 | NIA | 55000 |  | no-geocode | [33 empty] | 2.08 | 92 | [35 empty] | 10735230000
4303 | 9 | REGUS UK LTD 3000 MANCHESTER BUSINESS PARK, AVIATOR WAY | MANCHESTER | M22 5TG | Manchester |  | Offices And Premises | office | 1 | 1310.68 | 14108 | NIA | 270000 | Ringway T1 | nearest-substation | 2.8 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.08 | 92 | 120 | 5447481 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 10090665250 | Offices and Workshop Businesses | 6755 | D | Natural Gas | 3 |  | Air Conditioning | 2022-11-21 |  | 1 | FALSE | 53.3673 | -2.2651 | SPM-RINGWAY_T1 | 6032210000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4304 | 9 | HM CUSTOMS & EXCISE (PROVIDED), TERMINAL 1, MANCHESTER AIRPORT | MANCHESTER | M90 3HA | Manchester |  | Offices And Premises | office | 1 | 1296.93 | 13960 | NIA | 397500 | Ringway T1 | inside-area | 2.13 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.06 | 91 | 120 | 5447629 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3623 | -2.2734 | SPM-RINGWAY_T1 | 897805000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4305 | 9 | 9TH FLR 10, FLEET PLACE | LONDON | EC2M 7RB | City Of London |  | Offices And Premises | office | 1 | 1292.56 | 13913 | NIA | 645000 |  | no-geocode | [33 empty] | 2.05 | 90 | [35 empty] | 14569276000
4306 | 9 | FOODBANK AT FORMER LIBRARY SHIRE HALL COMPLEX, RAIKES LANE | MOLD | CH7 6ZZ | Flintshire |  | Offices And Premises | office | 1 | 1290.02 | 13886 | NIA | 77000 |  | no-geocode | [33 empty] | 2.05 | 90 | [35 empty] | 10258822000
4307 | 9 | PRACTICE PLAN, CAMBRIAN WORKS, GOBOWEN ROAD | OSWESTRY | SY11 1HS | Shropshire |  | Offices And Premises | office | 1 | 1286.85 | 13852 | NIA | 140000 | Coney Green T1 / Oswestry T2 / Oswestry T1 | inside-area | 2.46 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.04 | 90 | 15 | 576605 | [9 empty] | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 0 | 2024-08 | 10007021401 | Offices and Workshop Businesses | 1344 | C | Grid Supplied Electricity | 3 |  | Air Conditioning | 2025-05-28 |  | 1 | FALSE | 52.8629 | -3.0477 | SPM-CONEY_GREEN_T1_OSWESTRY_T2_OSWESTRY_T1 | 9126784000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4308 | 9 | 1ST FLOOR VISTORM HOUSE 3200, DARESBURY PARK | WARRINGTON | WA4 4BU | Halton |  | Offices And Premises | office | 1 | 1267.6 | 13644 | NIA | 182000 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 4.56 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2.01 | 89 | 15 | 774937 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | 10010612110 | Offices and Workshop Businesses | 3790 | B | Grid Supplied Electricity | 3 |  | Air Conditioning | 2023-08-18 |  | 1 | FALSE | 53.3294 | -2.6455 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 2475541000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4309 | 9 | 2ND FLR AT 1100, DARESBURY PARK | WARRINGTON | WA4 4AG | Halton |  | Offices And Premises | office | 1 | 1258.8 | 13550 | NIA | 185000 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 3.2 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 2 | 88 | 15 | 775031 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | [12 empty] | 53.338 | -2.6254 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 12483805000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4310 | 9 | 2ND FLR OFFICES NORTH STAND, BLACKPOOL STADIUM, SEASIDERS WAY | BLACKPOOL | FY1 6TX | Blackpool |  | Offices And Premises | office | 1 | 1237.21 | 13317 | NIA | 135000 |  | no-geocode | [33 empty] | 1.97 | 87 | [35 empty] | 14237524000
4311 | 9 | 2ND FLR 3100, DARESBURY PARK | WARRINGTON | WA4 4BT | Halton |  | Offices And Premises | office | 1 | 1222.4 | 13158 | NIA | 175000 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 4.58 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.94 | 86 | 15 | 775423 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | 10090872166 | A1/A2 Retail and Financial/Professional services | 4086 | D | Grid Supplied Electricity | 4 |  | Mixed-mode with Mechanical Ventilation | 2012-06-14 |  | 1 | FALSE | 53.3304 | -2.6459 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 14264760000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4312 | 9 | 2ND FLR DAKOTA HOUSE CONCORD BUSINESS PARK, THREAPWOOD ROAD | MANCHESTER | M22 5LA | Manchester |  | Offices And Premises | office | 1 | 1205.27 | 12973 | NIA | 192000 | Ringway T1 | nearest-substation | 3.93 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.92 | 84 | 120 | 5448616 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3715 | -2.2495 | SPM-RINGWAY_T1 | 15040809000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4313 | 9 | STRATUS HOUSE, SOUTHMOOR ROAD | MANCHESTER | M23 9XB | Manchester |  | Offices And Premises | office | 1 | 1199.57 | 12912 | NIA | 163000 | Ringway T1 | nearest-substation | 4.19 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.91 | 84 | 120 | 5448677 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3967 | -2.294 | SPM-RINGWAY_T1 | 15099681000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4314 | 9 | SHERIFFS COURT, GREYFRIARS ROAD | COVENTRY | CV1 3PU | Coventry |  | Offices And Premises | office | 1 | 1199.5 | 12911 | NIA | 159000 |  | no-geocode | [33 empty] | 1.91 | 84 | [35 empty] | 2260925000
4315 | 9 | GND FLR 1100 DARESBURY PARK, DARESBURY PARK | WARRINGTON | WA4 4AG | Halton |  | Offices And Premises | office | 1 | 1173.4 | 12630 | NIA | 173000 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 3.2 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.86 | 82 | 15 | 775951 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | [12 empty] | 53.338 | -2.6254 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 12656638000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4316 | 9 | ROBINSON HOUSE 8-9, WYCH ELM | HARLOW | CM20 0QR | Harlow |  | Offices And Premises | office | 1 | 1144.27 | 12317 | NIA | 74000 |  | no-geocode | [33 empty] | 1.82 | 80 | [35 empty] | 13049219000
4317 | 9 | 4TH FLR 4, THOMAS MORE SQUARE | LONDON | EC1W 1YW | Tower Hamlets |  | Offices And Premises | office | 1 | 1124.8 | 12107 | NIA | 365000 |  | no-geocode | [33 empty] | 1.79 | 79 | [35 empty] | 9436227000
4318 | 9 | PERSTORPS UK LTD, ADMINISTRATIVE OFFICES, BARONET ROAD | WARRINGTON | WA4 6HA | Warrington |  | Offices And Premises | office | 1 | 1123.2 | 12090 | NIA | 80000 | British Aluminium Latchford T1 / Greenhall Whitley T1 / Latchford T1 / Latchford T2 / Thames Board Mill T1 | inside-area | 2.4 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | SANKEY BRIDGES GT3 / WARRINGTON GT5 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.78 | 79 | 25 | 1059827 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3706 | -2.6035 | SPM-BRITISH_ALUMINIUM_LATCHFORD_T1_GREENHALL_WHITLEY_T1_LATCHFOR | 10190260000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4319 | 9 | DWP, FORUM SQUARE | MANCHESTER | M22 5RT | Manchester |  | Offices And Premises | office | 1 | 1105.45 | 11899 | NIA | 136000 | Ringway T1 | nearest-substation | 3.42 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.76 | 77 | 120 | 5449690 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3796 | -2.266 | SPM-RINGWAY_T1 | 12193477000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4320 | 9 | 1ST FLR 10, GROSVENOR STREET | LONDON | W1K 4DH | Westminster City |  | Offices And Premises | office | 1 | 1099.41 | 11834 | NIA | 1260000 |  | no-geocode | [33 empty] | 1.75 | 77 | [35 empty] | 11352769000
4321 | 9 | 1ST FLR SOUTHMOOR HOUSE SOUTHMOOR INDUSTRIAL ESTATE, SOUTHMOOR ROAD | MANCHESTER | M23 9LR | Manchester |  | Offices And Premises | office | 1 | 1094.4 | 11780 | NIA | 160000 | Ringway T1 | nearest-substation | 3.62 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.74 | 77 | 120 | 5449809 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.3915 | -2.294 | SPM-RINGWAY_T1 | 12223566000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4322 | 9 | TOWN HALL, CROWN SQUARE | DENBIGH | LL16 3TB | Denbighshire |  | Offices And Premises | office | 1 | 1088.95 | 11721 | NIA | 32500 | Bryn Stanley T1 / Denbigh T1 | inside-area | 2.63 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.73 | 76 | 5 | 115916 | [9 empty] | Connahs Quay / SASA | [20 empty] | 53.1841 | -3.4195 | SPM-BRYN_STANLEY_T1_DENBIGH_T1 | 4377160000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4323 | 9 | 34, ARTHUR STREET | OSWESTRY | SY11 1JN | Shropshire | SHROPSHIRE COUNCIL | Offices, Office And Premises | office | 1 | 1068.7 | 11503 | NIA | 69000 | Coney Green T1 / Oswestry T2 / Oswestry T1 | inside-area | 3.09 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.7 | 75 | 15 | 578954 | [9 empty] | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 0 | 2024-08 | 100071367689 | B1 Offices and Workshop businesses | 330 | E | Natural Gas | 3 |  | Heating and Natural Ventilation | 2019-04-02 |  | 1 | FALSE | 52.8606 | -3.0562 | SPM-CONEY_GREEN_T1_OSWESTRY_T2_OSWESTRY_T1 | 7360818000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4324 | 9 | UNIT 4 TRIGG HOUSE, WARREN DRIVE | PRESTATYN | LL19 7HX | Denbighshire |  | Offices And Premises | office | 1 | 1067.48 | 11490 | NIA | 57500 | Church La T1 / Nant Hall T1 / Prestatyn T1 | inside-area | 0.69 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.7 | 75 | 2 | 100735 | [9 empty] | Connahs Quay / SASA | [20 empty] | 53.3418 | -3.3891 | SPM-CHURCH_LA_T1_NANT_HALL_T1_PRESTATYN_T1 | 9560663000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4325 | 9 | 25-26, LOVAT LANE | LONDON | EC3R 8ED | City Of London |  | Offices And Premises | office | 1 | 1063.95 | 11452 | OTH | 410000 |  | no-geocode | [33 empty] | 1.69 | 74 | [35 empty] | 8638076000
4326 | 9 | 4TH & 5TH FLRS 30, OLD BROAD STREET | LONDON | EC2M 1HQ | City Of London |  | Offices And Premises | office | 1 | 1060.7 | 11417 | NIA | 555000 |  | no-geocode | [33 empty] | 1.69 | 74 | [35 empty] | 14982390000
4327 | 9 | UNIT 5400, DARESBURY PARK | WARRINGTON | WA4 4GE | Halton |  | Offices And Premises | office | 1 | 1058.76 | 11396 | NIA | 149000 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 4.31 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.68 | 74 | 15 | 777185 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | 10093157469 | D1 Non-residential Institutions - Primary Health Care Building | 1210 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2021-03-22 |  | 1 | FALSE | 53.3321 | -2.6421 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 9218029000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4328 | 9 | 6TH-7TH FLRS 25, VICTORIA STREET | LONDON | SW1E 0EX | Westminster City |  | Offices And Premises | office | 1 | 1055.28 | 11359 | NIA | 710000 |  | no-geocode | [33 empty] | 1.68 | 74 | [35 empty] | 15053251000
4329 | 9 | 2, SOUTHPORT BUSINESS PARK, WIGHT MOSS WAY | SOUTHPORT | PR8 4HQ | Sefton |  | Offices And Premises | office | 1 | 1047.34 | 11273 | NIA | 102000 | Ivy St (Southport) T1 / Kensington Rd T1 / Market St T1 / Southport T1 | inside-area | 0.94 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 1.66 | 73 | 28 | 1144614 | [9 empty] | Lister Drive | KIRKBY | 4 | 514 | 514 | 400 | 0 | 0 | 2027-08 | 41129771 | A1/A2 Retail and Financial/Professional services | 1871 | C | Natural Gas | 3 |  | Air Conditioning | 2015-01-05 |  | 0.75 | FALSE | 53.6288 | -2.9879 | SPM-IVY_ST_SOUTHPORT_T1_KENSINGTON_RD_T1_MARKET_ST_T1_SOUTHPORT_ | 4213431000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4330 | 9 | (& 35-41 NEW BROAD ST) LGND FL NEW BROAD ST HSE 81-89, OLD BROAD STREET | LONDON | EC2N 1PR | City Of London |  | Offices And Premises | office | 1 | 1045.6 | 11255 | NIA | 285000 |  | no-geocode | [33 empty] | 1.66 | 73 | [35 empty] | 14044453000
4331 | 9 | (& 35-41 NEW BROAD ST) PT 4TH F WEST NEW BROAD ST HSE 81-89, OLD BROAD STREET | LONDON | EC2N 1PR | City Of London |  | Offices And Premises (Dabw) | office | 1 | 1039.75 | 11192 | NIA | 387500 |  | no-geocode | [33 empty] | 1.65 | 73 | [35 empty] | 8572440000
4332 | 9 | BRUEL & KJAER (UK) LTD HARROW WEALD LODGE 92, UXBRIDGE ROAD | HARROW | HA3 6ZZ | Harrow |  | Offices And Premises | office | 1 | 1025.3 | 11036 | NIA | 255000 |  | no-geocode | [33 empty] | 1.63 | 72 | [35 empty] | 574252065
4333 | 9 | 1ST F 90, QUEEN VICTORIA STREET | LONDON | EC4N 4LX | City Of London |  | Offices And Premises | office | 1 | 1025.2 | 11035 | NIA | 560000 |  | no-geocode | [33 empty] | 1.63 | 72 | [35 empty] | 2910373000
4334 | 9 | UNIT 7 6TH FLR AT 20, WATER STREET | LONDON | E15 5GX | Tower Hamlets |  | Offices And Premises | office | 1 | 1021.93 | 11000 | NIA | 335000 |  | no-geocode | [33 empty] | 1.62 | 72 | [35 empty] | 14663030000
4335 | 9 | BLACKPOOL PRIMARY CARE TRUST, SEASIDERS WAY | BLACKPOOL | FY1 6TX | Blackpool |  | Offices And Premises | office | 1 | 1004.11 | 10808 | NIA | 108000 |  | no-geocode | [33 empty] | 1.6 | 70 | [35 empty] | 13065280000
4336 | 7.5 | BAE SYSTEMS, RADWAY GREEN | CREWE | CW1 5UJ | Cheshire East |  | Factory And Premises | industrial | 1 | 35240.68 | 379327 | GIA | 1710000 | Radway Green T1 | inside-area | 0.28 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM | -3.2 | bsp | -2.348 | Red | 7.5 | 5.839 | thermal | 4 | 2.2 | 0.1 | 6.2 | 0.2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | -3.1663 | RED | 0 |  |  | 0 | 0 | 0 | 7.5 |  |  |  |  | Red (More than 5% overloaded) | 0 | 0 | 56 | 2114 | 7 | 430370 | [9 empty] | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 0 | 20 | 2027-07 | [12 empty] | 53.0865 | -2.3354 | SPM-RADWAY_GREEN_T1 | 10642523000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4337 | 7.5 | SAICA PAPER (UK) LTD 144, MANCHESTER ROAD | MANCHESTER | M31 4QN | Trafford |  | Papermill And Premises | industrial | 1 | 71818.35 | 773046 | GIA | 4370000 | Lymm T1 / Whiteleggs La T1 | nearest-substation | 7.36 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM | -3.6 | primary | -3.623 | Red | 10 | 8.623 | thermal | 10 | 3 | 0 | 13 | -0.4 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 2.392 | AMBER | 0 |  |  | 0 | 0 | 0 | 10 |  |  |  |  | Red (More than 5% overloaded) | 0 | 0 | 114.13 | 4309 | 68 | 3560849 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.4289 | -2.4172 | SPM-LYMM_T1_WHITELEGGS_LA_T1 | 13889693000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4338 | 7.5 | KINGSLAND WINES & SPIRITS THE WINERY, FAIRHILLS ROAD | MANCHESTER | M44 6BD | Salford |  | Factory And Premises; Workshop And Premises | industrial | 2 | 59676.2 | 642349 | GIA | 1975000 | Lymm T1 / Whiteleggs La T1 | nearest-substation | 8.28 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM | -3.6 | primary | -3.623 | Red | 10 | 8.623 | thermal | 10 | 3 | 0 | 13 | -0.4 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | 2.392 | AMBER | 0 |  |  | 0 | 0 | 0 | 10 |  |  |  |  | Red (More than 5% overloaded) | 0 | 0 | 94.83 | 3581 | 68 | 3691546 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | [12 empty] | 53.44 | -2.4181 | SPM-LYMM_T1_WHITELEGGS_LA_T1 | 6934975000;6934975000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4339 | 7.5 | UNIT 2, MOORE PARK WAY | ST HELENS | WA11 9FS | St Helens |  | Warehouse And Premises | industrial | 3 | 134400.97 | 1446679 | GIA | 11250000 | Almatex T1 / St Helens Wwtw T1 / Watery La T2 / Ex Delta Metals T1 | nearest-substation | 3.13 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 213.58 | 3360 | 70 | 4390029 | [9 empty] | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | 39099396 | B8 Storage or Distribution | 48914 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2019-06-12 |  | 1 | FALSE | 53.4745 | -2.6771 | SPM-ALMATEX_T1_ST_HELENS_WWTW_T1_WATERY_LA_T2_EX_DELTA_METALS_T1 | 12684351000;12684351000;12406114000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4340 | 7.5 | THE HUT GROUP ICON MANCHESTER, SUNBANK LANE | MANCHESTER | WA15 0TP | Manchester |  | Warehouses, Office And Premises | industrial | 1 | 111195.5 | 1196897 | GIA | 7940000 |  | no-geocode | [33 empty] | 176.7 | 7784 | [35 empty] | 13902684000
4341 | 7.5 | AMAZON 6, SUNBANK LANE, AIRPORT CITY | MANCHESTER | M90 5AA | Manchester |  | Warehouse And Premises | industrial | 1 | 86648.5 | 932676 | GIA | 3600000 | Ringway T1 | inside-area | 0.67 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 137.69 | 2166 | 120 | 4528913 | [9 empty] | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 0 | 930 | 2026-05 | 10093075590 | B8 Storage or Distribution | 2100 | A | Grid Supplied Electricity | 5 | 2 | Air Conditioning | 2016-02-02 |  | 1 | FALSE | 53.3591 | -2.2952 | SPM-RINGWAY_T1 | 10748441000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4342 | 7.5 | ASSOCIATED BISCUITS, LONG LANE | LIVERPOOL | L9 7ZA | Liverpool |  | Factory And Premises | industrial | 1 | 80337.2 | 864742 | GIA | 1260000 |  | no-geocode | [33 empty] | 127.66 | 4820 | [35 empty] | 6683193000
4343 | 7.5 | GKN AEROSPACE, GOLF COURSE LANE | BRISTOL | BS34 9AU | South Gloucestershire |  | Factory And Premises | industrial | 1 | 75754.64 | 815415 | GIA | 1150000 |  | no-geocode | [33 empty] | 120.38 | 4545 | [35 empty] | 7195954000
4344 | 7.5 | NEWS INTERNATIONAL NEWSPAPERS LTD (KNOWSLEY), KITLING ROAD | PRESCOT | L34 9HN | Knowsley | NEWS INTERNATIONAL NEWSPAPERS LTD (KNOWSLEY) | Works And Premises | industrial | 1 | 63222.54 | 680521 | GIA | 1630000 | Kelco T1 / News International T1 / News International T2 / Palco T1 / Southdene T1 | inside-area | 0.73 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 100.47 | 3793 | 67 | 4015671 | [9 empty] | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 400 | 0 | 0 | 2027-08 | 40023407 | General Industrial and Special Industrial Groups | 70961 | B | Grid Supplied Electricity | 4 |  | Air Conditioning | 2023-08-22 |  | 0.67 | FALSE | 53.4628 | -2.8529 | SPM-KELCO_T1_NEWS_INTERNATIONAL_T1_NEWS_INTERNATIONAL_T2_PALCO_T | 416514134 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4345 | 7.5 | POINT 23, HALLWOOD AVENUE | ST HELENS | WA11 9UL | St Helens | J SAINSBURY PLC | Warehouse And Premises | industrial | 1 | 59480.92 | 640247 | GIA | 4980000 | Almatex T1 / St Helens Wwtw T1 / Watery La T2 / Ex Delta Metals T1 | nearest-substation | 3.89 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 94.52 | 1487 | 70 | 5196461 | [9 empty] | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | [12 empty] | 53.4769 | -2.6578 | SPM-ALMATEX_T1_ST_HELENS_WWTW_T1_WATERY_LA_T2_EX_DELTA_METALS_T1 | 652030137 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4346 | 7.5 | ALDI DISTRIBUTION CENTRE, CHESTER HIGH ROAD | NESTON | CH64 3TS | Cheshire West And Chester |  | Warehouse And Premises | industrial | 1 | 43319.95 | 466292 | GIA | 2620000 | Buildwas Rd T1 / Morgan Refractories T1 / Neston Main T1 | inside-area | 1.89 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | BIRKENHEAD | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 68.84 | 1083 | 5 | 112387 | [9 empty] | Connahs Quay / SASA | BIRKENHEAD | 0 | 0 | 0 | 0 | 0 | 90 | [13 empty] | 53.3022 | -3.0612 | SPM-BUILDWAS_RD_T1_MORGAN_REFRACTORIES_T1_NESTON_MAIN_T1 | 4669766000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4347 | 7.5 | DARESBURY LABORATORY, KECKWICK LANE | WARRINGTON | WA4 4AD | Halton |  | Laboratory | industrial | 1 | 42457.5 | 457008 | GIA | 1610000 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 | inside-area | 4.33 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 67.47 | 4246 | 15 | 331573 | [9 empty] | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 0 | 2029-04 | 100012805852 | Offices and Workshop Businesses | 4777 | B | Natural Gas | 5 |  | Air Conditioning | 2026-06-12 |  | 1 | FALSE | 53.3434 | -2.6412 | SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | 2721857000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4348 | 7.5 | POINT 23, HALLWOOD AVENUE | ST HELENS | WA11 9WD | St Helens | LLOYD FRASER (WHOLESALE) LTD | Warehouse And Premises | industrial | 1 | 40855 | 439759 | GIA | 3190000 | Almatex T1 / St Helens Wwtw T1 / Watery La T2 / Ex Delta Metals T1 | nearest-substation | 4.09 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 64.92 | 1021 | 70 | 5396949 | [9 empty] | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | 39079965 | Storage or Distribution | 39538 | B | Natural Gas | 4 |  | Heating and Natural Ventilation | 2024-12-18 |  | 0.5 | FALSE | 53.479 | -2.6578 | SPM-ALMATEX_T1_ST_HELENS_WWTW_T1_WATERY_LA_T2_EX_DELTA_METALS_T1 | 652508137 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4349 | 7.5 | UNIT B, HAYDOCK CROSS, KILBUCK LANE | ST HELENS | WA11 9UX | St Helens |  | Warehouse And Premises | industrial | 1 | 33225.7 | 357638 | GIA | 1120000 | Almatex T1 / St Helens Wwtw T1 / Watery La T2 / Ex Delta Metals T1 | nearest-substation | 4.09 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 52.8 | 831 | 70 | 5479070 | [9 empty] | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | [12 empty] | 53.4748 | -2.6481 | SPM-ALMATEX_T1_ST_HELENS_WWTW_T1_WATERY_LA_T2_EX_DELTA_METALS_T1 | 773856000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4350 | 7.5 | GLEN DIMPLEX HOME APPLIANCES, STONEY LANE | PRESCOT | L35 2XW | Knowsley |  | Factory And Premises | industrial | 1 | 31784.11 | 342121 | GIA | 535000 | Holt La (Warrington Rd) T1 / Prescot T1 / Rainhill Local T1 / Whiston Hosp T1 | inside-area | 2.19 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 50.51 | 1907 | 3 | 79999 | [9 empty] | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 0 | 57 | 2026-09 | [12 empty] | 53.4188 | -2.7851 | SPM-HOLT_LA_WARRINGTON_RD_T1_PRESCOT_T1_RAINHILL_LOCAL_T1_WHISTO | 6524532000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4351 | 7.5 | UNILEVER BEST FOODS UK, TRAFFORD PARK ROAD | MANCHESTER | M17 1H | Trafford |  | Factory And Premises | industrial | 1 | 30607.21 | 329453 | GIA | 925000 |  | no-geocode | [33 empty] | 48.64 | 1836 | [35 empty] | 3765471000
4352 | 7.5 | 8, ARDRA ROAD | LONDON | N9 3BL | Enfield |  | Warehouse And Premises | industrial | 1 | 30379.58 | 327003 | GIA | 4260000 |  | no-geocode | [33 empty] | 48.28 | 759 | [35 empty] | 4425124000
4353 | 7.5 | DAIRY CREST, DEACON PARK, MOORGATE ROAD | LIVERPOOL | L33 7HX | Knowsley |  | Factory And Premises | industrial | 1 | 29958.2 | 322467 | GIA | 475000 |  | no-geocode | [33 empty] | 47.61 | 1797 | [35 empty] | 11637110000
4354 | 7.5 | BUILDINGS 549-552, CARGO TERMINAL | HOUNSLOW | TW6 1ZZ | Hillingdon |  | Warehouse And Premises | industrial | 1 | 29365.13 | 316083 | GIA | 8250000 |  | no-geocode | [33 empty] | 46.66 | 734 | [35 empty] | 10983517000
4355 | 7.5 | CO-OPERATIVE GROUP (CWS) LTD REGIONAL DISTRIBUTION CENTRE, OLIVER ROAD | GRAYS | RM20 3EN | Thurrock |  | Warehouse And Premises | industrial | 1 | 29351.28 | 315934 | GIA | 3070000 |  | no-geocode | [33 empty] | 46.64 | 734 | [35 empty] | 4995325000
4356 | 7.5 | SINGLETONS UNITS S1 & S2 SATURN PARK, SCHOOL LANE | PRESCOT | L34 9GJ | Knowsley |  | Warehouse And Premises | industrial | 1 | 29259.56 | 314947 | GIA | 965000 | Kelco T1 / News International T1 / News International T2 / Palco T1 / Southdene T1 | inside-area | 1.85 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM |  | unknown-primary | [5 empty] | 0 | 0 | 0 | 0 |  | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 |  |  | 0 |  |  | 0 | 0 | 0 | [8 empty] | 46.5 | 731 | 67 | 4381245 | [9 empty] | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 400 | 0 | 0 | 2027-08 | [12 empty] | 53.4635 | -2.8714 | SPM-KELCO_T1_NEWS_INTERNATIONAL_T1_NEWS_INTERNATIONAL_T2_PALCO_T | 10638813000 | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR
4357 | 7.5 | SMISBY ROAD | ASHBY-DE-LA-ZOUCH | LE67 5TJ | North West Leicestershire | UNITED BISCUITS LTD | Factory And Premises | industrial | 1 | 28375 | 305426 | GIA | 850000 |  | no-geocode | [33 empty] | 45.09 | 1702 | [35 empty] | 2806046
4358 | 7.5 | 200, GREAT SOUTH WEST ROAD | HOUNSLOW | TW4 7FD | Hounslow |  | Warehouse And Premises | industrial | 1 | 28259.03 | 304177 | GIA | 4830000 |  | no-geocode | [33 empty] | 44.91 | 706 | [35 empty] | 14179658000
4359 | 4.5 | (EXCL BM14 & CAR BAYS 1-4) MILTON HSE AND SHIRE HSE, SILK STREET | LONDON | EC2Y 7BU | City Of London |  | Offices And Premises | office | 1 | 41547.57 | 447214 | NIA | 13630000 |  | no-geocode | [33 empty] | 66.02 | 2908 | [35 empty] | 4438912000

## Primary substations
primary_floc | primary | hm_name | grid_site | bsp_name | gsp | zone | local_authority | demand_firm_mw | demand_max_mw | headroom_mw | rag_short | limiting_factor | offers_accepted_mw | offers_accepted_n | offers_made_mw | offers_made_n | budget_est_mw | budget_est_n | t6_accepted_mw | t6_pending_mw | t6_budget_mw | ltds_max_24_25_mw | ltds_forecast_29_30_mw | headroom_2030_mw | bsp_firm_mw | bsp_max_mw | bsp_headroom_mw | bsp_constraint | bsp_offers_made_mw | gsp_import_limit_mw | gsp_max_observed_mw | gsp_headroom_mw | gsp_rag | gsp_queue_apps | gsp_queue_mva | gsp_queue_large_demand_mva | gsp_queue_apps_since_2024 | effective_headroom_mw | binding_tier | pipeline_pressure_mw | tx_gsp_region | tx_tec_key | tx_tec_projects | tx_tec_pipeline_mw | tx_tec_storage_mw | tx_tec_gate2_mw | tx_tec_connected_mw | tx_tec_next_date | firm_mva_winter | firm_mva_summer | season | unutilised_pct | headroom_polygon_mw | site_postcode | transformers | trans_rating_winter | source | dno | lat | lon | candidate_sites | candidate_sqft | edge_sqft_supportable
SPM-ALMONDS_TURN_T1_ATLANTIC_COMPLEX_T1_GIRO_T1_MIDLAND_BANK_T1_ | Almonds Turn T1 / Atlantic Complex T1 / Giro T1 / Midland Bank T1 / Netherton T1 | ALMONDS TURN T1 / ATLANTIC COMPLEX T1 / GIRO T1 / MIDLAND BANK T1 / NETHERTON T1 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1A | KIRKBY | SPM |  | 37.5 | 11.643 | 25.857 | Green | thermal | 0 | 0 | 1.6 | 4 | 0 | 0 | 0 | 0 | 0 | 11.643 | 14.7762 | 22.7 | 101.9 | 76.2256 | 24.7 | GREEN | 1.5 |  |  |  |  | 0 | 0 | 0 | 0 | 24.7 | bsp | 1.6 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4914 | -2.9866 | 28 | 1832516 | 176114
SPM-ALLERTON_T1_ECP_WEST_BANKS_RD_T1_GARSTON_T1_WEAVER_IND_EST_T | Allerton T1 / Ecp West-Banks Rd T1 / Garston T1 / Weaver Ind Est T1 / Yew Tree Rd T1 | ALLERTON T1 / ECP WEST-BANKS RD T1 / GARSTON T1 / WEAVER IND EST T1 / YEW TREE RD T1 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | LISTER DRIVE | SPM |  | 37.5 | 13.182 | 24.318 | Green | thermal | 0 | 0 | 12.8 | 15 | 7.5 | 5 | 1.5 | 1.5 | 0 | 13.182 | 16.1633 | 21.3 | 108.3 | 52.644 | 54.021 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 24.3 | primary | 12.8 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3453 | -2.8831 | 16 | 1974994 | 173262
SPM-ALBERT_DOCK_T1_KINGS_DOCK_T1_KINGS_DOCK_T2_WAPPING_T1 | Albert Dock T1 / Kings Dock T1 / Kings Dock T2 / Wapping T1 | ALBERT DOCK T1 / KINGS DOCK T1 / KINGS DOCK T2 / WAPPING T1 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 30 | 5.785 | 24.215 | Green | thermal | 0 | 0 | 18.2 | 16 | 0 | 0 | 1.5 | 1.5 | 0 | 5.785 | 6.119 | 23.9 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 24.2 | primary | 18.2 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3962 | -2.9888 | 4 | 77736 | 172549
SPM-LUGSDALE_T1_PILK_SULLIVAN_T1_PILK_SULLIVAN_T2_USAC_T1 | Lugsdale T1 / Pilk Sullivan T1 / Pilk Sullivan T2 / Usac T1 | LUGSDALE T1 / PILK SULLIVAN T1 / PILK SULLIVAN T2 / USAC T1 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G4A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM |  | 30 | 8.025 | 21.975 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.025 | 9.1822 | 20.8 | 110.6 | 77.52 | 23.6331 | GREEN | 4.9 |  |  |  |  | 0 | 0 | 0 | 0 | 22 | primary | 0 | Fiddlers Ferry | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3661 | -2.7236 | 33 | 2110448 | 156862
SPM-ESTUARY_COMMERCE_PK_T1_LEEWARD_DR_T1_LEEWARD_DR_T2_SPEKE_HAL | Estuary Commerce Pk T1 / Leeward Dr T1 / Leeward Dr T2 / Speke Hall Rd T1 / Speke Sky Pk T1 | ESTUARY COMMERCE PK T1 / LEEWARD DR T1 / LEEWARD DR T2 / SPEKE HALL RD T1 / SPEKE SKY PK T1 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | LISTER DRIVE | SPM |  | 30 | 8.915 | 21.085 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.915 | 11.0358 | 19 | 108.3 | 52.644 | 54.021 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 21.1 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3455 | -2.8714 | 46 | 3300652 | 150445
SPM-BLACON_T1_COCOA_BARRY_T1_CRANE_BANK_T1_KNUTSFORD_WAY_T1_TOWE | Blacon T1 / Cocoa Barry T1 / Crane Bank T1 / Knutsford Way T1 / Tower Wharf T1 | BLACON T1 / COCOA BARRY T1 / CRANE BANK T1 / KNUTSFORD WAY T1 / TOWER WHARF T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 37.5 | 16.6932 | 20.5888 | Green | thermal | 1.3 | 6 | 4.8 | 6 | 1.5 | 6 | 1.1 | 1.1 | 0 | 16.6932 | 20.3817 | 17.1 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 20.6 | primary | 6.1 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1947 | -2.917 | 48 | 1947521 | 146880
SPM-AIRPORT_T1_ALDERWOOD_AVE_CROYDE_RD_T1_HAREFIELD_RD_T1_METAL_ | Airport T1 / Alderwood Ave (Croyde Rd) T1 / Harefield Rd T1 / Metal Box (Speke) T1 | AIRPORT T1 / ALDERWOOD AVE (CROYDE RD) T1 / HAREFIELD RD T1 / METAL BOX (SPEKE) T1 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | LISTER DRIVE | SPM |  | 30 | 9.7979 | 20.2021 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 9.7979 | 12.7969 | 17.2 | 108.3 | 52.644 | 54.021 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 20.2 | primary | 0 | Frodsham | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3395 | -2.8552 | 17 | 1095003 | 144028
SPM-ARROWE_PK_HOSP_T1_CHAMPION_PLUGS_T1_CHAMPION_PLUGS_T2_WOODCH | Arrowe Pk Hosp T1 / Champion Plugs T1 / Champion Plugs T2 / Woodchurch T1 | ARROWE PK HOSP T1 / CHAMPION PLUGS T1 / CHAMPION PLUGS T2 / WOODCHURCH T1 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | BIRKENHEAD | SPM |  | 30 | 9.791 | 20.209 | Green | thermal | 0 | 0 | 3.5 | 12 | 0.9 | 4 | 1.6 | 1.6 | 0 | 9.791 | 10.1803 | 19.8 | 86.9 | 65.376 | 21.2835 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 20.2 | primary | 3.5 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3748 | -3.0888 | 0 | 0 | 144028
SPM-BROMFIELD_T1_BROMFIELD_T2_PONTERWYL_T1_RHYD_Y_GOLEU_T1_SYNTH | Bromfield T1 / Bromfield T2 / Ponterwyl T1 / Rhyd-Y-Goleu T1 / Synthite T1 | BROMFIELD T1 / BROMFIELD T2 / PONTERWYL T1 / RHYD-Y-GOLEU T1 / SYNTHITE T1 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 37.5 | 17.137 | 20.363 | Green | thermal | 0 | 0 | 0 | 5 | 1.1 | 5 | 0 | 0 | 0 | 17.137 | 21.1697 | 16.3 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 19.9 | bsp | 0 | Connahs Quay / SASA | [7 empty] | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.157 | -3.133 | 20 | 1136678 | 141889
SPM-CEREAL_PARTNERS_T1_LEVER_GEORGIA_AVE_T1_POOL_LA_T1_UML_LEVER | Cereal Partners T1 / Lever Georgia Ave T1 / Pool La T1 / Uml Lever Bromborough T2 | CEREAL PARTNERS T1 / LEVER GEORGIA AVE T1 / POOL LA T1 / UML LEVER BROMBOROUGH T2 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BIRKENHEAD | SPM |  | 30 | 10.234 | 19.766 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.234 | 11.384 | 18.6 | 71.4 | 49.586 | 21.814 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 19.8 | primary | 0 | Capenhurst | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3412 | -2.9645 | 30 | 2245173 | 141176
SPM-ASTMOOR_IND_EST_T1_MACKAMAX_T1_MERSEY_RD_T1_PICOW_FARM_RD_T1 | Astmoor Ind Est T1 / Mackamax T1 / Mersey Rd T1 / Picow Farm Rd T1 | ASTMOOR IND EST T1 / MACKAMAX T1 / MERSEY RD T1 / PICOW FARM RD T1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | 30 | 11.12 | 18.28 | Green | thermal | 2.4 | 4 | 1.9 | 4 | 0 | 0 | 0.6 | 0.6 | 0 | 11.12 | 12.8753 | 17.1 | 106.2 | 72.984 | 32.616 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 18.3 | primary | 4.3 | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3434 | -2.7078 | 44 | 3019357 | 130481
SPM-EDGE_LA_TAPLEY_PLACE_T1_LISTER_DV_B_T3_MILL_LA_WAVERTREE_T1_ | Edge La (Tapley Place) T1 / Lister Dv B T3 / Mill La (Wavertree) T1 / Plessey (Edge La) T1 / Stoneycroft T1 | EDGE LA (TAPLEY PLACE) T1 / LISTER DV B T3 / MILL LA (WAVERTREE) T1 / PLESSEY (EDGE LA) T1 / STONEYCROFT T1 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 37.5 | 19.645 | 17.855 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.645 | 24.2822 | 13.2 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 17.9 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4195 | -2.932 | 29 | 1204521 | 127629
SPM-BANGOR_HOSP_T1_BANGOR_UNIVERSITY_T1_EITHINOG_T1_HIRAEL_T1 | Bangor Hosp T1 / Bangor University T1 / Eithinog T1 / Hirael T1 | BANGOR HOSP T1 / BANGOR UNIVERSITY T1 / EITHINOG T1 / HIRAEL T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 30 | 12.058 | 17.802 | Green | thermal | 0.6 | 4 | 2.1 | 8 | 1.2 | 4 | 0.1 | 0 | 0 | 12.058 | 14.3627 | 15.6 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 17.8 | primary | 2.7 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.221 | -4.1514 | 14 | 567185 | 126916
SPM-BROOK_ST_T1_KINGSWAY_TUNNEL_T1_NWWA_SANDON_DOCK_T1_NWWA_SAND | Brook St T1 / Kingsway Tunnel T1 / Nwwa Sandon Dock T1 / Nwwa Sandon Dock T2 | BROOK ST T1 / KINGSWAY TUNNEL T1 / NWWA SANDON DOCK T1 / NWWA SANDON DOCK T2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 30 | 12.229 | 17.771 | Green | thermal | 0 | 0 | 5.1 | 8 | 10.2 | 8 | 0 | 0 | 0 | 12.229 | 13.6767 | 16.3 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 17.8 | primary | 5.1 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4281 | -2.9986 | 35 | 1416338 | 126916
SPM-BOOTLE_GRID_T1_KELLOGGS_T1_PACIFIC_RD_T1_WASHINGTON_ST_T1_WA | Bootle Grid T1 / Kelloggs T1 / Pacific Rd T1 / Washington St T1 / Waterloo T1 | BOOTLE GRID T1 / KELLOGGS T1 / PACIFIC RD T1 / WASHINGTON ST T1 / WATERLOO T1 | BOOTLE GT1 / LITHERLAND GT1A | BOOTLE GT1 / LITHERLAND GT1B | KIRKBY | SPM |  | 37.5 | 19.812 | 17.262 | Green | thermal | 2.1 | 15 | 17.9 | 45 | 5.3 | 10 | 3.7 | 2.3 | 0 | 19.812 | 24.8498 | 12.7 | 68.6 | 46.6951 | 21.4789 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 17.3 | primary | 20 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4606 | -3.013 | 34 | 1541314 | 123351
SPM-HERONS_WAY_T1_LACHE_T1_MBNA_T1_SMFS_KINGSMEADOW_T1 | Herons Way T1 / Lache T1 / Mbna T1 / Smfs Kingsmeadow T1 | HERONS WAY T1 / LACHE T1 / MBNA T1 / SMFS KINGSMEADOW T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 30 | 10.843 | 17.012 | Green | thermal | 8.6 | 4 | 0.3 | 4 | 0.3 | 4 | 1.4 | 0.8 | 0 | 10.843 | 12.7227 | 17.3 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 17 | primary | 8.9 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1599 | -2.8949 | 16 | 973537 | 121212
SPM-AIGBURTH_VALE_T1_IVY_AVE_T1_MATHER_AVE_T1_MOSSLEY_HILL_T1_WA | Aigburth Vale T1 / Ivy Ave T1 / Mather Ave T1 / Mossley Hill T1 / Wavertree T1 | AIGBURTH VALE T1 / IVY AVE T1 / MATHER AVE T1 / MOSSLEY HILL T1 / WAVERTREE T1 | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | GARSTON GT2 / SPEKE GT3 / WAVERTREE GT1A | LISTER DRIVE | SPM |  | 37.5 | 18.823 | 17.042 | Green | thermal | 8.2 | 10 | 6.8 | 5 | 0 | 0 | 4.5 | 1.5 | 0 | 18.823 | 22.6765 | 14.8 | 108.3 | 52.644 | 54.021 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 17 | primary | 15 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.375 | -2.9211 | 8 | 243232 | 121212
SPM-EDGE_HILL_T1_LIVERPOOL_UNIVERSITY_T1_LIVERPOOL_UNIVERSITY_T2 | Edge Hill T1 / Liverpool University T1 / Liverpool University T2 / Liverpool University T3 | EDGE HILL T1 / LIVERPOOL UNIVERSITY T1 / LIVERPOOL UNIVERSITY T2 / LIVERPOOL UNIVERSITY T3 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 30 | 13.452 | 16.548 | Green | thermal | 0 | 0 | 5.5 | 4 | 0 | 0 | 0.9 | 0 | 0 | 13.452 | 14.1972 | 15.8 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 16.5 | primary | 5.5 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4044 | -2.9567 | 4 | 171904 | 117647
SPM-CASTLE_BEESTON_ST_T1_HARTFORD_T2_LEICESTER_ST_T1_NORTHWICH_T | Castle Beeston St T1 / Hartford T2 / Leicester St T1 / Northwich Town T1 / Winnington T1 | CASTLE BEESTON ST T1 / HARTFORD T2 / LEICESTER ST T1 / NORTHWICH TOWN T1 / WINNINGTON T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 37.5 | 21.101 | 16.399 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.101 | 26.1382 | 11.4 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 16.4 | primary | 0 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2557 | -2.5208 | 14 | 666231 | 116934
SPM-LOWER_BEBINGTON_T1_NEW_FERRY_T1_SPITAL_T1_UNILEVER_RESEARCH_ | Lower Bebington T1 / New Ferry T1 / Spital T1 / Unilever Research T1 | LOWER BEBINGTON T1 / NEW FERRY T1 / SPITAL T1 / UNILEVER RESEARCH T1 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BIRKENHEAD | SPM |  | 30 | 13.675 | 16.247 | Green | thermal | 0.3 | 4 | 2.7 | 12 | 0 | 0 | 0.3 | 0.3 | 0 | 13.675 | 17.4576 | 12.5 | 71.4 | 49.586 | 21.814 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 16.2 | primary | 3 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3412 | -3.007 | 2 | 375313 | 115508
SPM-BLUNDELLSANDS_NORTH_T1_BLUNDELLSANDS_SOUTH_T1_CROSBY_T1_KERS | Blundellsands (North) T1 / Blundellsands (South) T1 / Crosby T1 / Kershaw Ave T1 / Waterloo T2 | BLUNDELLSANDS (NORTH) T1 / BLUNDELLSANDS (SOUTH) T1 / CROSBY T1 / KERSHAW AVE T1 / WATERLOO T2 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1A | KIRKBY | SPM |  | 37.5 | 21.64 | 15.86 | Green | thermal | 0 | 0 | 1 | 5 | 0 | 0 | 0.8 | 0.8 | 0 | 21.64 | 26.2599 | 11.2 | 101.9 | 76.2256 | 24.7 | GREEN | 1.5 |  |  |  |  | 0 | 0 | 0 | 0 | 15.9 | primary | 1 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4934 | -3.0461 | 3 | 67253 | 113368
SPM-CONWY_T1_DEGANWY_T1_LLANDUDNO_JUNCTION_T1 | Conwy T1 / Deganwy T1 / Llandudno Junction T1 | CONWY T1 / DEGANWY T1 / LLANDUDNO JUNCTION T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 27.3 | 11.491 | 15.74 | Green | thermal | 0.2 | 3 | 0.2 | 3 | 0.1 | 3 | 0.1 | 0 | 0 | 11.491 | 15.1001 | 12.2 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 15.7 | primary | 0.4 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 27.3 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2838 | -3.8384 | 24 | 809736 | 111942
SPM-MINFFORDD_T1_PARC_BRYN_CEGIN_T1_PARC_BRYN_CEGIN_T2 | Minffordd T1 / Parc Bryn Cegin T1 / Parc Bryn Cegin T2 | MINFFORDD T1 / PARC BRYN CEGIN T1 / PARC BRYN CEGIN T2 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 4.042 | 15.538 | Green | thermal | 1.3 | 6 | 11 | 12 | 2.6 | 3 | 0 | 0 | 0 | 4.042 | 5.1961 | 14.8 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 15.5 | primary | 12.3 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2163 | -4.1311 | 11 | 280045 | 110516
SPM-DESOTO_RD_T1_MERSEY_BRIDGE_T1_PITT_ST_T1 | Desoto Rd T1 / Mersey Bridge T1 / Pitt St T1 | DESOTO RD T1 / MERSEY BRIDGE T1 / PITT ST T1 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G4A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM |  | 20 | 4.67 | 15.33 | Green | thermal | 0 | 0 | 0 | 0 | 12.2 | 3 | 0 | 0 | 0 | 4.67 | 5.2895 | 14.7 | 110.6 | 77.52 | 23.6331 | GREEN | 4.9 |  |  |  |  | 0 | 0 | 0 | 0 | 15.3 | primary | 0 | Frodsham | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3587 | -2.7388 | 21 | 1786107 | 109090
SPM-NEW_BRIGHTON_T1_SEAVIEW_RD_T2_WALLASEY_T1_WALLASEY_VILLAGE_T | New Brighton T1 / Seaview Rd T2 / Wallasey T1 / Wallasey Village T1 | NEW BRIGHTON T1 / SEAVIEW RD T2 / WALLASEY T1 / WALLASEY VILLAGE T1 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | BIRKENHEAD | SPM |  | 30 | 14.847 | 15.153 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 2.7 | 0 | 14.847 | 18.6864 | 11.3 | 95 | 52.555 | 42.195 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 15.2 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.436 | -3.0404 | 12 | 599046 | 108377
SPM-BASS_CHARRINGTON_T1_BASS_CHARRINGTON_T2_CLIFTON_T1_YKK_T1 | Bass Charrington T1 / Bass Charrington T2 / Clifton T1 / Ykk T1 | BASS CHARRINGTON T1 / BASS CHARRINGTON T2 / CLIFTON T1 / YKK T1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | 30 | 15.01 | 14.99 | Green | thermal | 0 | 0 | 6.4 | 9 | 0 | 0 | 4.6 | 4.6 | 0 | 15.01 | 17.8319 | 12.2 | 106.2 | 72.984 | 32.616 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 15 | primary | 6.4 | Frodsham | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3203 | -2.7166 | 37 | 3846490 | 106951
SPM-BERSHAM_RD_T1_IND_COOPE_T1_RHYD_BROUGHTON_LA_T1_TUTTLE_ST_T1 | Bersham Rd T1 / Ind Coope T1 / Rhyd Broughton La T1 / Tuttle St T1 | BERSHAM RD T1 / IND COOPE T1 / RHYD BROUGHTON LA T1 / TUTTLE ST T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 30 | 15.043 | 14.957 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.043 | 18.4255 | 11.6 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 15 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0395 | -3.012 | 22 | 974756 | 106951
SPM-CHESTER_ST_WREXHAM_T1_EAGLES_MEADOW_T1_RHOSNESNI_T1_WHITEGAT | Chester St (Wrexham) T1 / Eagles Meadow T1 / Rhosnesni T1 / Whitegate T1 | CHESTER ST (WREXHAM) T1 / EAGLES MEADOW T1 / RHOSNESNI T1 / WHITEGATE T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 30 | 15.204 | 14.796 | Green | thermal | 0 | 0 | 0.6 | 4 | 0 | 0 | 0 | 0 | 0 | 15.204 | 19.2681 | 10.7 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 14.8 | primary | 0.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0439 | -2.9882 | 19 | 1382317 | 105525
SPM-ILFORDS_T1_KNUTSFORD_T1_MOBBERLEY_T1_RADBROKE_HALL_T1 | Ilfords T1 / Knutsford T1 / Mobberley T1 / Radbroke Hall T1 | ILFORDS T1 / KNUTSFORD T1 / MOBBERLEY T1 / RADBROKE HALL T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 30 | 14.758 | 14.665 | Green | thermal | 2.3 | 20 | 1.3 | 20 | 2 | 4 | 0.3 | 0.2 | 0.1 | 14.758 | 17.7376 | 12.3 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 14.7 | primary | 3.6 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1947 | -2.917 | 55 | 2707064 | 104812
SPM-BOOTLE_GRID_T2_ORRELL_MOUNT_T1_SCARISBRICK_AVE_T1_TATTON_RD_ | Bootle Grid T2 / Orrell Mount T1 / Scarisbrick Ave T1 / Tatton Rd T1 | BOOTLE GRID T2 / ORRELL MOUNT T1 / SCARISBRICK AVE T1 / TATTON RD T1 | BOOTLE GT1 / LITHERLAND GT1A | BOOTLE GT1 / LITHERLAND GT1B | KIRKBY | SPM |  | 30 | 15.28 | 14.72 | Green | thermal | 0 | 0 | 5.3 | 12 | 1.6 | 4 | 0.2 | 0.2 | 0 | 15.28 | 19.2144 | 10.8 | 68.6 | 46.6951 | 21.4789 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 14.7 | primary | 5.3 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4566 | -2.9858 | 13 | 469699 | 104812
SPM-CALDY_T1_HOYLAKE_T1_MEOLS_T1_WEST_KIRBY_SOUTH_T1 | Caldy T1 / Hoylake T1 / Meols T1 / West Kirby South T1 | CALDY T1 / HOYLAKE T1 / MEOLS T1 / WEST KIRBY SOUTH T1 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | BIRKENHEAD | SPM |  | 30 | 15.2328 | 14.5872 | Green | thermal | 0.7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2328 | 18.7352 | 11.3 | 86.9 | 65.376 | 21.2835 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 14.6 | primary | 0.7 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3988 | -3.1554 | 4 | 90736 | 104099
SPM-CLOCKFACE_T1_GEC_ST_HELENS_T1_HILLS_MOSS_T1_NCB_SUTTON_MANOR | Clockface T1 / Gec St Helens T1 / Hills Moss T1 / Ncb Sutton Manor T2 | CLOCKFACE T1 / GEC ST HELENS T1 / HILLS MOSS T1 / NCB SUTTON MANOR T2 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G4A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM |  | 30 | 15.574 | 14.426 | Green | thermal | 0 | 0 | 4.6 | 8 | 0 | 0 | 0 | 0 | 1.1 | 15.574 | 19.0172 | 11 | 110.6 | 77.52 | 23.6331 | GREEN | 4.9 |  |  |  |  | 0 | 0 | 0 | 0 | 14.4 | primary | 4.6 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4164 | -2.7413 | 61 | 6580092 | 102673
SPM-GRAVEL_T1_WCB_PLASTICS_T1_WHARTON_T1 | Gravel T1 / Wcb Plastics T1 / Wharton T1 | GRAVEL T1 / WCB PLASTICS T1 / WHARTON T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 20 | 5.726 | 14.274 | Green | thermal | 0 | 0 | 23.1 | 15 | 0 | 0 | 0.7 | 0.7 | 0 | 5.726 | 6.7811 | 13.2 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 14.3 | primary | 23.1 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1926 | -2.4894 | 41 | 2480257 | 101960
SPM-CHILDWALL_T1_CHILDWALL_FIVEWAYS_T1_LYNDENE_RD_T1_MIDDLEMASS_ | Childwall T1 / Childwall Fiveways T1 / Lyndene Rd T1 / Middlemass Hey T1 / Naylors Rd T1 | CHILDWALL T1 / CHILDWALL FIVEWAYS T1 / LYNDENE RD T1 / MIDDLEMASS HEY T1 / NAYLORS RD T1 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | 37.5 | 23.249 | 14.251 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.249 | 27.7341 | 9.8 | 114.8 | 83.378 | 31.422 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 14.3 | primary | 0 | Lister Drive | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3977 | -2.8983 | 8 | 298812 | 101960
SPM-CONIX_T1_CONIX_T2_MEDEVA_T1 | Conix T1 / Conix T2 / Medeva T1 | CONIX T1 / CONIX T2 / MEDEVA T1 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | HALEWOOD GT3 / SPEKE GT1A | RAINHILL | SPM |  | 20 | 5.971 | 14.029 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.971 | 6.3081 | 13.7 | 64.1 | 26.1394 | 37.9606 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 14 | primary | 0 | Lister Drive | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3495 | -2.846 | 6 | 426593 | 99821
SPM-BROADGREEN_T1_CROXTETH_T1_EAST_PRESCOT_RD_FINCH_LA_T1_KNOTTY | Broadgreen T1 / Croxteth T1 / East Prescot Rd (Finch La) T1 / Knotty Ash T1 / Leyfield Rd T1 | BROADGREEN T1 / CROXTETH T1 / EAST PRESCOT RD (FINCH LA) T1 / KNOTTY ASH T1 / LEYFIELD RD T1 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | 37.5 | 23.582 | 13.918 | Green | thermal | 0 | 0 | 2.1 | 8 | 0 | 0 | 5.6 | 5.6 | 1 | 23.582 | 28.6725 | 8.8 | 114.8 | 83.378 | 31.422 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 13.9 | primary | 2.1 | Lister Drive | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4186 | -2.8945 | 4 | 154070 | 99108
SPM-CARBORUNDUM_T1_HOUGHTONS_LA_T1_RAINFORD_T1_WINDLEHURST_T2 | Carborundum T1 / Houghtons La T1 / Rainford T1 / Windlehurst T2 | CARBORUNDUM T1 / HOUGHTONS LA T1 / RAINFORD T1 / WINDLEHURST T2 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAINHILL | SPM |  | 30 | 15.129 | 13.871 | Green | thermal | 4 | 4 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 15.129 | 17.8796 | 12.1 | 69.1 | 42.44 | 26.66 | GREEN | 17.1 |  |  |  |  | 0 | 0 | 0 | 0 | 13.9 | primary | 4 | Kirkby (_D) | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4605 | -2.7837 | 81 | 6781354 | 99108
SPM-ACORNFIELD_RD_T1_DICKINSONS_T1_HAMMOND_RD_T1_KODAK_T1 | Acornfield Rd T1 / Dickinsons T1 / Hammond Rd T1 / Kodak T1 | ACORNFIELD RD T1 / DICKINSONS T1 / HAMMOND RD T1 / KODAK T1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM |  | 30 | 16.209 | 13.791 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.209 | 19.4996 | 10.5 | 90.2 | 52.84 | 37.36 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 13.8 | primary | 0 | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4843 | -2.849 | 93 | 7298126 | 98395
SPM-HUNTS_CROSS_T1_KENTON_RD_T1_WOODEND_AVE_T1_WOOLTON_T1 | Hunts Cross T1 / Kenton Rd T1 / Woodend Ave T1 / Woolton T1 | HUNTS CROSS T1 / KENTON RD T1 / WOODEND AVE T1 / WOOLTON T1 | HALEWOOD G1B / HALEWOOD G2B / HALEWOOD GT3 / SPEKE GT1A | HALEWOOD GT3 / SPEKE GT1A | RAINHILL | SPM |  | 30 | 16.447 | 13.553 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.447 | 20.1238 | 9.9 | 64.1 | 26.1394 | 37.9606 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 13.6 | primary | 0 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.354 | -2.8531 | 29 | 3192050 | 96969
SPM-BURLINGTON_AVE_T1_FRESHFIELD_T1_MARSH_BROWS_T1_SOUTHPORT_RD_ | Burlington Ave T1 / Freshfield T1 / Marsh Brows T1 / Southport Rd T1 | BURLINGTON AVE T1 / FRESHFIELD T1 / MARSH BROWS T1 / SOUTHPORT RD T1 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1A | KIRKBY | SPM |  | 28 | 14.513 | 13.487 | Green | thermal | 0 | 0 | 0 | 0 | 5.2 | 12 | 2.2 | 2.2 | 1.7 | 14.513 | 18.1454 | 9.9 | 101.9 | 76.2256 | 24.7 | GREEN | 1.5 |  |  |  |  | 0 | 0 | 0 | 0 | 13.5 | primary | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 28 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.5562 | -3.047 | 4 | 202623 | 96256
SPM-DITTON_T1_GAVIN_RD_T1_HOUGH_GREEN_T1_RTZ_T1 | Ditton T1 / Gavin Rd T1 / Hough Green T1 / Rtz T1 | DITTON T1 / GAVIN RD T1 / HOUGH GREEN T1 / RTZ T1 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G4A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM |  | 30 | 17.125 | 12.874 | Green | thermal | 0 | 3 | 2.8 | 9 | 0 | 0 | 2.7 | 2.7 | 0 | 17.125 | 20.608 | 9.4 | 110.6 | 77.52 | 23.6331 | GREEN | 4.9 |  |  |  |  | 0 | 0 | 0 | 0 | 12.9 | primary | 2.8 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3792 | -2.7753 | 37 | 1937197 | 91978
SPM-BARNSTON_T1_GAYTON_T1_IRBY_T1_THINGWALL_T1 | Barnston T1 / Gayton T1 / Irby T1 / Thingwall T1 | BARNSTON T1 / GAYTON T1 / IRBY T1 / THINGWALL T1 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | BIRKENHEAD | SPM |  | 30 | 17.171 | 12.829 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.171 | 21.3261 | 8.7 | 86.9 | 65.376 | 21.2835 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 12.8 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3522 | -3.1173 | 1 | 57002 | 91265
SPM-EGREMONT_T1_LISCARD_T1_POULTON_T1_STONE_MANGANESE_T1 | Egremont T1 / Liscard T1 / Poulton T1 / Stone Manganese T1 | EGREMONT T1 / LISCARD T1 / POULTON T1 / STONE MANGANESE T1 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | BIRKENHEAD | SPM |  | 30 | 17.09 | 12.66 | Green | thermal | 1 | 4 | 1.5 | 4 | 7.2 | 4 | 1.8 | 1.8 | 0 | 17.09 | 21.1081 | 8.9 | 95 | 52.555 | 42.195 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 12.7 | primary | 2.5 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4075 | -3.0345 | 18 | 607228 | 90552
SPM-GROSVENOR_ST_T1_LINENHALL_ST_T1_NORTHGATE_TERRACE_T1_STATION | Grosvenor St T1 / Linenhall St T1 / Northgate Terrace T1 / Station View T1 / Tomular Place T1 | GROSVENOR ST T1 / LINENHALL ST T1 / NORTHGATE TERRACE T1 / STATION VIEW T1 / TOMULAR PLACE T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 30 | 17.492 | 12.508 | Green | thermal | 0 | 0 | 6.2 | 10 | 0 | 0 | 0.2 | 0.2 | 0 | 17.492 | 19.6187 | 10.4 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 12.5 | primary | 6.2 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1941 | -2.893 | 17 | 561558 | 89126
SPM-CHURCH_ST_WINSFORD_T1_OVER_T1_WHARTON_PK_T1_WOODFORD_PK_T1 | Church St Winsford T1 / Over T1 / Wharton Pk T1 / Woodford Pk T1 | CHURCH ST WINSFORD T1 / OVER T1 / WHARTON PK T1 / WOODFORD PK T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 30 | 16.589 | 12.511 | Green | thermal | 3.6 | 8 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0.3 | 16.589 | 20.7471 | 9.3 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 12.5 | primary | 3.6 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.194 | -2.5197 | 26 | 1345783 | 89126
SPM-AIRBUS_T1_BROUGHTON_RETAIL_PARK_T1_MIXALLOY_T1 | Airbus T1 / Broughton Retail Park T1 / Mixalloy T1 | AIRBUS T1 / BROUGHTON RETAIL PARK T1 / MIXALLOY T1 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 7.778 | 12.222 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.778 | 10.1876 | 9.8 | 119.8 | 87.04 | 32.76 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 12.2 | primary | 0 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1669 | -2.9737 | 29 | 1678440 | 86987
SPM-BICC_HUYTON_QUARRY_T1_TARBOCK_T1_WHISTON_T1 | Bicc Huyton Quarry T1 / Tarbock T1 / Whiston T1 | BICC HUYTON QUARRY T1 / TARBOCK T1 / WHISTON T1 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | 20 | 7.777 | 12.223 | Green | thermal | 0 | 0 | 1.2 | 9 | 0 | 0 | 5.5 | 4.7 | 0 | 7.777 | 10.4544 | 9.5 | 114.8 | 83.378 | 31.422 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 12.2 | primary | 1.2 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.405 | -2.8103 | 26 | 1724487 | 86987
SPM-HIGHFIELD_ST_T2_LIME_ST_T2_OLD_HAYMARKET_T1 | Highfield St T2 / Lime St T2 / Old Haymarket T1 | HIGHFIELD ST T2 / LIME ST T2 / OLD HAYMARKET T1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 20 | 8.024 | 11.976 | Green | thermal | 0 | 0 | 0 | 0 | 1.3 | 3 | 0 | 0 | 0 | 8.024 | 8.4416 | 11.6 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 12 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4102 | -2.9896 | 8 | 291277 | 85561
SPM-DODDS_LA_T1_HOLBORN_HILL_T1_MAGHULL_T1_MAGHULL_T2_ROBBINS_BR | Dodds La T1 / Holborn Hill T1 / Maghull T1 / Maghull T2 / Robbins Bridge T1 | DODDS LA T1 / HOLBORN HILL T1 / MAGHULL T1 / MAGHULL T2 / ROBBINS BRIDGE T1 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1A | KIRKBY | SPM |  | 37.5 | 24.581 | 11.9446 | Green | thermal | 4.9 | 15 | 27.1 | 50 | 0 | 0 | 2.4 | 2.4 | 2.5 | 24.581 | 32.7602 | 4.7 | 101.9 | 76.2256 | 24.7 | GREEN | 1.5 |  |  |  |  | 0 | 0 | 0 | 0 | 11.9 | primary | 32 | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.5562 | -2.9069 | 44 | 1529893 | 84848
SPM-BROOK_LA_T1_MANNINGS_LA_T1_NEWTOWN_CHESTER_T1_UPTON_HEATH_T1 | Brook La T1 / Mannings La T1 / Newtown Chester T1 / Upton Heath T1 | BROOK LA T1 / MANNINGS LA T1 / NEWTOWN CHESTER T1 / UPTON HEATH T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 30 | 17.7397 | 11.9303 | Green | thermal | 1.3 | 4 | 5.2 | 12 | 0 | 0 | 0.6 | 0.2 | 0 | 17.7397 | 23.4871 | 6.5 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 11.9 | primary | 6.5 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2008 | -2.8891 | 5 | 146699 | 84848
SPM-CONNAHS_QUAY_LOCAL_T1_CONNAHS_QUAY_LOCAL_T2_HAWARDEN_T1_KING | Connahs Quay Local T1 / Connahs Quay Local T2 / Hawarden T1 / King George St T1 | CONNAHS QUAY LOCAL T1 / CONNAHS QUAY LOCAL T2 / HAWARDEN T1 / KING GEORGE ST T1 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 30 | 17.125 | 11.753 | Green | thermal | 4.5 | 12 | 7.6 | 8 | 7.5 | 8 | 1.8 | 0.9 | 0 | 17.125 | 20.8346 | 9.2 | 119.8 | 87.04 | 32.76 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 11.8 | primary | 12.1 | Connahs Quay / SASA | [7 empty] | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.227 | -3.0728 | 14 | 355643 | 84135
SPM-MORGANITE_CERAMICS_T1_PLYMYARD_T2_VAUXHALL_NORTH_RD_T1 | Morganite Ceramics T1 / Plymyard T2 / Vauxhall North Rd T1 | MORGANITE CERAMICS T1 / PLYMYARD T2 / VAUXHALL NORTH RD T1 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | CAPENHURST | SPM |  | 20 | 3.3025 | 16.6975 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 3.3025 | 4.6877 | 15.3 | 88.1 | 76.397 | 11.703 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 11.7 | bsp | 0 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3069 | -2.9333 | 2 | 42484 | 83422
SPM-GILBROOK_DOCK_T1_HILL_RD_T1_MOBIL_OIL_WALLASEY_T1 | Gilbrook Dock T1 / Hill Rd T1 / Mobil Oil (Wallasey) T1 | GILBROOK DOCK T1 / HILL RD T1 / MOBIL OIL (WALLASEY) T1 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | BIRKENHEAD | SPM |  | 18.2 | 7.05 | 11.15 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 2 | 0 | 7.05 | 8.7587 | 9.4 | 95 | 52.555 | 42.195 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 11.2 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 18.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3929 | -3.062 | 13 | 746531 | 79857
SPM-DYSERTH_RD_T1_FFORDD_LAS_T1_FFORDD_LAS_T2_WESTBOURNE_AVE_T1 | Dyserth Rd T1 / Ffordd Las T1 / Ffordd Las T2 / Westbourne Ave T1 | DYSERTH RD T1 / FFORDD LAS T1 / FFORDD LAS T2 / WESTBOURNE AVE T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 30 | 17.069 | 10.8185 | Green | thermal | 8.4 | 12 | 5.3 | 12 | 13 | 8 | 5.1 | 1.9 | 0 | 17.069 | 21.0064 | 9 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10.8 | primary | 13.7 | Connahs Quay / SASA | [7 empty] | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3192 | -3.4572 | 13 | 677341 | 77005
SPM-COLWYN_BAY_T1_COLWYN_BAY_T2_RHOS_ON_SEA_T1 | Colwyn Bay T1 / Colwyn Bay T2 / Rhos-On-Sea T1 | COLWYN BAY T1 / COLWYN BAY T2 / RHOS-ON-SEA T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 18 | 7.33 | 10.67 | Green | thermal | 0 | 0 | 1 | 6 | 5.8 | 9 | 0.1 | 0.1 | 0 | 7.33 | 8.9495 | 9.1 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10.7 | primary | 1 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 18 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2967 | -3.7624 | 16 | 340349 | 76292
SPM-BANASTRE_RD_T1_DOVER_RD_T1_GRANTHAM_CL_T1 | Banastre Rd T1 / Dover Rd T1 / Grantham Cl T1 | BANASTRE RD T1 / DOVER RD T1 / GRANTHAM CL T1 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM |  | 20 | 9.524 | 10.476 | Green | thermal | 0 | 0 | 0 | 0 | 0.6 | 3 | 0.5 | 0.5 | 0 | 9.524 | 11.8933 | 8.1 | 75 | 59.016 | 12.484 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10.5 | primary | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.6366 | -3.0069 | 3 | 257769 | 74866
SPM-NEVILL_ST_T1_OCEAN_PLAZA_T1_YORK_RD_T1 | Nevill St T1 / Ocean Plaza T1 / York Rd T1 | NEVILL ST T1 / OCEAN PLAZA T1 / YORK RD T1 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM |  | 20 | 9.574 | 10.426 | Green | thermal | 0 | 0 | 0 | 0 | 0.8 | 3 | 0.2 | 0.2 | 0 | 9.574 | 10.8335 | 9.2 | 75 | 59.016 | 12.484 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10.4 | primary | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.65 | -3.0086 | 7 | 322403 | 74153
SPM-CABLE_ST_T2_CROWN_COURTS_T1_GRADWELL_ST_T1 | Cable St T2 / Crown Courts T1 / Gradwell St T1 | CABLE ST T2 / CROWN COURTS T1 / GRADWELL ST T1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 20 | 9.326 | 10.346 | Green | thermal | 1 | 3 | 6 | 6 | 0 | 0 | 0.3 | 0.3 | 0 | 9.326 | 9.9415 | 10.1 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10.3 | primary | 7 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4045 | -2.9893 | 2 | 29489 | 73440
SPM-BENTINCK_ST_T1_BENTINCK_ST_T2_CHESTER_ST_T1 | Bentinck St T1 / Bentinck St T2 / Chester St T1 | BENTINCK ST T1 / BENTINCK ST T2 / CHESTER ST T1 | PRENTON GRID GT1 / ROCK FERRY GT1 | PRENTON GRID GT1 / ROCK FERRY GT1 | BIRKENHEAD | SPM |  | 18.2 | 7.8665 | 10.3335 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8665 | 9.9984 | 8.2 | 74.4 | 55.945 | 18.455 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10.3 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 18.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3909 | -3.0318 | 33 | 1099851 | 73440
SPM-FORD_T1_OXTON_T1_PRENTON_LOCAL_T1_SINGLETON_AVE_T2 | Ford T1 / Oxton T1 / Prenton Local T1 / Singleton Ave T2 | FORD T1 / OXTON T1 / PRENTON LOCAL T1 / SINGLETON AVE T2 | PRENTON GRID GT1 / ROCK FERRY GT1 | PRENTON GRID GT1 / ROCK FERRY GT1 | BIRKENHEAD | SPM |  | 30 | 19.957 | 10.043 | Green | thermal | 0 | 0 | 12.7 | 20 | 0 | 0 | 2.2 | 2.2 | 0 | 19.957 | 25.6065 | 4.4 | 74.4 | 55.945 | 18.455 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 10 | primary | 12.7 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3752 | -3.0386 | 14 | 453794 | 71301
SPM-CLUBMOOR_T1_DUNLOPS_WALTON_T1_WALTON_T2 | Clubmoor T1 / Dunlops Walton T1 / Walton T2 | CLUBMOOR T1 / DUNLOPS WALTON T1 / WALTON T2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.5 | 7.5509 | 9.9491 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 7.5509 | 9.2341 | 8.3 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.9 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4471 | -2.9683 | 5 | 404738 | 70588
SPM-KIRKBY_CENTRAL_T1_NORTHWOOD_T1_TOWER_HILL_BANK_LA_T1_WESTVAL | Kirkby Central T1 / Northwood T1 / Tower Hill (Bank La) T1 / Westvale T1 | KIRKBY CENTRAL T1 / NORTHWOOD T1 / TOWER HILL (BANK LA) T1 / WESTVALE T1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM |  | 30 | 20.3064 | 9.6936 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.4 | 0 | 20.3064 | 24.9057 | 5.1 | 90.2 | 52.84 | 37.36 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.7 | primary | 0 | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4824 | -2.8867 | 10 | 1754632 | 69162
SPM-TACO_PLASTICS_T1_TACO_PLASTICS_T2_UNITED_PERIPHERALS_T1 | Taco Plastics T1 / Taco Plastics T2 / United Peripherals T1 | TACO PLASTICS T1 / TACO PLASTICS T2 / UNITED PERIPHERALS T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 20 | 10.2736 | 9.7264 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2736 | 11.0853 | 8.9 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.7 | primary | 0 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2005 | -2.4966 | 18 | 1882294 | 69162
SPM-BEAUMONT_ST_T1_DINGLE_VALE_T1_LARK_LA_T1_MDHB_BRUNSWICK_DOCK | Beaumont St T1 / Dingle Vale T1 / Lark La T1 / Mdhb Brunswick Dock T1 | BEAUMONT ST T1 / DINGLE VALE T1 / LARK LA T1 / MDHB BRUNSWICK DOCK T1 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 30 | 20.51 | 9.49 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.51 | 22.1241 | 7.9 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.5 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3974 | -2.9504 | 15 | 549380 | 67736
SPM-CADBURYS_T1_CADBURYS_T2_HOPFIELD_RD_T1 | Cadburys T1 / Cadburys T2 / Hopfield Rd T1 | CADBURYS T1 / CADBURYS T2 / HOPFIELD RD T1 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | WALLASEY GT1 / WALLASEY GT2 / WOODSIDE GT2 | BIRKENHEAD | SPM |  | 20 | 10.473 | 9.527 | Green | thermal | 0 | 0 | 1.5 | 6 | 0 | 0 | 2.2 | 1.7 | 0 | 10.473 | 12.8533 | 7.1 | 95 | 52.555 | 42.195 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.5 | primary | 1.5 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4098 | -3.1105 | 6 | 272026 | 67736
SPM-BUCKINGHAM_ST_T1_EVERTON_RD_T1_SUBURBAN_RD_T1 | Buckingham St T1 / Everton Rd T1 / Suburban Rd T1 | BUCKINGHAM ST T1 / EVERTON RD T1 / SUBURBAN RD T1 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.5 | 8.035 | 9.465 | Green | thermal | 0 | 0 | 0.6 | 3 | 0 | 0 | 0.8 | 0.8 | 0 | 8.035 | 8.354 | 9.1 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.5 | primary | 0.6 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4174 | -2.9668 | 0 | 0 | 67736
SPM-BLUNDELL_ST_T1_ROPEWALKS_T1_ST_JAMES_T1 | Blundell St T1 / Ropewalks T1 / St James T1 | BLUNDELL ST T1 / ROPEWALKS T1 / ST JAMES T1 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 18.5 | 9.14 | 9.36 | Green | thermal | 0 | 0 | 1.9 | 3 | 0 | 0 | 0.5 | 0 | 0 | 9.14 | 9.7922 | 8.7 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.4 | primary | 1.9 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 18.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3975 | -2.9821 | 5 | 112109 | 67023
SPM-DINGLE_T1_GRANBY_T1_ST_JAMES_T2 | Dingle T1 / Granby T1 / St James T2 | DINGLE T1 / GRANBY T1 / ST JAMES T2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 17.5 | 8.434 | 9.066 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.434 | 10.3323 | 7.2 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.1 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3843 | -2.9578 | 10 | 353819 | 64884
SPM-ATHOL_ST_T1_CHISENHALE_ST_T1_SANDHILLS_LA_T1 | Athol St T1 / Chisenhale St T1 / Sandhills La T1 | ATHOL ST T1 / CHISENHALE ST T1 / SANDHILLS LA T1 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.4 | 8.267 | 9.133 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.267 | 9.4584 | 7.9 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9.1 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4244 | -2.9881 | 30 | 1241815 | 64884
SPM-BIRKENHEAD_CENTRAL_T1_SINGLETON_AVE_T1_TRANMERE_T1 | Birkenhead Central T1 / Singleton Ave T1 / Tranmere T1 | BIRKENHEAD CENTRAL T1 / SINGLETON AVE T1 / TRANMERE T1 | PRENTON GRID GT1 / ROCK FERRY GT1 | PRENTON GRID GT1 / ROCK FERRY GT1 | BIRKENHEAD | SPM |  | 18.2 | 9.163 | 9.037 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 0 | 9.163 | 10.9041 | 7.3 | 74.4 | 55.945 | 18.455 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 18.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3824 | -3.0176 | 10 | 346049 | 64171
SPM-OPTICAL_FIBRES_T1_SHOTWICK_T1_WALBRO_T1 | Optical Fibres T1 / Shotwick T1 / Walbro T1 | OPTICAL FIBRES T1 / SHOTWICK T1 / WALBRO T1 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 10.965 | 9.035 | Green | thermal | 0 | 0 | 16.5 | 6 | 0 | 0 | 4.2 | 4.2 | 0 | 10.965 | 12.074 | 7.9 | 51.7 | 41.886 | 9.814 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 9 | primary | 16.5 | Connahs Quay / SASA | [7 empty] | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.231 | -3.0118 | 25 | 3586854 | 64171
SPM-CARLTON_ST_T1_CARLTON_ST_T2_CHALON_WAY_T2 | Carlton St T1 / Carlton St T2 / Chalon Way T2 | CARLTON ST T1 / CARLTON ST T2 / CHALON WAY T2 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAINHILL | SPM |  | 18.2 | 9.37 | 8.83 | Green | thermal | 0 | 0 | 1.5 | 9 | 0 | 0 | 0 | 0 | 0 | 9.37 | 11.4929 | 6.7 | 69.1 | 42.44 | 26.66 | GREEN | 17.1 |  |  |  |  | 0 | 0 | 0 | 0 | 8.8 | primary | 1.5 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 18.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4516 | -2.7514 | 12 | 756377 | 62745
SPM-DIBBINSDALE_T1_PLYMYARD_T1_WIBP_HARDKNOTT_RD_T1 | Dibbinsdale T1 / Plymyard T1 / Wibp Hardknott Rd T1 | DIBBINSDALE T1 / PLYMYARD T1 / WIBP HARDKNOTT RD T1 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BIRKENHEAD | SPM |  | 20 | 11.26 | 8.74 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 4.8 | 0.2 | 11.26 | 13.839 | 6.2 | 71.4 | 49.586 | 21.814 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.7 | primary | 0 | Capenhurst | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3172 | -2.9685 | 13 | 515464 | 62032
SPM-GREASBY_T1_SAUGHALL_MASSIE_T1_UPTON_T1 | Greasby T1 / Saughall Massie T1 / Upton T1 | GREASBY T1 / SAUGHALL MASSIE T1 / UPTON T1 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | BIRKENHEAD | SPM |  | 20 | 11.54 | 8.46 | Green | thermal | 0 | 0 | 0 | 0 | 0.2 | 3 | 0 | 0 | 0 | 11.54 | 15.1083 | 4.9 | 86.9 | 65.376 | 21.2835 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.5 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3845 | -3.0986 | 7 | 389506 | 60606
SPM-NORTH_WALES_PAPER_T1_NORTH_WALES_PAPER_T2_WOODFIELD_AVE_T1 | North Wales Paper T1 / North Wales Paper T2 / Woodfield Ave T1 | NORTH WALES PAPER T1 / NORTH WALES PAPER T2 / WOODFIELD AVE T1 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 11.62 | 8.38 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.62 | 23.6888 | -3.7 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.4 | primary | 0 | Connahs Quay / SASA | [7 empty] | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.236 | -3.1073 | 2 | 240012 | 59893
SPM-ROYAL_INSURANCE_NEW_QUAY_T1_ROYAL_INSURANCE_NEW_QUAY_T2 | Royal Insurance (New Quay) T1 / Royal Insurance (New Quay) T2 | ROYAL INSURANCE (NEW QUAY) T1 / ROYAL INSURANCE (NEW QUAY) T2 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 8.7 | 0.388 | 8.312 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.388 | 0.71172 | 8 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.3 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 8.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4055 | -2.9942 | 10 | 437935 | 59180
SPM-BRITISH_SIDAC_T1_SHERDLEY_RD_T1_ST_HELENS_LINKWAY_T1_WATERY_ | British Sidac T1 / Sherdley Rd T1 / St Helens Linkway T1 / Watery La T1 | BRITISH SIDAC T1 / SHERDLEY RD T1 / ST HELENS LINKWAY T1 / WATERY LA T1 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | BOLD G4B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | 18.2 | 9.924 | 8.276 | Green | thermal | 0 | 0 | 5 | 20 | 0.9 | 4 | 2.6 | 2.6 | 0 | 9.924 | 12.1744 | 6 | 64.6 | 43.2692 | 20.6708 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.3 | primary | 5 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 18.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4429 | -2.7268 | 22 | 2108859 | 59180
SPM-BOLTON_ST_T1_GREEK_ST_T1_HPO_COPPERAS_HILL_T1_OLDHAM_PLACE_T | Bolton St T1 / Greek St T1 / Hpo Copperas Hill T1 / Oldham Place T1 | BOLTON ST T1 / GREEK ST T1 / HPO COPPERAS HILL T1 / OLDHAM PLACE T1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 20 | 11.781 | 8.219 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.4 | 0.4 | 11.781 | 13.1985 | 6.8 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.2 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4062 | -2.9778 | 12 | 240085 | 58467
SPM-ABERYSTWYTH_T1_NORTH_RD_T1_PARC_Y_LLYN_T1_PARC_Y_LLYN_T2_U_C | Aberystwyth T1 / North Rd T1 / Parc-Y-Llyn T1 / Parc-Y-Llyn T2 / U C Wales T1 | ABERYSTWYTH T1 / NORTH RD T1 / PARC-Y-LLYN T1 / PARC-Y-LLYN T2 / U C WALES T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 37.5 | 16.37 | 21.043 | Green | thermal | 0.4 | 10 | 20.2 | 30 | 5.6 | 20 | 2 | 2 | 0.9 | 16.37 | 19.6538 | 17.8 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8.1 | bsp | 20.6 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.4136 | -4.0609 | 23 | 721466 | 57754
SPM-IVY_ST_T1_LLYSFAEN_RD_T1_OLD_MILL_T1 | Ivy St T1 / Llysfaen Rd T1 / Old Mill T1 | IVY ST T1 / LLYSFAEN RD T1 / OLD MILL T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 11.851 | 8.009 | Green | thermal | 0.6 | 4 | 0.6 | 4 | 0.5 | 4 | 0 | 0 | 3 | 11.851 | 14.8468 | 5.2 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 8 | primary | 1.2 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.295 | -3.7265 | 13 | 366863 | 57040
SPM-DEESIDE_IND_PK_T1_DEESIDE_IND_PK_6TH_AVE_T1_RAF_SEALAND_T1 | Deeside Ind Pk T1 / Deeside Ind Pk 6Th Ave T1 / Raf Sealand T1 | DEESIDE IND PK T1 / DEESIDE IND PK 6TH AVE T1 / RAF SEALAND T1 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | DEESIDE PK GRID GT1 / SIXTH AVE GRID GT1 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 12.28 | 7.72 | Green | thermal | 0 | 0 | 16.6 | 30 | 5.6 | 9 | 3.9 | 0.2 | 0.5 | 12.28 | 13.8172 | 6.2 | 51.7 | 41.886 | 9.814 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7.7 | primary | 16.6 | Connahs Quay / SASA | [7 empty] | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2303 | -3.0054 | 42 | 2881545 | 54901
SPM-LORD_ST_T1_MARSHSIDE_T1_MULLARDS_BALMORAL_DV_T1_SOUTHPORT_T2 | Lord St T1 / Marshside T1 / Mullards Balmoral Dv T1 / Southport T2 | LORD ST T1 / MARSHSIDE T1 / MULLARDS BALMORAL DV T1 / SOUTHPORT T2 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM |  | 30 | 19.105 | 7.395 | Green | thermal | 14 | 4 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 3.2 | 19.105 | 24.013 | 6 | 75 | 59.016 | 12.484 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7.4 | primary | 14 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.665 | -2.9742 | 8 | 282431 | 52762
SPM-ASSOCIATED_LEAD_T1_GREAT_BOUGHTON_T1_PIPERS_ASH_T1 | Associated Lead T1 / Great Boughton T1 / Pipers Ash T1 | ASSOCIATED LEAD T1 / GREAT BOUGHTON T1 / PIPERS ASH T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 20 | 12.911 | 7.089 | Green | thermal | 0 | 0 | 2.4 | 3 | 0 | 0 | 1.3 | 1.3 | 0 | 12.911 | 16.1443 | 3.9 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 7.1 | primary | 2.4 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1941 | -2.8742 | 3 | 177707 | 50623
SPM-EVERTON_BROW_T1_GARDNERS_ROW_T1_SHEIL_PK_T1 | Everton Brow T1 / Gardners Row T1 / Sheil Pk T1 | EVERTON BROW T1 / GARDNERS ROW T1 / SHEIL PK T1 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.5 | 10.442 | 7.058 | Green | thermal | 0 | 0 | 1.1 | 3 | 7.4 | 9 | 4.2 | 2.4 | 2.5 | 10.442 | 12.2981 | 5.2 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7.1 | primary | 1.1 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4157 | -2.9744 | 21 | 729231 | 50623
SPM-ARUNDEL_T1_GROVE_PK_T1_WAVERTREE_VALE_T1 | Arundel T1 / Grove Pk T1 / Wavertree Vale T1 | ARUNDEL T1 / GROVE PK T1 / WAVERTREE VALE T1 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 17.5 | 10.447 | 7.053 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.447 | 12.1419 | 5.4 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7.1 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3888 | -2.9283 | 4 | 363421 | 50623
SPM-ORB_CL_T1_STONEBRIDGE_LA_T1_STONEBRIDGE_LA_T2 | Orb Cl T1 / Stonebridge La T1 / Stonebridge La T2 | ORB CL T1 / STONEBRIDGE LA T1 / STONEBRIDGE LA T2 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | KIRKBY | SPM |  | 20 | 9.257 | 10.743 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.257 | 11.5256 | 8.5 | 65 | 57.984 | 7.016 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7 | bsp | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4593 | -2.9112 | 5 | 296890 | 49910
SPM-BEMROSE_T1_CARR_LA_EAST_T1_LUCAS_FAZAKERLEY_T1_NORRIS_GREEN_ | Bemrose T1 / Carr La East T1 / Lucas (Fazakerley) T1 / Norris Green T1 / West Derby T1 | BEMROSE T1 / CARR LA EAST T1 / LUCAS (FAZAKERLEY) T1 / NORRIS GREEN T1 / WEST DERBY T1 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | KIRKBY | SPM |  | 37.5 | 22.857 | 14.643 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.6 | 0 | 22.857 | 27.9544 | 9.5 | 65 | 57.984 | 7.016 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7 | bsp | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4431 | -2.9308 | 17 | 523605 | 49910
SPM-FAZAKERLEY_HOSPITAL_T1_JACOBS_T1_JACOBS_T2_SEEDS_LA_T1 | Fazakerley Hospital T1 / Jacobs T1 / Jacobs T2 / Seeds La T1 | FAZAKERLEY HOSPITAL T1 / JACOBS T1 / JACOBS T2 / SEEDS LA T1 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | KIRKBY | SPM |  | 30 | 13.291 | 16.709 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | 13.291 | 15.3706 | 14.6 | 65 | 57.984 | 7.016 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 7 | bsp | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4592 | -2.9498 | 22 | 841120 | 49910
SPM-HALTON_RD_T1_MURDISHAW_T1_PERCIVAL_LA_T4_RUNCORN_CENTRAL_T1 | Halton Rd T1 / Murdishaw T1 / Percival La T4 / Runcorn Central T1 | HALTON RD T1 / MURDISHAW T1 / PERCIVAL LA T4 / RUNCORN CENTRAL T1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | 25 | 18.063 | 6.937 | Green | thermal | 0 | 0 | 4.4 | 28 | 0 | 0 | 3.1 | 3.1 | 0 | 18.063 | 22.0693 | 2.9 | 106.2 | 72.984 | 32.616 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 6.9 | primary | 4.4 | Frodsham | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 25 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3397 | -2.7169 | 21 | 933572 | 49197
SPM-EGERTON_T1_ROCK_FERRY_T1_SHELL_TRANMERE_T1 | Egerton T1 / Rock Ferry T1 / Shell Tranmere T1 | EGERTON T1 / ROCK FERRY T1 / SHELL TRANMERE T1 | PRENTON GRID GT1 / ROCK FERRY GT1 | PRENTON GRID GT1 / ROCK FERRY GT1 | BIRKENHEAD | SPM |  | 20 | 13.33 | 6.67 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 13.33 | 15.7673 | 4.2 | 74.4 | 55.945 | 18.455 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 6.7 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3644 | -3.0047 | 11 | 209316 | 47771
SPM-BUCKLEY_T1_BUCKLEY_T2_BUCKLEY_CROSS_T1 | Buckley T1 / Buckley T2 / Buckley Cross T1 | BUCKLEY T1 / BUCKLEY T2 / BUCKLEY CROSS T1 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 11.448 | 6.552 | Green | thermal | 6 | 3 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0 | 11.448 | 14.7458 | 5.3 | 119.8 | 87.04 | 32.76 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 6.6 | primary | 6 | Connahs Quay / SASA | [7 empty] | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1643 | -3.0556 | 24 | 670512 | 47058
SPM-PEBLIC_MILLS_T1 | Peblic Mills T1 | PEBLIC MILLS T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 1.15 | 6.35 | Green | thermal | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.2 | 0.2 | 0 | 1.15 | 1.4061 | 6.1 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 6.3 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1332 | -4.2573 | 0 | 0 | 44919
SPM-PILKINGTONS_T1_PILKINGTONS_T2 | Pilkingtons T1 / Pilkingtons T2 | PILKINGTONS T1 / PILKINGTONS T2 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 10 | 3.671 | 6.329 | Green | thermal | 0 | 0 | 1.6 | 4 | 0 | 0 | 1.1 | 0.6 | 0 | 3.671 | 4.0145 | 6 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 6.3 | primary | 1.6 | Connahs Quay / SASA | [7 empty] | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2542 | -3.4722 | 11 | 452750 | 44919
SPM-MONSANTO_T1 | Monsanto T1 | MONSANTO T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 1.54 | 5.96 | Green | thermal | 0 | 0 | 2.1 | 1 | 0 | 0 | 0.1 | 0.1 | 0 | 1.54 | 2.0875 | 5.4 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 6 | primary | 2.1 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9727 | -3.0818 | 1 | 19558 | 42780
SPM-MERES_EDGE_T1_MERES_EDGE_T2 | Meres Edge T1 / Meres Edge T2 | MERES EDGE T1 / MERES EDGE T2 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | INCE LOCAL GT1 / INCE LOCAL GT2 | FRODSHAM - INCE | SPM |  | 10 | 4.2475 | 5.7525 | Green | thermal | 0 | 0 | 6.4 | 8 | 0.2 | 2 | 0.5 | 0.5 | 0 | 4.2475 | 5.3662 | 4.6 | 45 | 18.8567 | 26.1433 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.8 | primary | 6.4 | Frodsham | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2684 | -2.7767 | 2 | 76359 | 41354
SPM-RHM_FOODS_LTD_T1 | Rhm Foods Ltd T1 | RHM FOODS LTD T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 1.71 | 5.79 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 1.803 | 5.7 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.8 | primary | 0 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1755 | -2.4213 | 8 | 1416183 | 41354
SPM-PARC_MENAI_T1 | Parc Menai T1 | PARC MENAI T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 1.655 | 5.845 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.655 | 1.8112 | 5.7 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.8 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2075 | -4.1849 | 2 | 198566 | 41354
SPM-AINTREE_LOCAL_T1_OLD_ROAN_T1_WANGO_LA_T1 | Aintree Local T1 / Old Roan T1 / Wango La T1 | AINTREE LOCAL T1 / OLD ROAN T1 / WANGO LA T1 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | AINTREE GT2 / FAZAKERLEY GT1 / GILLMOSS GT2 | KIRKBY | SPM |  | 20 | 13.315 | 5.725 | Green | thermal | 1.9 | 2 | 4.3 | 16 | 0.5 | 2 | 4.1 | 4.1 | 0 | 13.315 | 16.6038 | 3.4 | 65 | 57.984 | 7.016 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.7 | primary | 6.2 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.477 | -2.9227 | 25 | 1370329 | 40641
SPM-CLUBMOOR_T2_LISTER_DV_A_T1_SUBURBAN_RD_T2 | Clubmoor T2 / Lister Dv A T1 / Suburban Rd T2 | CLUBMOOR T2 / LISTER DV A T1 / SUBURBAN RD T2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.5 | 11.01 | 5.69 | Green | thermal | 2.4 | 3 | 0.5 | 3 | 0 | 0 | 0 | 0 | 0 | 11.01 | 12.9102 | 4.6 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.7 | primary | 2.9 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4341 | -2.9376 | 0 | 0 | 40641
SPM-ENGINEER_PK_T1_PILKINGTONS_QUEENSFERRY_T1_QUEENSFERRY_T1 | Engineer Pk T1 / Pilkingtons Queensferry T1 / Queensferry T1 | ENGINEER PK T1 / PILKINGTONS QUEENSFERRY T1 / QUEENSFERRY T1 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 20 | 14.318 | 5.682 | Green | thermal | 0 | 0 | 2.2 | 3 | 2.6 | 3 | 0 | 0 | 0 | 14.318 | 16.2127 | 3.8 | 119.8 | 87.04 | 32.76 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.7 | primary | 2.2 | Connahs Quay / SASA | [7 empty] | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.203 | -3.0123 | 48 | 2265474 | 40641
SPM-MIDPOINT_POCHIN_WAY_T1 | Midpoint Pochin Way T1 | MIDPOINT POCHIN WAY T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 1.92 | 5.58 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.92 | 2.4867 | 5 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.6 | primary | 0 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1864 | -2.4253 | 8 | 1621567 | 39928
SPM-BOWATER_CONTAINERS_T1_ELLESMERE_PORT_LOCAL_T1_HH_ROBERTSONS_ | Bowater Containers T1 / Ellesmere Port Local T1 / Hh Robertsons T1 / Mobil Oil (E Port) T1 / Whitby T1 | BOWATER CONTAINERS T1 / ELLESMERE PORT LOCAL T1 / HH ROBERTSONS T1 / MOBIL OIL (E PORT) T1 / WHITBY T1 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | CAPENHURST | SPM |  | 25.5 | 19.207 | 5.623 | Green | thermal | 2.7 | 8 | 21.1 | 16 | 0 | 0 | 0.7 | 0.7 | 0 | 19.207 | 24.5256 | 1 | 88.1 | 76.397 | 11.703 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.6 | primary | 23.8 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 25.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2805 | -2.8943 | 66 | 4700124 | 39928
SPM-LLANFWROG_T1_RUTHIN_T1 | Llanfwrog T1 / Ruthin T1 | LLANFWROG T1 / RUTHIN T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 15 | 9.237 | 5.607 | Green | thermal | 0.3 | 4 | 1.1 | 12 | 0.1 | 4 | 0.2 | 0.1 | 0 | 9.237 | 10.8931 | 4.1 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.6 | primary | 1.4 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 15 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1083 | -3.3298 | 15 | 349763 | 39928
SPM-FAIRBOURNE_T1 | Fairbourne T1 | FAIRBOURNE T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 7.5 | 2.036 | 5.464 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.036 | 2.6583 | 4.8 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.5 | primary | 0 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7018 | -4.025 | 0 | 0 | 39215
SPM-KNOWSLEY_T1_MARLED_HEY_T1 | Knowsley T1 / Marled Hey T1 | KNOWSLEY T1 / MARLED HEY T1 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | 10 | 4.46 | 5.54 | Green | thermal | 0 | 0 | 0 | 0 | 5 | 2 | 0 | 0 | 2.5 | 4.46 | 5.5574 | 4.4 | 114.8 | 83.378 | 31.422 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.5 | primary | 0 | Kirkby (_D) | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4366 | -2.8731 | 0 | 0 | 39215
SPM-LLANFAIRFECHAN_T1 | Llanfairfechan T1 | LLANFAIRFECHAN T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 1.994 | 5.506 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.994 | 2.8304 | 4.7 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.5 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2499 | -3.9698 | 0 | 0 | 39215
SPM-BIBBYS_T1_INLAND_REVENUE_OFFICES_T1_REGENT_RD_T1 | Bibbys T1 / Inland Revenue Offices T1 / Regent Rd T1 | BIBBYS T1 / INLAND REVENUE OFFICES T1 / REGENT RD T1 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.5 | 12.12 | 5.38 | Green | thermal | 0 | 0 | 0 | 0 | 1.2 | 3 | 7.5 | 2.5 | 0 | 12.12 | 14.5452 | 3 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.4 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4356 | -2.9978 | 55 | 2145782 | 38502
SPM-LLANARMON_T1 | Llanarmon T1 | LLANARMON T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.215 | 5.285 | Green | thermal | 0 | 0 | 0.6 | 5 | 0 | 2 | 0.1 | 0.1 | 0 | 2.215 | 2.4056 | 5.1 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.3 | primary | 0.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0977 | -3.2174 | 0 | 0 | 37789
SPM-HARRINGTON_ST_T3_LIME_ST_T1 | Harrington St T3 / Lime St T1 | HARRINGTON ST T3 / LIME ST T1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 8.7 | 3.361 | 5.339 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 3.361 | 3.5904 | 5.1 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.3 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 8.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4059 | -2.9872 | 1 | 11800 | 37789
SPM-LEGACY_LOCAL_T1 | Legacy Local T1 | LEGACY LOCAL T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 2.23 | 5.27 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.23 | 2.5565 | 4.9 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.3 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.024 | -3.0583 | 1 | 26958 | 37789
SPM-WINCHAM_T1 | Wincham T1 | WINCHAM T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 2.228 | 5.272 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.228 | 2.6174 | 4.9 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.3 | primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2747 | -2.4855 | 9 | 502423 | 37789
SPM-CABLE_ST_T1_GRADWELL_ST_T2_OLDHAM_PLACE_T2 | Cable St T1 / Gradwell St T2 / Oldham Place T2 | CABLE ST T1 / GRADWELL ST T2 / OLDHAM PLACE T2 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 20 | 14.737 | 5.263 | Green | thermal | 0 | 0 | 0 | 0 | 9 | 3 | 1.3 | 1.3 | 8 | 14.737 | 15.894 | 4.1 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.3 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.403 | -2.9834 | 6 | 152409 | 37789
SPM-ELTON_T1 | Elton T1 | ELTON T1 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | ELLESMERE PORT GT2 / INCE LOCAL GT3 | FRODSHAM - INCE | SPM |  | 7.5 | 2.329 | 5.171 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.329 | 3.0644 | 4.4 | 60 | 25.1423 | 34.8577 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.2 | primary | 0 | Frodsham | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.273 | -2.8127 | 1 | 1683967 | 37076
SPM-ASH_RD_T1_KELLOGGS_WREXHAM_T1_KELLOGGS_WREXHAM_T2 | Ash Rd T1 / Kelloggs (Wrexham) T1 / Kelloggs (Wrexham) T2 | ASH RD T1 / KELLOGGS (WREXHAM) T1 / KELLOGGS (WREXHAM) T2 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 20 | 14.7664 | 5.2336 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.7664 | 16.487 | 3.5 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 5.2 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0484 | -2.9313 | 38 | 5281315 | 37076
SPM-BICC_WREXHAM_T1_MARCHWIEL_T1_WIE_CENTRAL_T1 | Bicc Wrexham T1 / Marchwiel T1 / Wie Central T1 | BICC WREXHAM T1 / MARCHWIEL T1 / WIE CENTRAL T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 20 | 14.774 | 5.226 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 14.774 | 15.7245 | 4.3 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 5.2 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0424 | -2.9163 | 1 | 14588 | 37076
SPM-DUDDON_T1 | Duddon T1 | DUDDON T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 7.5 | 2.14 | 5.16 | Green | thermal | 0.2 | 1 | 0.8 | 7 | 0 | 0 | 1.1 | 0.9 | 0 | 2.14 | 2.6303 | 4.9 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 5.2 | primary | 1 | Frodsham | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1805 | -2.7234 | 1 | 24654 | 37076
SPM-DAILY_POST_ECHO_T1_DAILY_POST_ECHO_T2 | Daily Post & Echo T1 / Daily Post & Echo T2 | DAILY POST & ECHO T1 / DAILY POST & ECHO T2 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 8.7 | 3.54 | 5.16 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.54 | 4.0454 | 4.7 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5.2 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 8.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.409 | -2.9963 | 11 | 425476 | 37076
SPM-GLAN_YR_AFON_T1 | Glan-Yr-Afon T1 | GLAN-YR-AFON T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 |  | TRAWSFYNYDD | SPM |  | 7.5 | 2.326 | 4.986 | Green | thermal | 0.2 | 2 | 2 | 3 | 0 | 1 | 0.4 | 0.2 | 0 | 2.326 | 2.421 | 5.1 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5 | primary | 2.2 | Legacy | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9714 | -3.4602 | 0 | 0 | 35650
SPM-CHESTER_GATES_T1_UNILEVER_DUNKIRK_T1 | Chester Gates T1 / Unilever Dunkirk T1 | CHESTER GATES T1 / UNILEVER DUNKIRK T1 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | CAPENHURST | SPM |  | 10 | 5 | 5 | Green | thermal | 0 | 0 | 1.9 | 10 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6985 | 4.3 | 88.1 | 76.397 | 11.703 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5 | primary | 1.9 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2455 | -2.9288 | 10 | 585339 | 35650
SPM-RHYD_Y_FOEL_T1 | Rhyd-Y-Foel T1 | RHYD-Y-FOEL T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.519 | 4.963 | Green | thermal | 0 | 1 | 1.7 | 2 | 0 | 1 | 0.3 | 0 | 0 | 2.519 | 2.8458 | 4.7 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5 | primary | 1.7 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2678 | -3.6336 | 0 | 0 | 35650
SPM-HASKAYNE_T1 | Haskayne T1 | HASKAYNE T1 | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1B | AINTREE GT1 / FORMBY GT2A / LITHERLAND GT1A | KIRKBY | SPM |  | 7.5 | 2.496 | 5.004 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.496 | 2.778 | 4.7 | 101.9 | 76.2256 | 24.7 | GREEN | 1.5 |  |  |  |  | 0 | 0 | 0 | 0 | 5 | primary | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.5603 | -2.9684 | 4 | 196683 | 35650
SPM-PENMAENMAWR_T1 | Penmaenmawr T1 | PENMAENMAWR T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.479 | 5.021 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.479 | 3.0956 | 4.4 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2646 | -3.9248 | 0 | 0 | 35650
SPM-LOSTOCK_TRIANGLE_T1 | Lostock Triangle T1 | LOSTOCK TRIANGLE T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 2.492 | 5.008 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.492 | 3.0516 | 4.4 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 5 | primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2708 | -2.4602 | 12 | 383326 | 35650
SPM-LCWW_HUNTINGTON_T1_LCWW_HUNTINGTON_T2 | Lcww Huntington T1 / Lcww Huntington T2 | LCWW HUNTINGTON T1 / LCWW HUNTINGTON T2 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 9.1 | 4.1793 | 4.9207 | Green | thermal | 0 | 0 | 2.5 | 12 | 0 | 0 | 1.8 | 1.8 | 0.1 | 4.1793 | 4.4464 | 4.7 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 4.9 | primary | 2.5 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 9.1 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1698 | -2.8667 | 1 | 14132 | 34937
SPM-POINT_OF_AYR_COLLIERY_T1 | Point Of Ayr Colliery T1 | POINT OF AYR COLLIERY T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.5891 | 4.9109 | Green | thermal | 0 | 0 | 0.1 | 1 | 0 | 0 | 0.7 | 0.7 | 0 | 2.5891 | 3.0535 | 4.4 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.9 | primary | 0.1 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3409 | -3.3147 | 3 | 331770 | 34937
SPM-BODFARI_PRODUCERS_T1 | Bodfari Producers T1 | BODFARI PRODUCERS T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 7.5 | 2.751 | 4.749 | Green | thermal | 0 | 0 | 0.8 | 5 | 0 | 0 | 1 | 0.6 | 0 | 2.751 | 2.9305 | 4.6 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 4.7 | primary | 0.8 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1544 | -2.9279 | 0 | 0 | 33511
SPM-ABERDYFI_T1 | Aberdyfi T1 | ABERDYFI T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 7.5 | 2.81 | 4.69 | Green | thermal | 0 | 0 | 0.2 | 1 | 0 | 0 | 0.1 | 0.1 | 0 | 2.81 | 3.1567 | 4.3 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.7 | primary | 0.2 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5451 | -4.0605 | 2 | 30777 | 33511
SPM-BEECH_ST_T1_LISTER_DV_A_T2 | Beech St T1 / Lister Dv A T2 | BEECH ST T1 / LISTER DV A T2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DV B GT3 / SPARLING ST GT1 / WAVERTREE GT2 | LISTER DRIVE | SPM |  | 8.7 | 4.0554 | 4.6446 | Green | thermal | 0 | 0 | 2.1 | 4 | 1.4 | 4 | 0.3 | 0.3 | 0 | 4.0554 | 5.122 | 3.6 | 138.4 | 86.729 | 51.671 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.6 | primary | 2.1 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 8.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4104 | -2.9425 | 4 | 256987 | 32798
SPM-OTIS_ELEVATOR_T1_ST_IVEL_FOODS_T1 | Otis Elevator T1 / St Ivel Foods T1 | OTIS ELEVATOR T1 / ST IVEL FOODS T1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM |  | 10 | 5.441 | 4.559 | Green | thermal | 0 | 0 | 4 | 2 | 0 | 0 | 2.2 | 0.8 | 0 | 5.441 | 5.5231 | 4.5 | 90.2 | 52.84 | 37.36 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.6 | primary | 4 | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4683 | -2.8721 | 0 | 0 | 32798
SPM-FERODO_T1 | Ferodo T1 | FERODO T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.86 | 4.64 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.8 | 0 | 2.86 | 3.1457 | 4.4 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.6 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1654 | -4.2457 | 3 | 65005 | 32798
SPM-LLANRWST_T1 | Llanrwst T1 | LLANRWST T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.736 | 4.535 | Green | thermal | 0.2 | 3 | 0.2 | 3 | 0 | 0 | 0.1 | 0.1 | 0 | 2.736 | 3.1719 | 4.3 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.5 | primary | 0.4 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1332 | -3.7827 | 2 | 55008 | 32085
SPM-PRIMROSE_HALL_T1 | Primrose Hall T1 | PRIMROSE HALL T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 2.973 | 4.527 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.973 | 3.3267 | 4.2 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.5 | primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1976 | -2.3771 | 0 | 0 | 32085
SPM-LLANSANNAN_T1 | Llansannan T1 | LLANSANNAN T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 2.965 | 4.48 | Green | thermal | 0.1 | 1 | 0.2 | 2 | 0 | 0 | 0.5 | 0.5 | 0 | 2.965 | 3.1551 | 4.3 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.5 | primary | 0.3 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1789 | -3.5853 | 2 | 35309 | 32085
SPM-LLANGOLLEN_T1_LLANGOLLEN_T2 | Llangollen T1 / Llangollen T2 | LLANGOLLEN T1 / LLANGOLLEN T2 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 10 | 5.47 | 4.53 | Green | thermal | 0 | 0 | 0.6 | 6 | 0 | 0 | 0.1 | 0.1 | 0 | 5.47 | 6.3913 | 3.6 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.5 | primary | 0.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9657 | -3.1622 | 3 | 73351 | 32085
SPM-CADBURYS_KRONOSPAN_T1_CADBURYS_KRONOSPAN_T2 | Cadburys Kronospan T1 / Cadburys Kronospan T2 | CADBURYS KRONOSPAN T1 / CADBURYS KRONOSPAN T2 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 10 | 5.598 | 4.402 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.598 | 6.2509 | 3.7 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.4 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9366 | -3.0668 | 3 | 1597464 | 31372
SPM-BARMOUTH_T1 | Barmouth T1 | BARMOUTH T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 2.408 | 5.092 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0 | 2.408 | 2.9103 | 4.6 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | bsp | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7249 | -4.0594 | 0 | 0 | 30659
SPM-PORTHMADOG_T1_PORTHMADOG_T2 | Porthmadog T1 / Porthmadog T2 | PORTHMADOG T1 / PORTHMADOG T2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 10 | 4.522 | 5.478 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.522 | 5.7115 | 4.3 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | bsp | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.934 | -4.1345 | 9 | 280456 | 30659
SPM-DYFFRYN_ARDUDWY_T1 | Dyffryn Ardudwy T1 | DYFFRYN ARDUDWY T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 2.164 | 5.336 | Green | thermal | 0 | 0 | 0.5 | 5 | 0.3 | 3 | 0.1 | 0 | 0.7 | 2.164 | 2.9866 | 4.5 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | bsp | 0.5 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7818 | -4.1 | 0 | 0 | 30659
SPM-BOTWNNOG_T1 | Botwnnog T1 | BOTWNNOG T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 2.533 | 4.967 | Green | thermal | 0 | 0 | 0.4 | 3 | 0 | 0 | 0.2 | 0.1 | 0 | 2.533 | 2.8374 | 4.7 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | bsp | 0.4 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8489 | -4.5797 | 0 | 0 | 30659
SPM-HARLECH_T1 | Harlech T1 | HARLECH T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 2.293 | 5.163 | Green | thermal | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0.1 | 2.293 | 2.8978 | 4.6 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | bsp | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8637 | -4.1058 | 0 | 0 | 30659
SPM-MAENTWROG_T1 | Maentwrog T1 | MAENTWROG T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 1.585 | 5.915 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1.585 | 1.7856 | 5.7 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | bsp | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9358 | -4.0036 | 0 | 0 | 30659
SPM-WERVIN_T1 | Wervin T1 | WERVIN T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 7.5 | 3.16 | 4.34 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 3.5833 | 3.9 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 4.3 | primary | 0 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2305 | -2.8668 | 2 | 107594 | 30659
SPM-LLANDUDNO_T1_LLANDUDNO_T2 | Llandudno T1 / Llandudno T2 | LLANDUDNO T1 / LLANDUDNO T2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 10 | 5.822 | 4.178 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.4 | 0 | 5.822 | 6.7903 | 3.2 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.2 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3139 | -3.8245 | 5 | 99801 | 29946
SPM-DELAMORE_ST_T1_KIRKDALE_T1_WALTON_T1 | Delamore St T1 / Kirkdale T1 / Walton T1 | DELAMORE ST T1 / KIRKDALE T1 / WALTON T1 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | BOOTLE GT2A / BURLINGTON ST GT1 / LISTER DV A GT2 | LISTER DRIVE | SPM |  | 17.4 | 13.2356 | 4.1644 | Green | thermal | 0 | 0 | 2.1 | 9 | 0 | 0 | 0.6 | 0.6 | 0 | 13.2356 | 16.5857 | 0.8 | 138.1 | 75.432 | 61.868 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.2 | primary | 2.1 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 17.4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4294 | -2.9723 | 8 | 258012 | 29946
SPM-RHOSLAN_T1 | Rhoslan T1 | RHOSLAN T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 3.371 | 4.129 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 3.371 | 4.5475 | 3 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.1 | primary | 0 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9426 | -4.2615 | 3 | 73767 | 29233
SPM-MOCHDRE_T1 | Mochdre T1 | MOCHDRE T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 3.364 | 4.136 | Green | thermal | 0 | 0 | 0 | 1 | 0 | 0 | 1.3 | 1.3 | 0 | 3.364 | 3.9863 | 3.5 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4.1 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5014 | -3.3338 | 10 | 760428 | 29233
SPM-APPLETON_T1_HORNSBRIDGE_T1_LUGSDALE_T2 | Appleton T1 / Hornsbridge T1 / Lugsdale T2 | APPLETON T1 / HORNSBRIDGE T1 / LUGSDALE T2 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G4A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM |  | 20 | 15.892 | 4.108 | Green | thermal | 0 | 0 | 0 | 0 | 7.5 | 6 | 1.6 | 1.6 | 0 | 15.892 | 18.7925 | 1.2 | 110.6 | 77.52 | 23.6331 | GREEN | 4.9 |  |  |  |  | 0 | 0 | 0 | 0 | 4.1 | primary | 0 | Fiddlers Ferry | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3853 | -2.7163 | 15 | 720288 | 29233
SPM-MDHB_EGERTON_DOCK_T1_MDHB_EGERTON_DOCK_T2 | Mdhb Egerton Dock T1 / Mdhb Egerton Dock T2 | MDHB EGERTON DOCK T1 / MDHB EGERTON DOCK T2 | PRENTON GRID GT1 / ROCK FERRY GT1 | PRENTON GRID GT1 / ROCK FERRY GT1 | BIRKENHEAD | SPM |  | 9.1 | 5.144 | 3.956 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.144 | 5.6591 | 3.4 | 74.4 | 55.945 | 18.455 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4 | primary | 0 | Birkenhead | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 9.1 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3989 | -3.0219 | 13 | 462581 | 28520
SPM-BETWS_Y_COED_T1 | Betws-Y-Coed T1 | BETWS-Y-COED T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 3.488 | 3.994 | Green | thermal | 0 | 1 | 0 | 0 | 0 | 0 | 1.4 | 1.4 | 0 | 3.488 | 3.8922 | 3.6 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0932 | -3.8016 | 2 | 26859 | 28520
SPM-LLANFROTHEN_T1 | Llanfrothen T1 | LLANFROTHEN T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 3.123 | 4.049 | Green | thermal | 0.3 | 2 | 0 | 0 | 0 | 1 | 0.1 | 0.1 | 0 | 3.123 | 4.1613 | 3.3 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4 | primary | 0.3 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9417 | -4.061 | 2 | 60481 | 28520
SPM-BALA_T1 | Bala T1 | BALA T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 3.545 | 3.955 | Green | thermal | 0 | 0 | 0 | 2 | 0 | 0 | 0.1 | 0 | 0.1 | 3.545 | 3.9938 | 3.5 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 4 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9202 | -3.5865 | 3 | 96606 | 28520
SPM-GADBROOK_T1 | Gadbrook T1 | GADBROOK T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 3.617 | 3.883 | Green | thermal | 0 | 0 | 0.3 | 4 | 0.5 | 1 | 0.8 | 0.8 | 0 | 3.617 | 4.2897 | 3.2 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.9 | primary | 0.3 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.248 | -2.4819 | 3 | 99261 | 27807
SPM-GREENFIELD_T1_GREENFIELD_T2 | Greenfield T1 / Greenfield T2 | GREENFIELD T1 / GREENFIELD T2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 10 | 6.084 | 3.916 | Green | thermal | 0 | 0 | 0.5 | 2 | 0 | 0 | 0 | 0 | 0 | 6.084 | 8.8347 | 1.2 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.9 | primary | 0.5 | Connahs Quay / SASA | [7 empty] | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2929 | -3.2028 | 15 | 1075021 | 27807
SPM-EGA_ELECTRIC_T1 | Ega Electric T1 | EGA ELECTRIC T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 3.724 | 3.776 | Green | thermal | 0 | 0 | 3.5 | 6 | 1.1 | 2 | 0.9 | 0.9 | 0 | 3.724 | 4.2937 | 3.2 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.8 | primary | 3.5 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2523 | -3.452 | 6 | 242379 | 27094
SPM-CROWTON_T1 | Crowton T1 | CROWTON T1 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | INCE LOCAL GT1 / INCE LOCAL GT2 | FRODSHAM - INCE | SPM |  | 7.5 | 3.732 | 3.768 | Green | thermal | 0 | 0 | 2 | 3 | 0 | 0 | 0.6 | 0.6 | 0 | 3.732 | 4.3392 | 3.2 | 45 | 18.8567 | 26.1433 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.8 | primary | 2 | Frodsham | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2613 | -2.6324 | 1 | 17069 | 27094
SPM-OVERTON_T1 | Overton T1 | OVERTON T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 3.697 | 3.803 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.697 | 4.4887 | 3 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.8 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9591 | -2.9134 | 4 | 101581 | 27094
SPM-AINSDALE_T1_PINFOLD_LA_T1 | Ainsdale T1 / Pinfold La T1 | AINSDALE T1 / PINFOLD LA T1 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM |  | 9.1 | 5.27 | 3.83 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.27 | 6.6581 | 2.4 | 75 | 59.016 | 12.484 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.8 | primary | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | 9.1 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.603 | -3.0354 | 1 | 23754 | 27094
SPM-BRITISH_PIPE_ASSOCIATION_T1 | British Pipe Association T1 | BRITISH PIPE ASSOCIATION T1 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | ELLESMERE PORT GT2 / INCE LOCAL GT3 | FRODSHAM - INCE | SPM |  | 7.5 | 3.693 | 3.807 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.693 | 4.2916 | 3.2 | 60 | 25.1423 | 34.8577 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.8 | primary | 0 | Capenhurst | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2647 | -2.8722 | 10 | 981027 | 27094
SPM-CAERSWS_T1 | Caersws T1 | CAERSWS T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 3.671 | 3.811 | Green | thermal | 0 | 1 | 1 | 5 | 0.1 | 2 | 0.7 | 0.3 | 0 | 3.671 | 4.2678 | 3.2 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.8 | primary | 1 | Trawsfynydd | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5233 | -3.4199 | 3 | 197972 | 27094
SPM-MAELOR_CREAMERY_T1 | Maelor Creamery T1 | MAELOR CREAMERY T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 7.5 | 3.77 | 3.712 | Green | thermal | 0 | 1 | 0.1 | 1 | 0 | 0 | 2.8 | 2.8 | 0.1 | 3.77 | 3.9548 | 3.5 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 3.7 | primary | 0.1 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0139 | -2.9162 | 1 | 20422 | 26381
SPM-ST_ASAPH_BUSINESS_PK_T1 | St Asaph Business Pk T1 | ST ASAPH BUSINESS PK T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 3.823 | 3.677 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.823 | 4.6224 | 2.9 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.7 | primary | 0 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.259 | -3.4736 | 17 | 825644 | 26381
SPM-BUTLINS_T1 | Butlins T1 | BUTLINS T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 3.796 | 3.704 | Green | thermal | 0 | 0 | 0.8 | 4 | 0 | 1 | 0.7 | 0.5 | 0 | 3.796 | 3.9954 | 3.5 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.7 | primary | 0.8 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9064 | -4.3369 | 2 | 34635 | 26381
SPM-YSBYTY_GLAN_CLWYD_T1 | Ysbyty Glan Clwyd T1 | YSBYTY GLAN CLWYD T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 3.938 | 3.562 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.938 | 4.0696 | 3.4 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.6 | primary | 0 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2712 | -3.4984 | 0 | 0 | 25668
SPM-DEESIDE_ALUMINIUM_T1_DUNLOP_PLASTICS_T1_FIRESTONE_T1_TETRAPA | Deeside Aluminium T1 / Dunlop Plastics T1 / Firestone T1 / Tetrapak T1 | DEESIDE ALUMINIUM T1 / DUNLOP PLASTICS T1 / FIRESTONE T1 / TETRAPAK T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 30 | 26.386 | 3.614 | Green | thermal | 0 | 0 | 0.1 | 4 | 0 | 0 | 1.8 | 0 | 0.5 | 26.386 | 28.0622 | 1.9 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 3.6 | primary | 0.1 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0368 | -2.9321 | 46 | 4448049 | 25668
SPM-ST_HELENS_RD_T1 | St Helens Rd T1 | ST HELENS RD T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 3.937 | 3.563 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.937 | 4.6938 | 2.8 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.6 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1338 | -4.2721 | 6 | 181281 | 25668
SPM-ROSSETT_T1 | Rossett T1 | ROSSETT T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 7.5 | 3.967 | 3.533 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.967 | 4.6463 | 2.9 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 3.5 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1056 | -2.9468 | 1 | 12277 | 24955
SPM-LLANSILIN_T1 | Llansilin T1 | LLANSILIN T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 3.891 | 3.534 | Green | thermal | 0.1 | 2 | 1.1 | 6 | 0 | 0 | 2.9 | 0.6 | 1.7 | 3.891 | 4.4042 | 3.1 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.5 | primary | 1.2 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.85 | -3.1685 | 0 | 0 | 24955
SPM-WAENFAWR_T1 | Waenfawr T1 | WAENFAWR T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 4.005 | 3.495 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.005 | 4.9109 | 2.6 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.5 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1239 | -4.2014 | 5 | 224759 | 24955
SPM-KINNERTON_T1 | Kinnerton T1 | KINNERTON T1 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 4.088 | 3.412 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.088 | 4.608 | 2.9 | 119.8 | 87.04 | 32.76 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.4 | primary | 0 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.156 | -2.9764 | 1 | 177680 | 24242
SPM-FLINT_T1_FLINT_T2 | Flint T1 / Flint T2 | FLINT T1 / FLINT T2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 10 | 6.44 | 3.443 | Green | thermal | 0.2 | 4 | 4.4 | 6 | 0.5 | 2 | 3.6 | 3.6 | 0 | 6.44 | 14.699 | -4.7 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.4 | primary | 4.6 | Connahs Quay / SASA | [7 empty] | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2522 | -3.142 | 21 | 1882460 | 24242
SPM-MORRISONS_T1 | Morrisons T1 | MORRISONS T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 4.109 | 3.391 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.109 | 4.8161 | 2.7 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.4 | primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2489 | -2.4731 | 6 | 1193682 | 24242
SPM-LLYNCLYS_T1 | Llynclys T1 | LLYNCLYS T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 4.209 | 3.291 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.209 | 4.8393 | 2.7 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.3 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8085 | -3.0627 | 1 | 118434 | 23529
SPM-DAVY_WAY_T1_LLAY_T1 | Davy Way T1 / Llay T1 | DAVY WAY T1 / LLAY T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 10 | 6.742 | 3.258 | Green | thermal | 0 | 0 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0.1 | 6.742 | 7.6473 | 2.4 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 3.3 | primary | 0.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1 | -3.0065 | 19 | 1006086 | 23529
SPM-MORDA_T1 | Morda T1 | MORDA T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 4.227 | 3.273 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.227 | 5.0389 | 2.5 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.3 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8479 | -3.0547 | 1 | 50716 | 23529
SPM-RHUDDLAN_T1 | Rhuddlan T1 | RHUDDLAN T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 4.2084 | 3.2916 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2084 | 5.1864 | 2.3 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.3 | primary | 0 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2842 | -3.4688 | 11 | 295984 | 23529
SPM-TYWYN_T1 | Tywyn T1 | TYWYN T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 7.5 | 4.266 | 3.165 | Green | thermal | 0.1 | 1 | 0.2 | 3 | 0 | 1 | 0.2 | 0.1 | 0 | 4.266 | 5.4756 | 2 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.2 | primary | 0.3 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5876 | -4.0803 | 2 | 38475 | 22816
SPM-PWLLHELI_T1 | Pwllheli T1 | PWLLHELI T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 4.296 | 3.204 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.296 | 5.5762 | 1.9 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.2 | primary | 0 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8945 | -4.4168 | 6 | 182789 | 22816
SPM-MILFORD_T1 | Milford T1 | MILFORD T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 4.332 | 3.168 | Green | thermal | 0 | 0 | 1 | 1 | 0 | 0 | 0.8 | 0.8 | 0 | 4.332 | 5.3111 | 2.2 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.2 | primary | 1 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5048 | -3.3364 | 4 | 68958 | 22816
SPM-LOSTOCK_T1 | Lostock T1 | LOSTOCK T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 4.362 | 3.138 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.362 | 5.2201 | 2.3 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.1 | primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2665 | -2.4632 | 4 | 146487 | 22103
SPM-EXPRESS_FOODS_T1 | Express Foods T1 | EXPRESS FOODS T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 7.5 | 1.499 | 6.001 | Green | thermal | 0 | 0 | 1.3 | 5 | 0 | 1 | 0.2 | 0.2 | 0.2 | 1.499 | 1.6079 | 5.9 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.1 | bsp | 1.3 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7956 | -2.9062 | 1 | 100179 | 22103
SPM-LIVERPOOL_RD_33_T1 | Liverpool Rd 33 T1 | LIVERPOOL RD 33 T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 11 | 3.943 | 7.057 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 2.1 | 0.1 | 3.943 | 4.5192 | 6.5 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.1 | bsp | 0 | Frodsham | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 11 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9641 | -2.6919 | 4 | 197050 | 22103
SPM-YOCKINGS_GATE_T1 | Yockings Gate T1 | YOCKINGS GATE T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 10 | 3.443 | 6.557 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.443 | 4.0577 | 5.9 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.1 | bsp | 0 | Frodsham | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9733 | -2.6756 | 10 | 900974 | 22103
SPM-WEM_EAST_T1 | Wem East T1 | WEM EAST T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 7.5 | 3.17 | 4.33 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 3.7703 | 3.7 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.1 | bsp | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8612 | -2.7089 | 8 | 188389 | 22103
SPM-WHITCHURCH_T1 | Whitchurch T1 | WHITCHURCH T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 11 | 5.078 | 5.665 | Green | thermal | 0.5 | 6 | 2.4 | 18 | 3.7 | 8 | 0 | 0 | 0 | 5.078 | 5.9003 | 5.1 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3.1 | bsp | 2.9 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 11 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9802 | -2.7074 | 2 | 35265 | 22103
SPM-HUYTON_HEY_RD_T1_WILSON_RD_T1 | Huyton Hey Rd T1 / Wilson Rd T1 | HUYTON HEY RD T1 / WILSON RD T1 | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM |  | 10 | 7.044 | 2.956 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.044 | 8.9081 | 1.1 | 114.8 | 83.378 | 31.422 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 0 | Kirkby (_D) | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4102 | -2.8346 | 8 | 225699 | 21390
SPM-HOLYWELL_T1 | Holywell T1 | HOLYWELL T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 4.214 | 3.006 | Green | thermal | 0.3 | 2 | 1.2 | 1 | 0 | 0 | 0.3 | 0 | 0.2 | 4.214 | 5.0425 | 2.5 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 1.5 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2587 | -3.2809 | 4 | 100080 | 21390
SPM-WEM_T1 | Wem T1 | WEM T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 7.5 | 4.516 | 2.984 | Green | thermal | 0 | 0 | 0.6 | 4 | 0 | 0 | 2.9 | 2.9 | 0 | 4.516 | 5.1268 | 2.4 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 0.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8612 | -2.7089 | 3 | 112927 | 21390
SPM-HARRINGTON_ST_T1_PARADISE_ST_T1 | Harrington St T1 / Paradise St T1 | HARRINGTON ST T1 / PARADISE ST T1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 8.7 | 5.731 | 2.969 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.731 | 6.7666 | 1.9 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 8.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4059 | -2.9872 | 13 | 396528 | 21390
SPM-IFTON_T1_IFTON_T2 | Ifton T1 / Ifton T2 | IFTON T1 / IFTON T2 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 10 | 6.803 | 2.957 | Green | thermal | 0.5 | 2 | 1.3 | 10 | 1.4 | 2 | 2.7 | 2.5 | 0.5 | 6.803 | 8.4439 | 1.6 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 1.8 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9285 | -3.0092 | 11 | 331264 | 21390
SPM-CWM_DYLI_T1 | Cwm Dyli T1 | CWM DYLI T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 1.04 | 2.96 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 1.1102 | 2.9 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.066 | -4.0114 | 0 | 0 | 21390
SPM-DOLGELLAU_T1 | Dolgellau T1 | DOLGELLAU T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 4.37 | 3.03 | Green | thermal | 0.1 | 1 | 0.1 | 3 | 1 | 2 | 1.8 | 1.8 | 0 | 4.37 | 5.2971 | 2.2 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 3 | primary | 0.2 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7422 | -3.8725 | 5 | 131760 | 21390
SPM-BXL_BROMBOROUGH_T1_TULIP_T1 | Bxl Bromborough T1 / Tulip T1 | BXL BROMBOROUGH T1 / TULIP T1 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BROMBOROUGH GT3 / ROCK FERRY GT2 | BIRKENHEAD | SPM |  | 10 | 6.084 | 2.861 | Green | thermal | 2.1 | 4 | 1.9 | 8 | 0 | 0 | 0 | 0 | 0 | 6.084 | 7.6032 | 2.4 | 71.4 | 49.586 | 21.814 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.9 | primary | 4 | Capenhurst | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 |  | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.336 | -2.9624 | 29 | 1821917 | 20677
SPM-MANOD_T1 | Manod T1 | MANOD T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 1.15 | 2.85 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 1.3026 | 2.7 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.9 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.969 | -3.9303 | 1 | 11043 | 20677
SPM-HOOTON_MAIN_T1 | Hooton Main T1 | HOOTON MAIN T1 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | CAPENHURST | SPM |  | 7.5 | 4.659 | 2.772 | Green | thermal | 0.1 | 1 | 0.2 | 2 | 0 | 0 | 0 | 0 | 0.2 | 4.659 | 6.2653 | 1.2 | 88.1 | 76.397 | 11.703 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.8 | primary | 0.3 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2967 | -2.9813 | 13 | 1363156 | 19964
SPM-CHOWLEY_T1_CHOWLEY_T2 | Chowley T1 / Chowley T2 | CHOWLEY T1 / CHOWLEY T2 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 10 | 6.64 | 2.822 | Green | thermal | 1.1 | 4 | 0.2 | 4 | 1.3 | 2 | 1.8 | 1.8 | 0.2 | 6.64 | 7.7878 | 2.2 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 2.8 | primary | 1.3 | Capenhurst | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1007 | -2.7886 | 6 | 111550 | 19964
SPM-HOLWAY_RD_T1 | Holway Rd T1 | HOLWAY RD T1 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 4.833 | 2.667 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.833 | 6.0418 | 1.5 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.7 | primary | 0 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2763 | -3.2292 | 3 | 68054 | 19251
SPM-MAES_Y_CLAWDD_T1 | Maes-Y-Clawdd T1 | MAES-Y-CLAWDD T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 4.768 | 2.732 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.768 | 5.834 | 1.7 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.7 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.845 | -3.0344 | 25 | 994976 | 19251
SPM-MANOR_PK_T1_NORTON_CHAINS_T1 | Manor Pk T1 / Norton Chains T1 | MANOR PK T1 / NORTON CHAINS T1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM |  | 10 | 7.301 | 2.699 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.301 | 8.1984 | 1.8 | 106.2 | 72.984 | 32.616 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.7 | primary | 0 | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.349 | -2.6722 | 14 | 2598695 | 19251
SPM-BRITISH_OXYGEN_T1_WINDLEHURST_T1 | British Oxygen T1 / Windlehurst T1 | BRITISH OXYGEN T1 / WINDLEHURST T1 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAINHILL | SPM |  | 9.1 | 6.42 | 2.68 | Green | thermal | 0 | 0 | 5.4 | 4 | 5 | 4 | 0 | 0 | 0 | 6.42 | 7.8606 | 1.2 | 69.1 | 42.44 | 26.66 | GREEN | 17.1 |  |  |  |  | 0 | 0 | 0 | 0 | 2.7 | primary | 5.4 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 9.1 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4644 | -2.7506 | 3 | 134953 | 19251
SPM-GREAT_SUTTON_T1_LITTLE_SUTTON_T1_STRAWBERRY_ROUNDABOUT_T1_SU | Great Sutton T1 / Little Sutton T1 / Strawberry Roundabout T1 / Sutton Hall Wwb T1 / Whitby Main T2 | GREAT SUTTON T1 / LITTLE SUTTON T1 / STRAWBERRY ROUNDABOUT T1 / SUTTON HALL WWB T1 / WHITBY MAIN T2 | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | BROMBOROUGH GT2 / ELLESMERE PORT GT1 / HOOTON PK GT1A / HOOTON PK GT2A | CAPENHURST | SPM |  | 26.4 | 23.7904 | 2.6096 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 4.1 | 1.4 | 23.7904 | 29.0256 | -2.6 | 88.1 | 76.397 | 11.703 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.6 | primary | 0 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 26.4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2723 | -2.9221 | 2 | 144808 | 18538
SPM-DOLGARROG_T1_DOLGARROG_T2 | Dolgarrog T1 / Dolgarrog T2 | DOLGARROG T1 / DOLGARROG T2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 4.996 | 2.504 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.996 | 5.4129 | 2.1 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.5 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1918 | -3.8419 | 0 | 0 | 17825
SPM-NANT_Y_GAMAR_T1 | Nant-Y-Gamar T1 | NANT-Y-GAMAR T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 5.003 | 2.497 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.003 | 6.2465 | 1.3 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.5 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3185 | -3.8012 | 2 | 70097 | 17825
SPM-RHYDLYDAN_T2 | Rhydlydan T2 | RHYDLYDAN T2 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 4 | 1.526 | 2.474 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.526 | 1.6117 | 2.4 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.5 | primary | 0 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.4128 | -3.8781 | 0 | 0 | 17825
SPM-GIGG_LA_THELWALL_T1_HILLCLIFFE_T1_STOCKTON_HEATH_T1_STRETTON | Gigg La Thelwall T1 / Hillcliffe T1 / Stockton Heath T1 / Stretton Ind Est T1 | GIGG LA THELWALL T1 / HILLCLIFFE T1 / STOCKTON HEATH T1 / STRETTON IND EST T1 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM |  | 30 | 19.291 | 10.609 | Green | thermal | 0.4 | 4 | 1.3 | 12 | 2.2 | 12 | 3.7 | 2.6 | 0 | 19.291 | 23.3248 | 6.7 | 75.4 | 65.191 | 2.392 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.4 | bsp | 1.7 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3828 | -2.525 | 27 | 1489152 | 17112
SPM-JOHNSTOWN_T1 | Johnstown T1 | JOHNSTOWN T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 5.14 | 2.36 | Green | thermal | 0 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 5.14 | 6.0818 | 1.4 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.4 | primary | 0.2 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0012 | -3.0369 | 7 | 553162 | 17112
SPM-MIDDLEWICH_T1 | Middlewich T1 | MIDDLEWICH T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 5.063 | 2.437 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.063 | 6.1476 | 1.4 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.4 | primary | 0 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.197 | -2.4256 | 18 | 1143143 | 17112
SPM-CROSSFIELDS_T1_CROSSFIELDS_T2_LEVERS_CROSSFIELDS_T3_GATEWART | Crossfields T1 / Crossfields T2 / Levers Crossfields T3 / Gatewarth Sewage T1 | CROSSFIELDS T1 / CROSSFIELDS T2 / LEVERS CROSSFIELDS T3 / GATEWARTH SEWAGE T1 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM |  | 30 | 9.749 | 20.251 | Green | thermal | 0 | 0 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 9.749 | 10.5876 | 19.4 | 75.4 | 65.191 | 2.392 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.4 | bsp | 2 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3806 | -2.6291 | 9 | 245588 | 17112
SPM-LLANDYRNOG_T1 | Llandyrnog T1 | LLANDYRNOG T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 5 | 2.51 | 2.438 | Green | thermal | 0.1 | 3 | 0.1 | 2 | 0 | 0 | 0.7 | 0.4 | 0 | 2.51 | 2.7564 | 2.2 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.4 | primary | 0.2 | Connahs Quay / SASA | [7 empty] | 5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1811 | -3.3301 | 2 | 181382 | 17112
SPM-MACHYNLLETH_T2 | Machynlleth T2 | MACHYNLLETH T2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 1.503 | 2.327 | Green | thermal | 0.2 | 2 | 0.1 | 2 | 0.1 | 1 | 0 | 0 | 0 | 1.503 | 1.6374 | 2.4 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.3 | primary | 0.3 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5908 | -3.8324 | 0 | 0 | 16399
SPM-CEFN_MAWR_T1 | Cefn Mawr T1 | CEFN MAWR T1 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 3.739 | 2.3455 | Green | thermal | 1.4 | 10 | 1.2 | 11 | 0 | 0 | 3.1 | 2.5 | 0 | 3.739 | 4.9462 | 2.6 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.3 | primary | 2.6 | Connahs Quay / SASA | [7 empty] | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.167 | -3.1985 | 0 | 0 | 16399
SPM-BETHESDA_T1 | Bethesda T1 | BETHESDA T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 5.115 | 2.203 | Green | thermal | 0.2 | 2 | 3.3 | 9 | 6.1 | 5 | 0.9 | 0.8 | 1 | 5.115 | 6.2586 | 1.2 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.2 | primary | 3.5 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1751 | -4.0701 | 4 | 104598 | 15686
SPM-CORWEN_T1 | Corwen T1 | CORWEN T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 7.5 | 5.281 | 2.219 | Green | thermal | 0 | 0 | 1 | 1 | 0 | 0 | 1.7 | 1.1 | 0.1 | 5.281 | 6.7114 | 0.8 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.2 | primary | 1 | Legacy | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9798 | -3.3979 | 9 | 471596 | 15686
SPM-ANDERTON_T1 | Anderton T1 | ANDERTON T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 4.4608 | 2.2292 | Green | thermal | 0.8 | 2 | 1.6 | 5 | 0.2 | 1 | 2.1 | 0.8 | 0 | 4.4608 | 5.9764 | 1.5 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.2 | primary | 2.4 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2774 | -2.5281 | 0 | 0 | 15686
SPM-PEN_Y_GROES_T1 | Pen-Y-Groes T1 | PEN-Y-GROES T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 5.2 | 2.95 | 2.25 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 3.4366 | 1.8 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.2 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 5.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0569 | -4.3015 | 1 | 109696 | 15686
SPM-PREES_T1 | Prees T1 | PREES T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 7.5 | 5.171 | 2.216 | Green | thermal | 0.1 | 2 | 1 | 3 | 0 | 0 | 0.3 | 0.2 | 0 | 5.171 | 5.9987 | 1.5 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.2 | primary | 1.1 | Frodsham | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8975 | -2.6739 | 13 | 662923 | 15686
SPM-FISONS_T1 | Fisons T1 | FISONS T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 2.64 | 2.181 | Green | thermal | 2.7 | 3 | 0.3 | 2 | 0 | 0 | 1.2 | 0.3 | 0.1 | 2.64 | 2.977 | 4.5 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.2 | primary | 3 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1973 | -2.3499 | 3 | 39129 | 15686
SPM-BOW_ST_T1 | Bow St T1 | BOW ST T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 7.5 | 5.4 | 2.1 | Green | thermal | 0 | 0 | 0 | 1 | 0 | 0 | 0.1 | 0.1 | 0 | 5.4 | 6.2982 | 1.2 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.1 | primary | 0 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.4524 | -4.0162 | 2 | 60430 | 14973
SPM-TRYWERYN_T1 | Tryweryn T1 | TRYWERYN T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 1.862 | 2.138 | Green | thermal | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1.862 | 2.0371 | 2 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.1 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9492 | -3.6665 | 0 | 0 | 14973
SPM-KNUTSFORD_T2 | Knutsford T2 | KNUTSFORD T2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 5.424 | 2.076 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.424 | 6.1014 | 1.4 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.1 | primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1947 | -2.917 | 6 | 182480 | 14973
SPM-LLANDRINIO_T1 | Llandrinio T1 | LLANDRINIO T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 5.3 | 3.217 | 2.06 | Green | thermal | 0 | 1 | 0.4 | 4 | 0.1 | 1 | 0.5 | 0.5 | 0.1 | 3.217 | 3.8474 | 1.4 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.1 | primary | 0.4 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 5.3 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7497 | -3.063 | 8 | 141357 | 14973
SPM-LLANFYLLIN_T1_LLANFYLLIN_T2 | Llanfyllin T1 / Llanfyllin T2 | LLANFYLLIN T1 / LLANFYLLIN T2 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.8 | 5.693 | 2.089 | Green | thermal | 0 | 2 | 0 | 2 | 0 | 0 | 0.4 | 0.4 | 0 | 5.693 | 6.952 | 0.8 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2.1 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.8 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7574 | -3.2423 | 3 | 129043 | 14973
SPM-RUABON_T1 | Ruabon T1 | RUABON T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 10 | 8.004 | 1.996 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.004 | 9.4666 | 0.5 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9867 | -3.0574 | 6 | 219287 | 14260
SPM-LLANFAIR_CAEREINION_T1 | Llanfair Caereinion T1 | LLANFAIR CAEREINION T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 5.329 | 2.033 | Green | thermal | 0.1 | 1 | 0.1 | 4 | 0.7 | 2 | 0.8 | 0.5 | 0.2 | 5.329 | 5.9879 | 1.5 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2 | primary | 0.2 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.6454 | -3.3145 | 5 | 97780 | 14260
SPM-BLAENAU_FFESTINIOG_T1 | Blaenau Ffestiniog T1 | BLAENAU FFESTINIOG T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 2.015 | 1.985 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.4 | 0 | 2.015 | 2.6043 | 1.4 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 2 | primary | 0 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9937 | -3.9445 | 4 | 288066 | 14260
SPM-CAERGWRLE_T1 | Caergwrle T1 | CAERGWRLE T1 | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CASTLE CEMENT GT1 / HAWARDEN GT1 / SALTNEY GT1 / SALTNEY G2B | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 5.6 | 1.9 | Green | thermal | 0 | 0 | 0 | 0 | 0.3 | 2 | 2.5 | 2.3 | 0 | 5.6 | 6.7699 | 0.7 | 119.8 | 87.04 | 32.76 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.9 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1205 | -3.053 | 2 | 38185 | 13547
SPM-HARRINGTON_ST_T2_HIGHFIELD_ST_T1 | Harrington St T2 / Highfield St T1 | HARRINGTON ST T2 / HIGHFIELD ST T1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM |  | 8.7 | 6.829 | 1.871 | Green | thermal | 0 | 0 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 6.829 | 7.9549 | 0.7 | 139 | 79.4 | 59.6 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.9 | primary | 3 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | 8.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4059 | -2.9872 | 13 | 309066 | 13547
SPM-FRODSHAM_LOCAL_T1 | Frodsham Local T1 | FRODSHAM LOCAL T1 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | INCE LOCAL GT1 / INCE LOCAL GT2 | FRODSHAM - INCE | SPM |  | 8.2 | 6.257 | 1.943 | Green | thermal | 0 | 0 | 0.1 | 3 | 0 | 0 | 0.2 | 0.2 | 0 | 6.257 | 7.7695 | 0.4 | 45 | 18.8567 | 26.1433 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.9 | primary | 0.1 | Frodsham | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | 8.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2972 | -2.7269 | 6 | 101825 | 13547
SPM-RIVALS_T1 | Rivals T1 | RIVALS T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 1.736 | 1.79 | Green | thermal | 0.5 | 2 | 0 | 2 | 0 | 1 | 0.5 | 0.3 | 0 | 1.736 | 1.8331 | 2.2 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.8 | primary | 0.5 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9838 | -4.4089 | 2 | 55441 | 12834
SPM-RAVEN_SQUARE_T1 | Raven Square T1 | RAVEN SQUARE T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 5.74 | 1.76 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.74 | 7.2812 | 0.2 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.8 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.6587 | -3.1624 | 22 | 1075605 | 12834
SPM-MERE_T1 | Mere T1 | MERE T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 4.433 | 1.829 | Green | thermal | 1.2 | 3 | 2.1 | 11 | 1.8 | 2 | 2.4 | 2.1 | 0.4 | 4.433 | 6.3181 | 1.2 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.8 | primary | 3.3 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3293 | -2.4089 | 12 | 571307 | 12834
SPM-BUTTINGTON_CROSS_T1 | Buttington Cross T1 | BUTTINGTON CROSS T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 5.19 | 1.8441 | Green | thermal | 0.5 | 5 | 2.1 | 6 | 0 | 0 | 1.7 | 1.6 | 1.2 | 5.19 | 5.7114 | 1.8 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.8 | primary | 2.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.6687 | -3.1261 | 5 | 471752 | 12834
SPM-TARPORLEY_T1 | Tarporley T1 | TARPORLEY T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | LEGACY | SPM |  | 7.5 | 5.484 | 1.783 | Green | thermal | 0.2 | 3 | 0.4 | 4 | 0 | 0 | 1.2 | 0.8 | 0.4 | 5.484 | 6.7461 | 0.8 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 1.8 | primary | 0.6 | Frodsham | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.153 | -2.6705 | 3 | 73803 | 12834
SPM-BRD_T1 | Brd T1 | BRD T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 7.5 | 5.444 | 1.718 | Green | thermal | 0.3 | 3 | 0.1 | 3 | 0 | 0 | 0.3 | 0.2 | 0 | 5.444 | 7.022 | 0.5 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.7 | primary | 0.4 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.4998 | -3.27 | 21 | 1058282 | 12121
SPM-SHAWBURY_T1 | Shawbury T1 | SHAWBURY T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 6.8 | 5.042 | 1.668 | Green | thermal | 0.1 | 1 | 1.9 | 4 | 0 | 0 | 1.1 | 0.9 | 0 | 5.042 | 6.0079 | 0.8 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.7 | primary | 2 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 6.8 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7996 | -2.679 | 15 | 841447 | 12121
SPM-CAERNARFON_T1 | Caernarfon T1 | CAERNARFON T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 5.797 | 1.703 | Green | thermal | 0 | 0 | 0.3 | 2 | 0 | 0 | 0.2 | 0.2 | 0 | 5.797 | 7.203 | 0.3 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.7 | primary | 0.3 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1476 | -4.2569 | 12 | 379549 | 12121
SPM-PANDY_T1_PANDY_T2 | Pandy T1 / Pandy T2 | PANDY T1 / PANDY T2 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 10 | 8.403 | 1.597 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.403 | 10.1845 | -0.2 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 1.6 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0737 | -2.991 | 9 | 198752 | 11408
SPM-LLANBEDROG_T1 | Llanbedrog T1 | LLANBEDROG T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 2.428 | 1.572 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.428 | 3.0476 | 1 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.6 | primary | 0 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8688 | -4.4986 | 1 | 12847 | 11408
SPM-FOUR_CROSSES_T1 | Four Crosses T1 | FOUR CROSSES T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 2.5 | 1.5 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.8478 | 1.2 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.5 | primary | 0 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9315 | -4.384 | 4 | 207623 | 10695
SPM-CEMMAES_RD_T1 | Cemmaes Rd T1 | CEMMAES RD T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 2.45 | 1.532 | Green | thermal | 0 | 1 | 0.5 | 4 | 0 | 1 | 0 | 0 | 0 | 2.45 | 3.2114 | 0.8 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.5 | primary | 0.5 | Trawsfynydd | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.6262 | -3.7474 | 1 | 34863 | 10695
SPM-CRIGGION_RADIO_STATION_T1 | Criggion Radio Station T1 | CRIGGION RADIO STATION T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 4 | 1.781 | 1.519 | Green | thermal | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.781 | 1.8663 | 2.1 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.5 | primary | 0.7 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.7246 | -3.0679 | 1 | 21778 | 10695
SPM-GWERSYLLT_T1 | Gwersyllt T1 | GWERSYLLT T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 7.5 | 6.038 | 1.462 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.038 | 7.7097 | -0.2 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 1.5 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0709 | -3.0158 | 2 | 48600 | 10695
SPM-LLANIDLOES_T1_LLANIDLOES_T2 | Llanidloes T1 / Llanidloes T2 | LLANIDLOES T1 / LLANIDLOES T2 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 5.7 | 4.144 | 1.52 | Green | thermal | 0.1 | 2 | 0.3 | 8 | 0 | 0 | 0.5 | 0.5 | 0 | 4.144 | 5.573 | 0.2 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.5 | primary | 0.4 | Trawsfynydd | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 5.7 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.4555 | -3.5356 | 5 | 162687 | 10695
SPM-CHALON_WAY_T1_TECHNOLOGY_CAMPUS_T1_WOODVILLE_ST_T1 | Chalon Way T1 / Technology Campus T1 / Woodville St T1 | CHALON WAY T1 / TECHNOLOGY CAMPUS T1 / WOODVILLE ST T1 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAVENHEAD G1A1 / ST HELENS GT2B / WINDLE GT1 | RAINHILL | SPM |  | 9.1 | 7.67 | 1.43 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.67 | 9.5073 | -0.4 | 69.1 | 42.44 | 26.66 | GREEN | 17.1 |  |  |  |  | 0 | 0 | 0 | 0 | 1.4 | primary | 0 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 9.1 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4509 | -2.733 | 18 | 680294 | 9982
SPM-HOLMES_CHAPEL_T1 | Holmes Chapel T1 | HOLMES CHAPEL T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 6.08 | 1.42 | Green | thermal | 0 | 0 | 1 | 3 | 0 | 0 | 0.1 | 0.1 | 0 | 6.08 | 7.4972 | 0 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.4 | primary | 1 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2061 | -2.3526 | 4 | 118754 | 9982
SPM-LEA_GREEN_T1_PILKINGTONS_HO_T1_RAVENHEAD_RETAIL_PK_T1_SOMERF | Lea Green T1 / Pilkingtons Ho T1 / Ravenhead Retail Pk T1 / Somerfield Distribution T1 | LEA GREEN T1 / PILKINGTONS HO T1 / RAVENHEAD RETAIL PK T1 / SOMERFIELD DISTRIBUTION T1 | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | BOLD G4B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM |  | 20 | 18.6264 | 1.3736 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6264 | 22.6063 | -2.6 | 64.6 | 43.2692 | 20.6708 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.4 | primary | 0 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4234 | -2.7387 | 12 | 2823682 | 9982
SPM-BERSHAM_COLLIERY_T1 | Bersham Colliery T1 | BERSHAM COLLIERY T1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 4 | 2.8015 | 1.1985 | Green | thermal | 0 | 0 | 0 | 0 | 0.3 | 1 | 0.9 | 0.9 | 0 | 2.8015 | 3.3268 | 0.7 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | 1.2 | primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0252 | -3.0248 | 6 | 220710 | 8556
SPM-ABERSOCH_T1 | Abersoch T1 | ABERSOCH T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 2.597 | 1.207 | Green | thermal | 0.2 | 1 | 0.3 | 4 | 0.4 | 1 | 0.5 | 0.4 | 1.7 | 2.597 | 3.0863 | 0.9 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.2 | primary | 0.5 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8218 | -4.5243 | 0 | 0 | 8556
SPM-MACHYNLLETH_T1 | Machynlleth T1 | MACHYNLLETH T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 4 | 2.909 | 1.091 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.909 | 4.2199 | -0.2 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.1 | primary | 0 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5908 | -3.8324 | 2 | 31725 | 7843
SPM-WIMPEYS_PANT_QUARRY_T1_WIMPEYS_PANT_QUARRY_T2 | Wimpeys Pant Quarry T1 / Wimpeys Pant Quarry T2 | WIMPEYS PANT QUARRY T1 / WIMPEYS PANT QUARRY T2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | BRYMBO GT2 / HAWARDEN GT2 / HOLYWELL GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 5.2 | 4.137 | 1.062 | Green | thermal | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.137 | 4.4236 | 0.8 | 82 | 60.5487 | 19.9178 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.1 | primary | 0 | Connahs Quay / SASA | [7 empty] | 5.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2253 | -3.2022 | 2 | 32783 | 7843
SPM-ELLESMERE_T1_MMB_ELLESMERE_T1 | Ellesmere T1 / Mmb Ellesmere T1 | ELLESMERE T1 / MMB ELLESMERE T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 9 | 7.802 | 1.144 | Green | thermal | 0.1 | 4 | 0.7 | 18 | 0 | 0 | 13.2 | 13.1 | 0.5 | 7.802 | 8.9868 | 0 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1.1 | primary | 0.8 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 9 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9045 | -2.8947 | 11 | 400780 | 7843
SPM-HARTFORD_T1 | Hartford T1 | HARTFORD T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 6.534 | 0.966 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.534 | 8.139 | -0.6 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1 | primary | 0 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2381 | -2.5504 | 1 | 70941 | 7130
SPM-CARMEL_T1 | Carmel T1 | CARMEL T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 2.959 | 0.981 | Green | thermal | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.959 | 3.2496 | 0.8 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1 | primary | 0.1 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0757 | -4.2495 | 0 | 0 | 7130
SPM-BASCHURCH_T1 | Baschurch T1 | BASCHURCH T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 7.5 | 6.232 | 0.998 | Green | thermal | 0.3 | 1 | 0.5 | 1 | 0.5 | 1 | 0.1 | 0.1 | 0.1 | 6.232 | 7.382 | 0.1 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1 | primary | 0.8 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8054 | -2.858 | 65 | 2052209 | 7130
SPM-LLANBERIS_T1 | Llanberis T1 | LLANBERIS T1 | BANGOR GT2 / CAERNARFON GT2 | BANGOR GT2 / CAERNARFON GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 5 | 4.007 | 0.993 | Green | thermal | 0 | 0 | 0 | 1 | 0 | 0 | 1.6 | 0.2 | 0 | 4.007 | 4.4886 | 0.5 | 82.1 | 50.414 | 31.686 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 1 | primary | 0 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.115 | -4.1137 | 0 | 0 | 7130
SPM-REFORM_ST_T1 | Reform St T1 | REFORM ST T1 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | COLWYN BAY GT1 / COLWYN BAY GT2 / DOLGARROG GT2 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 7.5 | 5.592 | 0.8532 | Green | thermal | 1.1 | 3 | 2.7 | 3 | 0 | 0 | 0 | 0 | 0 | 5.592 | 6.4931 | 1 | 92.5 | 75.858 | 16.642 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.9 | primary | 3.8 | Pentir | PENTIR | 2 | 1082 | 1082 | 57 | 39 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3234 | -3.8302 | 0 | 0 | 6417
SPM-TARVIN_T1 | Tarvin T1 | TARVIN T1 | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM |  | 7.5 | 6.622 | 0.822 | Green | thermal | 0.1 | 1 | 0.2 | 1 | 0 | 0 | 0.1 | 0.1 | 0 | 6.622 | 8.2381 | -0.7 | 128.6 | 92.299 | 31.649 | GREEN | 39.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0.8 | primary | 0.3 | Frodsham | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1999 | -2.7618 | 6 | 132647 | 5704
SPM-EDERN_T1 | Edern T1 | EDERN T1 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | FOUR CROSSES GT2 / MAENTWROG GT1 / MAENTWROG GT2 | TRAWSFYNYDD | SPM |  | 4 | 3.385 | 0.615 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 3.385 | 4.1314 | -0.1 | 69.6 | 65.294 | 4.306 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.6 | primary | 0 | Pentir | TRAWSFYNYDD | 1 | 940 | 0 | 0 | 10 | 2037-11 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9207 | -4.5602 | 0 | 0 | 4278
SPM-LLANDDU_QUARRY_T1 | Llanddu Quarry T1 | LLANDDU QUARRY T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 4 | 3.423 | 0.577 | Green | thermal | 0 | 0 | 0.6 | 2 | 0.5 | 1 | 0.3 | 0.2 | 0.1 | 3.423 | 4.0319 | 0 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.6 | primary | 0.6 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.799 | -3.1056 | 0 | 0 | 4278
SPM-ABERGELE_T1_PENSARN_T1 | Abergele T1 / Pensarn T1 | ABERGELE T1 / PENSARN T1 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM |  | 10 | 9.153 | 0.647 | Green | thermal | 0.4 | 2 | 9.7 | 16 | 1.9 | 2 | 1 | 0.6 | 0 | 9.153 | 11.5886 | -1.6 | 112.9 | 87.5677 | 22.4768 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.6 | primary | 10.1 | Connahs Quay / SASA | [7 empty] | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2754 | -3.561 | 11 | 238680 | 4278
SPM-LLANILAR_T1 | Llanilar T1 | LLANILAR T1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | ABERYSTWYTH GT2 / RHYDLYDAN GT1 | SWANSEA NORTH | SPM |  | 3.2 | 2.682 | 0.498 | Green | thermal | 0 | 1 | 0 | 1 | 0 | 0 | 0.2 | 0.2 | 0 | 2.682 | 2.9883 | 0.2 | 45.4 | 37.321 | 8.079 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.5 | primary | 0 | Trawsfynydd | SWANSEA NORTH | 10 | 2020.9 | 2020.9 | 0 | 61 | 2024-08 | 3.2 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.3613 | -4.0467 | 0 | 0 | 3565
SPM-CLEDFORD_T1 | Cledford T1 | CLEDFORD T1 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 5.15 | 0.414 | Green | thermal | 1.9 | 2 | 2.2 | 3 | 0 | 0 | 3.3 | 0 | 0.2 | 5.15 | 6.0307 | 1.5 | 85.4 | 52.367 | 26.603 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.4 | primary | 4.1 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1765 | -2.4375 | 5 | 82417 | 2852
SPM-EDEN_VALE_T1 | Eden Vale T1 | EDEN VALE T1 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | HARTFORD GT1 / LOSTOCK GT2 / WINSFORD GT1 / WINSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM |  | 7.5 | 4.2461 | 0.29228 | Amber | thermal | 3 | 7 | 0.6 | 4 | 0.2 | 1 | 2.9 | 2.5 | 0 | 4.2461 | 5.0659 | 2.4 | 113 | 77.12 | 35.88 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.3 | primary | 3.6 | Frodsham | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.247 | -2.5981 | 2 | 79323 | 2139
SPM-FORDEN_T1 | Forden T1 | FORDEN T1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM |  | 4 | 3.799 | 0.201 | Green | thermal | 0 | 0 | 0.1 | 1 | 0 | 0 | 0.2 | 0 | 0 | 3.799 | 4.2514 | -0.3 | 168.4 | 105.6806 | 60.6676 | GREEN | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0.2 | primary | 0.1 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.5891 | -3.1462 | 3 | 54058 | 1426
SPM-WEST_FELTON_T1 | West Felton T1 | WEST FELTON T1 | OSWESTRY GT5 / WHITCHURCH GT1 | OSWESTRY GT5 / WHITCHURCH GT1 / WEM GT1 | LEGACY | SPM |  | 4 | 3.471 | -0.247 | Red | thermal | 0.8 | 1 | 0.1 | 2 | 0.2 | 2 | 2.7 | 1.1 | 0 | 3.471 | 3.8889 | 0.1 | 68.9 | 64.0286 | 3.1024 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -0.2 | primary | 0.9 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.8306 | -2.9742 | 3 | 85504 | 0
SPM-COEDPOETH_T1_COEDPOETH_T2 | Coedpoeth T1 / Coedpoeth T2 | COEDPOETH T1 / COEDPOETH T2 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | BRYMBO GT1 / LEGACY LOCAL GT1 / MARCHWIEL GT1 / MARCHWIEL GT2 / WREXHAM GT1 | LEGACY | SPM |  | 10 | 5.998 | -0.3902 | Red | thermal | 8.8 | 12 | 10.6 | 20 | 0.1 | 2 | 5.7 | 4.2 | 0.1 | 5.998 | 7.4739 | 2.5 | 154.7 | 107.901 | 41.8508 | GREEN | 1.6 |  |  |  |  | 0 | 0 | 0 | 0 | -0.4 | primary | 19.4 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0562 | -3.062 | 2 | 111433 | 0
SPM-ORFORD_T1_PADGATE_T1 | Orford T1 / Padgate T1 | ORFORD T1 / PADGATE T1 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 10 | 8.815 | 1.185 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 8.815 | 11.7687 | -1.8 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4112 | -2.5733 | 58 | 2861387 | 0
SPM-BOULEVARD_T1_CHAPELFORD_T1_HAWLEYS_LA_T1_WESTBROOK_T1_WINWIC | Boulevard T1 / Chapelford T1 / Hawleys La T1 / Westbrook T1 / Winwick Quay T1 | BOULEVARD T1 / CHAPELFORD T1 / HAWLEYS LA T1 / WESTBROOK T1 / WINWICK QUAY T1 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 37.5 | 21.052 | 16.448 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.052 | 25.0188 | 12.5 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4181 | -2.599 | 54 | 4379029 | 0
SPM-BARBAULD_ST_T1_HORROCKS_LA_T1_WARRINGTON_CENTRAL_T1 | Barbauld St T1 / Horrocks La T1 / Warrington Central T1 | BARBAULD ST T1 / HORROCKS LA T1 / WARRINGTON CENTRAL T1 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 20 | 8.037 | 10.664 | Green | thermal | 3.9 | 6 | 0.4 | 3 | 0 | 0 | 0.9 | 0.3 | 0 | 8.037 | 9.0191 | 11 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 4.3 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3893 | -2.5915 | 8 | 250104 | 0
SPM-BATTERSBY_LA_T1_RYLANDS_ELDON_ST_T2 | Battersby La T1 / Rylands Eldon St T2 | BATTERSBY LA T1 / RYLANDS ELDON ST T2 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 9.1 | 0.96 | 8.14 | Green | thermal | 0 | 0 | 0.4 | 2 | 0 | 0 | 0.4 | 0.4 | 0 | 0.96 | 1.1429 | 8 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 0.4 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 9.1 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.396 | -2.5846 | 0 | 0 | 0
SPM-BEWSEY_T1_OWEN_ST_T1_RODNEY_ST_T1_RYLANDS_ELDON_ST_T1 | Bewsey T1 / Owen St T1 / Rodney St T1 / Rylands Eldon St T1 | BEWSEY T1 / OWEN ST T1 / RODNEY ST T1 / RYLANDS ELDON ST T1 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 30 | 17.123 | 11.377 | Green | thermal | 6 | 12 | 12.4 | 20 | 3 | 4 | 6.2 | 3 | 0 | 17.123 | 21.2605 | 8.7 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 18.4 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3969 | -2.6136 | 40 | 2623415 | 0
SPM-KINGSLAND_33_T1_SAFEWAY_T1_WOOLSTON_T1_WOOLSTON_T2 | Kingsland 33 T1 / Safeway T1 / Woolston T1 / Woolston T2 | KINGSLAND 33 T1 / SAFEWAY T1 / WOOLSTON T1 / WOOLSTON T2 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 30 | 17.217 | 11.614 | Green | thermal | 4.7 | 12 | 4 | 12 | 0 | 0 | 2.5 | 1.5 | 0.8 | 17.217 | 20.7728 | 9.2 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 8.7 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 30 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4018 | -2.5217 | 77 | 5208739 | 0
SPM-NORTH_WEST_WATER_CAMPUS_T1_NORTH_WEST_WATER_CAMPUS_T2_OMEGA_ | North West Water Campus T1 / North West Water Campus T2 / Omega T1 / Omega T2 / Orion Boulevard T1 | NORTH WEST WATER CAMPUS T1 / NORTH WEST WATER CAMPUS T2 / OMEGA T1 / OMEGA T2 / ORION BOULEVARD T1 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 40 | 14.989 | 25.011 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.989 | 16.5109 | 23.5 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 40 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4088 | -2.645 | 12 | 5132060 | 0
SPM-GREAT_SANKEY_T1_PENKETH_T1_WIDNES_RD_T1 | Great Sankey T1 / Penketh T1 / Widnes Rd T1 | GREAT SANKEY T1 / PENKETH T1 / WIDNES RD T1 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | DALLAM GT1 / SANKEY BRIDGES GT1 / WARRINGTON GT3 | CARRINGTON - FIDDLERS FERRY | SPM |  | 20 | 11 | 4.75 | Green | thermal | 12.8 | 6 | 35.1 | 30 | 0 | 0 | 22.7 | 21 | 0 | 11 | 13.9364 | 6.1 | 103 | 95.754 | -0.972 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1 | bsp | 47.9 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 20 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3856 | -2.6331 | 8 | 600473 | 0
SPM-HOLYHEAD_T1 | Holyhead T1 | HOLYHEAD T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 2.554 | 4.946 | Green | thermal | 0 | 0 | 0 | 0 | 0.3 | 1 | 0 | 0 | 0 | 2.554 | 3.0488 | 4.5 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3041 | -4.6275 | 4 | 121278 | 0
SPM-LLANDEGFAN_T1 | Llandegfan T1 | LLANDEGFAN T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 2.35 | 4.965 | Green | thermal | 0.2 | 1 | 1 | 3 | 0 | 0 | 0.5 | 0.5 | 0 | 2.35 | 2.7748 | 4.7 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 1.2 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2422 | -4.1572 | 3 | 106203 | 0
SPM-BEAUMARIS_T1_BEAUMARIS_T2 | Beaumaris T1 / Beaumaris T2 | BEAUMARIS T1 / BEAUMARIS T2 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.8 | 3.237 | 4.563 | Green | thermal | 0 | 0 | 0.1 | 2 | 0.1 | 4 | 0 | 0 | 0 | 3.237 | 3.7658 | 4 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0.1 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.8 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2778 | -4.123 | 0 | 0 | 0
SPM-AMLWCH_T1_AMLWCH_T2 | Amlwch T1 / Amlwch T2 | AMLWCH T1 / AMLWCH T2 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 10 | 4.162 | 4.82 | Green | thermal | 2 | 6 | 4.6 | 12 | 0.1 | 2 | 0 | 0 | 0 | 4.162 | 5.1212 | 4.9 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 6.6 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4109 | -4.3377 | 4 | 55119 | 0
SPM-PARC_CYBI_T1_PARC_CYBI_T2 | Parc Cybi T1 / Parc Cybi T2 | PARC CYBI T1 / PARC CYBI T2 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 10 | 3.482 | 6.518 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.482 | 4.4253 | 5.6 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2957 | -4.6179 | 8 | 291537 | 0
SPM-LLANDYFRYDOG_T1 | Llandyfrydog T1 | LLANDYFRYDOG T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 2.982 | 4.518 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.4 | 0 | 2.982 | 3.22 | 4.3 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3679 | -4.3101 | 0 | 0 | 0
SPM-LLANGAFFO_T1 | Llangaffo T1 | LLANGAFFO T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 3.72 | 3.78 | Green | thermal | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.72 | 3.9386 | 3.6 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1874 | -4.3287 | 0 | 0 | 0
SPM-PENTRAETH_T1 | Pentraeth T1 | PENTRAETH T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 5.331 | 2.169 | Green | thermal | 0 | 0 | 0.1 | 1 | 0.2 | 1 | 0 | 0 | 0 | 5.331 | 5.9334 | 1.6 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0.1 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2825 | -4.2365 | 0 | 0 | 0
SPM-LLANGEFNI_T1 | Llangefni T1 | LLANGEFNI T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 3.96 | 3.54 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 2.2 | 0.1 | 3.96 | 4.5369 | 3 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2543 | -4.3091 | 13 | 462382 | 0
SPM-ALPOCO_T1 | Alpoco T1 | ALPOCO T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 2.46 | 4.813 | Green | thermal | 0.2 | 2 | 0.6 | 3 | 0 | 0 | 1.2 | 0.9 | 0.3 | 2.46 | 2.7693 | 4.7 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0.8 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2941 | -4.5962 | 1 | 38601 | 0
SPM-MONA_T1 | Mona T1 | MONA T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 2.26 | 5.24 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | 2.7331 | 4.8 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.251 | -4.3719 | 3 | 62107 | 0
SPM-LLANDDEUSANT_T1 | Llanddeusant T1 | LLANDDEUSANT T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 3.9039 | 3.5271 | Green | thermal | 0.1 | 1 | 0.1 | 1 | 0.1 | 1 | 0.1 | 0.1 | 0 | 3.9039 | 4.0648 | 3.4 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0.2 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3279 | -4.47 | 0 | 0 | 0
SPM-GAERWEN_VIEW_T1 | Gaerwen View T1 | GAERWEN VIEW T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 1.939 | 5.561 | Green | thermal | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 1.939 | 2.4059 | 5.1 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0.1 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2166 | -4.285 | 13 | 306555 | 0
SPM-LLANFAELOG_T1 | Llanfaelog T1 | LLANFAELOG T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 4 | 2.88 | 1.12 | Green | thermal | 0 | 0 | 0 | 0 | 0.1 | 1 | 0 | 0 | 0 | 2.88 | 3.0682 | 0.9 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2292 | -4.4824 | 0 | 0 | 0
SPM-LLANFAIR_PG_T1 | Llanfair Pg T1 | LLANFAIR PG T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 4.423 | 3.008 | Green | thermal | 0.1 | 1 | 0.8 | 4 | 0 | 0 | 0.5 | 0.5 | 0.5 | 4.423 | 5.4041 | 2.1 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0.9 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.229 | -4.197 | 2 | 50014 | 0
SPM-LLAINGOCH_T1 | Llaingoch T1 | LLAINGOCH T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 3.258 | 4.242 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.258 | 3.806 | 3.7 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3098 | -4.6506 | 1 | 46079 | 0
SPM-CEMAES_BAY_T1 | Cemaes Bay T1 | CEMAES BAY T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 4 | 1.997 | 2.003 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.997 | 2.3437 | 1.7 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4066 | -4.4538 | 0 | 0 | 0
SPM-LLANGEFNI_IND_EST_T1_LLANGEFNI_IND_EST_T2 | Llangefni Ind Est T1 / Llangefni Ind Est T2 | LLANGEFNI IND EST T1 / LLANGEFNI IND EST T2 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 10 | 3.87 | 5.792 | Green | thermal | 0.7 | 4 | 0.6 | 8 | 1.7 | 2 | 0 | 0 | 0 | 3.87 | 4.0777 | 5.9 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 1.3 | Pentir | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2481 | -4.3057 | 2 | 102021 | 0
SPM-CAERGEILIOG_T1 | Caergeiliog T1 | CAERGEILIOG T1 | AMLWCH GT1 / CAERGEILIOG GT1 | AMLWCH GT1 / CAERGEILIOG GT1 / CAERGEILIOG GT2 | WYLFA | SPM |  | 7.5 | 4.81 | 2.649 | Green | thermal | 0 | 1 | 0 | 1 | 0 | 0 | 0.1 | 0 | 0 | 4.81 | 5.9473 | 1.6 | 72.5 | 52.462 | -1.909 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -1.9 | bsp | 0 | Wylfa | WYLFA | 2 | 420 | 420 | 0 | 0 | 2028-10 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2741 | -4.5438 | 0 | 0 | 0
SPM-WHEELOCK_T1 | Wheelock T1 | WHEELOCK T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.924 | 1.576 | Green | thermal | 0 | 0 | 1.1 | 2 | 0 | 0 | 0.1 | 0.1 | 0 | 5.924 | 7.3979 | 0.1 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 1.1 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1337 | -2.368 | 6 | 172840 | 0
SPM-WISTASTON_HALL_T1 | Wistaston Hall T1 | WISTASTON HALL T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 4.459 | 3.041 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 4.459 | 5.4467 | 2.1 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0842 | -2.4715 | 1 | 11884 | 0
SPM-TWYFORDS_T1 | Twyfords T1 | TWYFORDS T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 3.02 | 3.08 | Green | thermal | 1.4 | 1 | 0 | 0 | 0 | 0 | 2.5 | 1.6 | 0 | 3.02 | 3.4854 | 4 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 1.4 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0946 | -2.2854 | 7 | 600582 | 0
SPM-DUCKINGTON_T1_DUCKINGTON_T2 | Duckington T1 / Duckington T2 | DUCKINGTON T1 / DUCKINGTON T2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 9.8 | 3.972 | 5.787 | Green | thermal | 0.1 | 2 | 0.9 | 6 | 0.2 | 6 | 1.7 | 1.2 | 0 | 3.972 | 4.7584 | 5 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 1 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 9.8 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0609 | -2.7536 | 2 | 52236 | 0
SPM-CHESHIRE_GREEN_T1_NWF_T1 | Cheshire Green T1 / Nwf T1 | CHESHIRE GREEN T1 / NWF T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 10 | 5.491 | 4.509 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.491 | 5.9312 | 4.1 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1132 | -2.5973 | 8 | 1438563 | 0
SPM-SNOWHILL_T1 | Snowhill T1 | SNOWHILL T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.293 | 2.207 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.293 | 6.1652 | 1.3 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0683 | -2.5236 | 2 | 74121 | 0
SPM-ROLLS_ROYCE_T1_ROLLS_ROYCE_T2_ROLLS_ROYCE_T3 | Rolls Royce T1 / Rolls Royce T2 / Rolls Royce T3 | ROLLS ROYCE T1 / ROLLS ROYCE T2 / ROLLS ROYCE T3 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 15 | 11.7572 | 3.2428 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7572 | 13.2732 | 1.7 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 15 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1057 | -2.4695 | 5 | 2763527 | 0
SPM-SANDBACH_T1 | Sandbach T1 | SANDBACH T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 7.586 | -0.086 | Red | thermal | 0 | 0 | 1.6 | 2 | 0 | 0 | 0 | 0 | 0 | 7.586 | 8.9786 | -1.5 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 1.6 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1543 | -2.3671 | 6 | 500368 | 0
SPM-ACER_AVE_T1 | Acer Ave T1 | ACER AVE T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 7.3485 | 0.050687 | Red | thermal | 0.1 | 1 | 0.6 | 2 | 0 | 0 | 0 | 0 | 0 | 7.3485 | 9.1846 | -1.7 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0.7 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1106 | -2.4338 | 2 | 28913 | 0
SPM-FODENS_T1 | Fodens T1 | FODENS T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 4.855 | 2.645 | Green | thermal | 0 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 4.855 | 5.8778 | 1.6 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0.7 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1454 | -2.3913 | 15 | 489286 | 0
SPM-AUDLEM_T1 | Audlem T1 | AUDLEM T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 3.56 | 3.84 | Green | thermal | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.56 | 3.9322 | 3.6 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0.1 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.9959 | -2.4889 | 2 | 573050 | 0
SPM-NEWHALL_T1_NEWHALL_T2 | Newhall T1 / Newhall T2 | NEWHALL T1 / NEWHALL T2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 10 | 4.928 | 4.934 | Green | thermal | 0.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.928 | 5.1669 | 4.8 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0.3 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0003 | -2.5899 | 2 | 104889 | 0
SPM-BR_STATION_T1_DUCHY_RD_T1_ELECTRA_WAY_T1_MIDLAND_ROLLMAKERS_ | Br Station T1 / Duchy Rd T1 / Electra Way T1 / Midland Rollmakers T1A / North Western Mills T1 | BR STATION T1 / DUCHY RD T1 / ELECTRA WAY T1 / MIDLAND ROLLMAKERS T1A / NORTH WESTERN MILLS T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 37.5 | 25.235 | 12.265 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 25.235 | 28.066 | 9.4 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 37.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.084 | -2.4287 | 83 | 6140217 | 0
SPM-NANTWICH_T1 | Nantwich T1 | NANTWICH T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.485 | 1.103 | Green | thermal | 0.9 | 3 | 0.8 | 1 | 0 | 0 | 1 | 0.9 | 0 | 5.485 | 6.2729 | 1.2 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 1.7 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0675 | -2.5128 | 6 | 324292 | 0
SPM-CHURCH_LAWTON_T1 | Church Lawton T1 | CHURCH LAWTON T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 3.73 | 3.77 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.73 | 4.7233 | 2.8 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0977 | -2.2747 | 9 | 648396 | 0
SPM-RADWAY_GREEN_T1 | Radway Green T1 | RADWAY GREEN T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.839 | -2.348 | Red | thermal | 4 | 2 | 2.2 | 4 | 0.1 | 1 | 0.5 | 0.5 | 0.1 | 5.839 | 7.3421 | 0.2 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 6.2 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0841 | -2.3365 | 8 | 809697 | 0
SPM-HATHERTON_T1 | Hatherton T1 | HATHERTON T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 4 | 2.235 | 1.468 | Green | thermal | 0.3 | 4 | 0.6 | 1 | 0.1 | 2 | 0.5 | 0.5 | 0.1 | 2.235 | 2.2995 | 1.7 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0.9 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0218 | -2.4781 | 2 | 48184 | 0
SPM-SMALLWOOD_T1 | Smallwood T1 | SMALLWOOD T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.43 | 1.982 | Green | thermal | 0.1 | 1 | 0.1 | 2 | 0.2 | 2 | 0.1 | 0.1 | 0 | 5.43 | 6.0727 | 1.4 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0.2 | Fiddlers Ferry | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1444 | -2.2727 | 62 | 2172976 | 0
SPM-STAPELEY_T1 | Stapeley T1 | STAPELEY T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.199 | 2.301 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.199 | 6.1584 | 1.3 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0566 | -2.4859 | 3 | 44268 | 0
SPM-WESTON_T1 | Weston T1 | WESTON T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 10 | 7.343 | 2.657 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.343 | 9.0703 | 0.9 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0732 | -2.3962 | 9 | 600815 | 0
SPM-WRENBURY_FRITH_T1 | Wrenbury Frith T1 | WRENBURY FRITH T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 4 | 2.6914 | 1.3086 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6914 | 3.0984 | 0.9 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 4 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0332 | -2.6356 | 2 | 29302 | 0
SPM-ACTON_T1 | Acton T1 | ACTON T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 4.667 | 2.399 | Green | thermal | 0.4 | 2 | 1 | 7 | 0 | 0 | 0.2 | 0.1 | 0 | 4.667 | 5.2528 | 2.2 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 1.4 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0769 | -2.5525 | 12 | 728130 | 0
SPM-CREWE_T1 | Crewe T1 | CREWE T1 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM |  | 7.5 | 5.043 | 2.457 | Green | thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.043 | 5.8378 | 1.7 | 197.4 | 164.4225 | -3.1663 | RED | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.2 | bsp | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | 7.5 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1034 | -2.4848 | 10 | 406798 | 0
SPM-LYMM_T1_WHITELEGGS_LA_T1 | Lymm T1 / Whiteleggs La T1 | LYMM T1 / WHITELEGGS LA T1 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM |  | 10 | 8.623 | -3.623 | Red | thermal | 10 | 2 | 3 | 10 | 0 | 0 | 0.3 | 0.3 | 0 | 8.623 | 10.3767 | -0.4 | 75.4 | 65.191 | 2.392 | AMBER | 0 |  |  |  |  | 0 | 0 | 0 | 0 | -3.6 | primary | 13 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | 10 | [7 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3803 | -2.4926 | 69 | 4333895 | 0
SPM-BEDBURN_DV_T1_BLUEBELL_LA_T1_BROOKBRIDGE_T1_ECCLESTON_T1 | Bedburn Dv T1 / Bluebell La T1 / Brookbridge T1 / Eccleston T1 |  | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | GATEACRE GT1 / HUYTON GT1 / KIRKBY GT3 / PRESCOT GT1A | RAINHILL | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Kirkby (_D) | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4296 | -2.8204 | 8 | 571642 | 0
SPM-BRITISH_ALUMINIUM_LATCHFORD_T1_GREENHALL_WHITLEY_T1_LATCHFOR | British Aluminium Latchford T1 / Greenhall Whitley T1 / Latchford T1 / Latchford T2 / Thames Board Mill T1 |  | SANKEY BRIDGES GT3 / WARRINGTON GT5 | SANKEY BRIDGES GT3 / WARRINGTON GT5 | CARRINGTON - FIDDLERS FERRY | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3819 | -2.5727 | 26 | 1071917 | 0
SPM-BRYN_STANLEY_T1_DENBIGH_T1 | Bryn Stanley T1 / Denbigh T1 |  | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Connahs Quay / SASA | [15 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1717 | -3.4532 | 6 | 127637 | 0
SPM-CHURCH_LA_T1_NANT_HALL_T1_PRESTATYN_T1 | Church La T1 / Nant Hall T1 / Prestatyn T1 |  | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 1.9 | 0.3 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Connahs Quay / SASA | [15 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3366 | -3.3836 | 3 | 112225 | 0
SPM-CIVIC_CENTRE_T1_CLAUGHTON_AVE_T1_ELECTRICITY_ST_T1 | Civic Centre T1 / Claughton Ave T1 / Electricity St T1 |  | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.0923 | -2.4456 | 16 | 529289 | 0
SPM-CONEY_GREEN_T1_OSWESTRY_T2_OSWESTRY_T1 | Coney Green T1 / Oswestry T2 / Oswestry T1 |  | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.872 | -3.0142 | 16 | 590457 | 0
SPM-HOLT_LA_WARRINGTON_RD_T1_PRESCOT_T1_RAINHILL_LOCAL_T1_WHISTO | Holt La (Warrington Rd) T1 / Prescot T1 / Rainhill Local T1 / Whiston Hosp T1 |  | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | BOLD G2A / PRESCOT GT1B / WIDNES GT1 / WIDNES GT2 | RAINHILL | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 1.1 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3997 | -2.7768 | 4 | 422120 | 0
SPM-LEIGHTON_HOSP_T1 | Leighton Hosp T1 |  | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | COPPENHALL GT1 / CREWE GT1 / CREWE GT2A / CREWE GT4A / RADWAY GREEN GT1 / RADWAY GREEN GT2 / WHITCHURCH GT2 | CELLARHEAD | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Frodsham | CELLARHEAD | 5 | 1680 | 1680 | 0 | 20 | 2027-07 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1386 | -2.4912 | 1 | 21785 | 0
SPM-RINGWAY_T1 | Ringway T1 |  | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | ELWORTH GT1 / ELWORTH GT2 / KNUTSFORD GT1 / KNUTSFORD GT2 | CARRINGTON - FIDDLERS FERRY | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Fiddlers Ferry | CARRINGTON | 5 | 2186.9 | 2186.9 | 0 | 930 | 2026-05 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3596 | -2.3052 | 121 | 5461589 | 0
SPM-ALMATEX_T1_ST_HELENS_WWTW_T1_WATERY_LA_T2_EX_DELTA_METALS_T1 | Almatex T1 / St Helens Wwtw T1 / Watery La T2 / Ex Delta Metals T1 |  | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | BOLD G2B / RAVENHEAD G1A2 / ST HELENS GT2A | RAINHILL | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Rainhill | RAINHILL | 1 | 85.5 | 85.5 | 0 | 57 | 2026-09 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4473 | -2.6891 | 71 | 5836708 | 0
SPM-BUILDWAS_RD_T1_MORGAN_REFRACTORIES_T1_NESTON_MAIN_T1 | Buildwas Rd T1 / Morgan Refractories T1 / Neston Main T1 |  | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | HESWALL GT1 / HOYLAKE GT2 / PRENTON GRID GT3 | BIRKENHEAD | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.7 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Connahs Quay / SASA | BIRKENHEAD | 0 | 0 | 0 | 0 | 90 | [9 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2853 | -3.0617 | 6 | 578679 | 0
SPM-EX_BIXTETH_ST_T1_LITTLEWOODS_T1_PALL_MALL_T1 | Ex Bixteth St T1 / Littlewoods T1 / Pall Mall T1 |  | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | BURLINGTON ST GT2 / LISTER DV B GT1 / PARADISE ST GT1 | LISTER DRIVE | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Lister Drive | LISTER DRIVE | 2 | 114 | 114 | 57 | 20 | 2026-09 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4105 | -2.9926 | 10 | 672295 | 0
SPM-KELCO_T1_NEWS_INTERNATIONAL_T1_NEWS_INTERNATIONAL_T2_PALCO_T | Kelco T1 / News International T1 / News International T2 / Palco T1 / Southdene T1 |  | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | GILLMOSS GT1 / KIRKBY GT2 / SIMONSWOOD GT1 | KIRKBY | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Kirkby (_D) | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.4666 | -2.8439 | 68 | 4696192 | 0
SPM-WELSHPOOL_T1 | Welshpool T1 |  | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY LOCAL GT2 / NEWTOWN GT2 / OSWESTRY GT8 / WELSHPOOL GT1 | LEGACY | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Legacy | LEGACY | 5 | 1714 | 1714 | 0 | 0 | 2024-08 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 52.681 | -3.1411 | 7 | 344084 | 0
SPM-BURMAH_OIL_T1_CABOT_CARBON_T1_VAN_LEER_NO_1_T1 | Burmah Oil T1 / Cabot Carbon T1 / Van Leer No 1 T1 |  | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | ELLESMERE PORT GT2 / INCE LOCAL GT1 / INCE LOCAL GT2 | FRODSHAM - INCE | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Capenhurst | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.2845 | -2.8774 | 10 | 250862 | 0
SPM-DARESBURY_NPL_T1_DARESBURY_NPL_T2_DARESBURY_PK_T1 | Daresbury Npl T1 / Daresbury Npl T2 / Daresbury Pk T1 |  | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | DUTTON GT2 / MOORE GT1 / PERCIVAL LA GT1 | FRODSHAM - INCE | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Fiddlers Ferry | FRODSHAM | 5 | 1090 | 1090 | 0 | 0 | 2029-04 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3352 | -2.5774 | 16 | 788581 | 0
SPM-GRAIG_FAWR_T1 | Graig Fawr T1 |  | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | HOLYWELL GT1 / RHYL GT1 / ST ASAPH GT2 / ST ASAPH GT4 | CONNAHS QUAY - PENTIR - ST ASAPH | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Connahs Quay / SASA | [15 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.3058 | -3.3731 | 2 | 40964 | 0
SPM-IVY_ST_SOUTHPORT_T1_KENSINGTON_RD_T1_MARKET_ST_T1_SOUTHPORT_ | Ivy St (Southport) T1 / Kensington Rd T1 / Market St T1 / Southport T1 |  | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | FORMBY GT2B / SOUTHPORT GT1 / SOUTHPORT GT2 | KIRKBY | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Lister Drive | KIRKBY | 4 | 514 | 514 | 0 | 0 | 2027-08 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.6373 | -2.9874 | 29 | 1155887 | 0
SPM-SALTNEY_T1 | Saltney T1 |  | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CHESTER MAIN GT4 / CRANE BANK GT1 / GUILDEN SUTTON GT1 / SALTNEY G2A | CAPENHURST | SPM | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  | unknown-primary | 0 | Capenhurst | CAPENHURST | 4 | 896.6 | 896.6 | 0 | 304 | 2029-10 | [8 empty] | SP Energy Networks open data (API key): NDP SPM primary-group polygons + Capacity Heatmaps Information Model SPM + LTDS appendices 3/6 + NSHR | SPEN-SPM | 53.1858 | -2.9681 | 26 | 568230 | 0

## Method & sources
item | detail
Built | 2026-10-01
Building source | VOA 2026 compiled rating list (epoch 3, 1 Apr 2026), summary valuations record 01: all 122 billing authorities inside UKPN's licence areas (EPN, LPN, SPN); industrial/office >= 1,000 m2, big-box retail/leisure >= 2,000 m2; hereditaments merged where postcode + address match
Power source | SP Energy Networks, Manweb (spenergynetworks.opendatasoft.com, API key): NDP SPM primary-group polygons (335, each a group of transformers) + Capacity Heatmaps Information Model SPM (firm, max demand, available capacity, constraint, offers made/accepted, budget estimates; tightest row per group kept, pipeline summed) + LTDS appendix 3 HV forecast (firm minus year-5 forecast = headroom_2030_mw, NSHR 2029/30 Holistic Transition as fallback) + LTDS appendix 6 connection activity 11kV/33kV (t6_*). No GSP tier. SP Distribution (Scotland) excluded: VOA building base stops at the border.
Site points | UKPN primary supply-area layer carries the substation coordinates; Knight Frank mirror used only where missing
Join | Nearest distribution substation within 400 m: UKPN secondary sites (ONAN rating x modelled demand-headroom band), ENWL distribution transformers (published demand headroom kVA) plus nearest 11kV section headroom within 300 m, Northern Powergrid substation sites (rating minus maximum demand). Not available for NGED (coordinates login-only), SSEN or SPEN. This is the test for a 0.3-2 MVA edge node connecting at LV/HV without reinforcement.
lm_* (last-mile tier) | England & Wales non-domestic EPC register (MHCLG 'Get energy performance of buildings data', Sep 2026 bulk extract; latest certificate per UPRN) matched to the VOA row by postcode + address tokens (epc_match_score; floor areas more than 4x apart rejected). Adds UPRN, EPC property type, EPC floor area, rating band, main heating fuel, building level, air-con kW, building environment, lodgement date and a data-centre/server-room flag. Address fields are not republished (OS/Royal Mail licence); UPRN and the rest are OGL.
tx_* (transmission tier) | NESO TEC register (28 Sep 2026): every transmission-contracted generation/storage/hybrid project not yet built, aggregated by connection site and matched to the primary's GSP name — projects, MW pipeline, storage MW, Gate 2 MW, earliest effective date, plus MW already connected. tx_gsp_region = NESO GSP region polygon the primary sits in. NESO publishes no demand-only register; transmission data-centre demand (c.140 projects, ~50 GW) is only in NESO's summary documents.
epc_* (EPC layer) | Building postcode centroid (postcodes.io) located inside the primary supply-area polygon; 'nearest-area' where the centroid fell outside every polygon
headroom_mw | UKPN heat map 'demand available capacity' (MW) at the primary = firm capacity minus maximum demand. headroom_polygon_mw is the older polygon-layer figure (firm x unutilised %) kept for comparison
bsp_headroom_mw / gsp_headroom_mw | same measure at the 33kV bulk supply point feeding the primary, and at the grid supply point (technical import limit winter minus maximum observed flow). Not every GSP publishes a limit (RED = no technical limit available)
effective_headroom_mw | min(primary, BSP, GSP) headroom — the tightest tier UKPN publishes; binding_tier names it. Still excludes transmission (NESO) constraints and connection offers already made
offers_* / budget_est_* / t6_* | demand connection offers accepted / made and budget estimates at the primary (heat map) and the LTDS table-6 breakdown by status: capacity already promised to others but not yet connected. pipeline_pressure_mw = accepted + made
gsp_queue_* | UKPN large-demand list aggregated by GSP: every live demand or storage-import application of 5 MVA and above (count, MVA, how many since 2024)
headroom_2030_mw | LTDS firm capacity minus UKPN's 2029/30 winter demand forecast for the primary — where headroom is heading before any new connections
edge_sqft_supportable_at_headroom | headroom_mw x 7,130 sq ft/MW (edge node: 55% white space, 150 W/sq ft IT, PUE 1.7) — gross floor an edge fit-out could power from local headroom
edge_fitout_whole_building_mva | area_sqft x 147.6 VA/gross sq ft / 1e6 (same edge-node spec, pf 0.95) — what a whole-building edge conversion would need
indicative_existing_kva | area_m2 x benchmark VA/m2 by use (warehouse 25, workshop 45, factory 60, office 70, big-box 90, lab 100, cold store 120) — a proxy for today's agreed supply capacity, which is private to the occupier/UKPN
score | headroom (0-60: min(headroom,20)/20 x 60) + size fit (25 if 20-150k sq ft, 15 if 10-20k or 150-300k, else 7.5) + RAG (Green 15 / Yellow 5 / Red 0)
Caveat 1 | Primary headroom is the binding limit only up to ~10-20 MVA; anything larger is a Grid/BSP or transmission question (NESO queue) and is NOT captured here
Caveat 2 | Supply-area polygons are indicative (built from MPAN postcodes); a building on a boundary may be fed from the neighbouring primary — confirm with a UKPN budget estimate
Caveat 3 | Floor areas are VOA valuation areas (GIA/NIA/other as flagged in 'unit'), not measured surveys